## 25F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023R2
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3139.302
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1789.65 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1708.31 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1737.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1827.42 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1708.31 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2033.24 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1911.64 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1964.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1868.51 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 651.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1827.42 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1737.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2136.46 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1868.51 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2082.6 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2082.6 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2033.24 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2047.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2102.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 743.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2047.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1789.65 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1964.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1911.64 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 811.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2136.46 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 743.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2102.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 651.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 811.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023R2
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2469.784
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1808.29 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1684.58 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1763.76 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1834.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1684.58 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2040.88 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1923.27 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1521.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1882.29 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 217.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1834.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1763.76 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2137.89 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1882.29 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2096.6 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2096.6 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2040.88 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1589.31 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1669.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 286.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1589.31 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1808.29 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1521.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1923.27 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 349.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2137.89 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 286.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1669.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 217.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 349.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023R2
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2237.4347
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1803.57 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1704.32 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1754.26 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1828.92 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1704.32 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2041.52 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1919.71 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 941.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1881.12 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -666.65 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1828.92 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1754.26 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2130.46 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1881.12 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2098.32 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2098.32 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2041.52 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1007.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1080.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -576.04 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1007.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1803.57 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 941.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1919.71 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | -531.35 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2130.46 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | -576.04 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1080.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -666.65 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -531.35 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023R2
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2765.3187
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1642.95 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1558.23 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1602.97 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1676.47 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1558.23 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1883.63 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1768.05 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1230.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1717.9 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -171.63 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1676.47 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 1602.97 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1972.47 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1717.9 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1942.38 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1942.38 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1883.63 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1300.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1369.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -174.18 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1300.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1642.95 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1230.03 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1768.05 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | -117.18 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1972.47 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | -174.18 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1369.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -171.63 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -117.18 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023R2
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3118.36
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1389.29 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1467.49 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1519.42 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1601.7 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1467.49 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1814.52 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1516.84 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1296.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1630.47 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -166.93 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1601.7 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1519.42 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1836.72 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1630.47 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1862.75 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1862.75 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1814.52 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1336.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1410.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -82.48 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1336.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1389.29 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 775 | 1296.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1516.84 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 140 | -13.06 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1836.72 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 460 | -82.48 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1410.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -166.93 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -13.06 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
G0 | 1789.65 | 1808.29 | 1803.57 | 1642.95 | 1389.29
G1 | 1737.18 | 1763.76 | 1754.26 | 1602.97 | 1519.42 | Season/Year: | WINTER 2009
G2 | 1708.31 | 1684.58 | 1704.32 | 1558.23 | 1467.49 | Direction: | South-to-North (SN)
G3 | 1911.64 | 1923.27 | 1919.71 | 1768.05 | 1516.84 | Case Loads: | Light Loads
G4 | 1868.51 | 1882.29 | 1881.12 | 1717.9 | 1630.47 | Outage: | 023R2
G5 | 1827.42 | 1834.91 | 1828.92 | 1676.47 | 1601.7 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2136.46 | 2137.89 | 2130.46 | 1972.47 | 1836.72 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2082.6 | 2096.6 | 2098.32 | 1942.38 | 1862.75 | Study Person: | FRP9899
G8 | 2033.24 | 2040.88 | 2041.52 | 1883.63 | 1814.52 | Source: | 023R2WINTER09v5SNL(COV-CRES BYP)
G9 | 2102.59 | 1669.79 | 1080.93 | 1369.92 | 1410.65
G10 | 2047.73 | 1589.31 | 1007.27 | 1300.49 | 1336.69
G11 | 1964.01 | 1521.97 | 941.11 | 1230.03 | 1296.52
G12 | 811.74 | 349.64 | -531.35 | -117.18 | -13.06
G13 | 743.83 | 286.03 | -576.04 | -174.18 | -82.48
G14 | 651.63 | 217.76 | -666.65 | -171.63 | -166.93
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 023R2 | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3139.302 | 1789.65 | 1737.18 | 1708.31 | 1911.64 | 1868.51 | 1827.42 | 2136.46 | 2082.6 | 2033.24 | 2102.59 | 2047.73 | 1964.01 | 811.74 | 743.83 | 651.63
35F | 2469.784 | 1808.29 | 1763.76 | 1684.58 | 1923.27 | 1882.29 | 1834.91 | 2137.89 | 2096.6 | 2040.88 | 1669.79 | 1589.31 | 1521.97 | 349.64 | 286.03 | 217.76
45F | 2237.4347 | 1803.57 | 1754.26 | 1704.32 | 1919.71 | 1881.12 | 1828.92 | 2130.46 | 2098.32 | 2041.52 | 1080.93 | 1007.27 | 941.11 | -531.35 | -576.04 | -666.65
60F | 2765.3187 | 1642.95 | 1602.97 | 1558.23 | 1768.05 | 1717.9 | 1676.47 | 1972.47 | 1942.38 | 1883.63 | 1369.92 | 1300.49 | 1230.03 | -117.18 | -174.18 | -171.63
70F | 3118.36 | 1389.29 | 1519.42 | 1467.49 | 1516.84 | 1630.47 | 1601.7 | 1836.72 | 1862.75 | 1814.52 | 1410.65 | 1336.69 | 1296.52 | -13.06 | -82.48 | -166.93

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1791.13 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -489.16 | -488.73 | 3196.37 | 1789.65 | 0 | FULL
G1 | 1739.77 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -491.48 | -491.31 | 3119.34 | 1737.18 | 0 | FULL
G2 | 1708.47 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 21.56 | 522.12 | 521.86 | 3127.19 | 1708.31 | 0 | FULL
G3 | 1913.98 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -489.99 | -489.81 | 3194.19 | 1911.64 | 0 | FULL
G4 | 1869.87 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -496.17 | -496.02 | 3119.44 | 1868.51 | 0 | FULL
G5 | 1828.23 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -499.76 | -499.7 | 3127.55 | 1827.42 | 0 | FULL
G6 | 2138.34 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -493.07 | -492.84 | 3192.41 | 2136.46 | 0 | FULL
G7 | 2084.48 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -494.92 | -494.8 | 3118.22 | 2082.6 | 0 | FULL
G8 | 2033.77 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -496.96 | -497.6 | 3127.48 | 2033.24 | 0 | FULL
G9 | 2103.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -466.43 | -466.4 | 3179.98 | 2102.59 | 0 | FULL
G10 | 2048.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -469.15 | -468.87 | 3107.69 | 2047.73 | 0 | FULL
G11 | 1964.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -462.9 | -462.84 | 3117.23 | 1964.01 | 0 | FULL
G12 | 812.31 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -456.36 | -456.34 | 3159.77 | 811.74 | 0 | FULL
G13 | 744.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -456.03 | -456.02 | 3093.25 | 743.83 | 0 | FULL
G14 | 651.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -453.36 | -453.34 | 3109.42 | 651.63 | 0 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1808.1 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -480.46 | -480.23 | 2522.5 | 1808.29 | 0 | FULL
G1 | 1764.86 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -484.46 | -484.7 | 2448.62 | 1763.76 | 0 | FULL
G2 | 1686.15 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 21.56 | 508.31 | 508.17 | 2457.14 | 1684.58 | 0 | FULL
G3 | 1924.96 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -481.42 | -481.31 | 2521.38 | 1923.27 | 0 | FULL
G4 | 1883.08 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -485.27 | -485.76 | 2448.15 | 1882.29 | 0 | FULL
G5 | 1835.73 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -487.53 | -487.68 | 2457.93 | 1834.91 | 0 | FULL
G6 | 2139.17 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -481.89 | -481.79 | 2521.35 | 2137.89 | 0 | FULL
G7 | 2098.21 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -486.23 | -486.75 | 2448.68 | 2096.6 | 0 | FULL
G8 | 2042.68 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -486.8 | -487.23 | 2459.78 | 2040.88 | 0 | FULL
G9 | 1669.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -457.59 | -457.46 | 2498.75 | 1669.79 | 0 | FULL
G10 | 1589.7 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -454.97 | -454.94 | 2429.13 | 1589.31 | 0 | FULL
G11 | 1522.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -454.13 | -454.1 | 2442.75 | 1521.97 | 0 | FULL
G12 | 349.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -446.86 | -446.87 | 2499.43 | 349.64 | 0 | FULL
G13 | 286.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -447.22 | -447.28 | 2435.8 | 286.03 | 0 | FULL
G14 | 218.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -448.11 | -448.17 | 2455.37 | 217.76 | 0 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1803.48 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -465.77 | -466.19 | 2284.89 | 1803.57 | 0 | FULL
G1 | 1754.27 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -468.6 | -468.96 | 2211.99 | 1754.26 | 0 | FULL
G2 | 1705.08 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 21.56 | 495.79 | 495.67 | 2222.36 | 1704.32 | 0 | FULL
G3 | 1920.25 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -466.29 | -466.88 | 2284.74 | 1919.71 | 0 | FULL
G4 | 1882.92 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -471.46 | -471.7 | 2212.33 | 1881.12 | 0 | FULL
G5 | 1829.77 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -472.93 | -472.95 | 2222.56 | 1828.92 | 0 | FULL
G6 | 2131.58 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -466.42 | -466.68 | 2285.07 | 2130.46 | 0 | FULL
G7 | 2099.69 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -472.35 | -472.53 | 2212.76 | 2098.32 | 0 | FULL
G8 | 2042.34 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -472.33 | -472.39 | 2223.32 | 2041.52 | 0 | FULL
G9 | 1081.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -414.5 | -414.19 | 2256.13 | 1080.93 | 0 | FULL
G10 | 1009.58 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -413.85 | -413.51 | 2189 | 1007.27 | 0 | FULL
G11 | 940.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -413.65 | -413.46 | 2205.01 | 941.11 | 0 | FULL
G12 | -533.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -421.13 | -421.27 | 2283.96 | -531.35 | 0 | FULL
G13 | -577.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -422.17 | -422.01 | 2222.52 | -576.04 | 0 | FULL
G14 | -665.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -421.81 | -421.86 | 2244.88 | -666.65 | 0 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1643.04 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -437 | -437.59 | 2814.84 | 1642.95 | 0 | FULL
G1 | 1603.54 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -441.81 | -442.37 | 2741.62 | 1602.97 | 0 | FULL
G2 | 1558.96 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -444.85 | -444.88 | 2751.68 | 1558.23 | 0 | FULL
G3 | 1769.06 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -439.64 | -439.87 | 2814.63 | 1768.05 | 0 | FULL
G4 | 1719.54 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -442.76 | -443 | 2741.55 | 1717.9 | 0 | FULL
G5 | 1677.33 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -445.65 | -445.66 | 2751.25 | 1676.47 | 0 | FULL
G6 | 1973.84 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -438.77 | -439.34 | 2815.28 | 1972.47 | 0 | FULL
G7 | 1943.02 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -444.64 | -444.75 | 2741.56 | 1942.38 | 0 | FULL
G8 | 1884.29 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -445.4 | -445.49 | 2752.48 | 1883.63 | 0 | FULL
G9 | 1371.21 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -420.7 | -420.5 | 2792.42 | 1369.92 | 0 | FULL
G10 | 1301.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -420.18 | -419.96 | 2723.05 | 1300.49 | 0 | FULL
G11 | 1230.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -418.73 | -418.62 | 2736.64 | 1230.03 | 0 | FULL
G12 | -116.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -416.43 | -416.49 | 2804.59 | -117.18 | 0 | FULL
G13 | -173.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -416.88 | -417.03 | 2740.38 | -174.18 | 0 | FULL
G14 | -171.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -420.79 | -420.82 | 2757.81 | -171.63 | 0 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1390.16 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.67 | -157.58 | -157.56 | 3161.63 | 1389.29 | 0 | FULL
G1 | 1521.03 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -423.37 | -423.68 | 3095.45 | 1519.42 | 0 | FULL
G2 | 1468.15 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -425.35 | -425.36 | 3103.68 | 1467.49 | 0 | FULL
G3 | 1518.85 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.67 | -157.14 | -157.14 | 3161.26 | 1516.84 | 0 | FULL
G4 | 1630.99 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -423.13 | -423.18 | 3094.73 | 1630.47 | 0 | FULL
G5 | 1602.37 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.87 | -429.61 | -429.65 | 3104.66 | 1601.7 | 0 | FULL
G6 | 1837.3 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.67 | -157.32 | -157.31 | 3164.89 | 1836.72 | 0 | FULL
G7 | 1863.37 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -427.7 | -427.78 | 3096.02 | 1862.75 | 0 | FULL
G8 | 1817.14 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.87 | -429.83 | -429.92 | 3104.95 | 1814.52 | 0 | FULL
G9 | 1409.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -416.79 | -416.76 | 3150.02 | 1410.65 | 0 | FULL
G10 | 1337.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -415.67 | -415.64 | 3079.62 | 1336.69 | 0 | FULL
G11 | 1297.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.65 | -421.09 | -420.76 | 3092.95 | 1296.52 | 0 | FULL
G12 | -12.74 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -416.64 | -416.5 | 3158.85 | -13.06 | 0 | FULL
G13 | -82.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -416.54 | -416.61 | 3094.6 | -82.48 | 0 | FULL
G14 | -166.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.74 | -416.66 | -416.65 | 3112.09 | -166.93 | 0 | FULL
023R2WINTER09v5SNL(COV-CRES BYP)