## 25F nomo
Monroe 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 026
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6632.3233
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -135.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 54.44 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | -67.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1015.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 54.44 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2719.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 107.64 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3177.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 859.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3047.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1015.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | -67.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 235.89 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 859.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 1989.33 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1989.33 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2719.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 1896.17 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 615.97 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2871.59 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1896.17 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -135.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3177.67 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 107.64 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1195.3 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 235.89 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2871.59 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 615.97 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3047.47 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1195.3 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Monroe 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 026
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6308.2633
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 145.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 452.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 306.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1355.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 452.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2989.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 966.58 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3103.38 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1198.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2970.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1355.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 306.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1160.83 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1198.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2851.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2851.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2989.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3079.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1529.04 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2944.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3079.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 145.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3103.38 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 966.58 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2094.67 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1160.83 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2944.41 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1529.04 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2970.57 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2094.67 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Monroe 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 026
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6026.656
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -43.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 247.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 106.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1097.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 247.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2765.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 790.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3043.05 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 947.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2905.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1097.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 106.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1774.86 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 947.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2630.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2630.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2765.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 3030.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2220.85 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2822.85 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3030.75 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -43.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3043.05 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 790.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2651.87 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1774.86 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2822.85 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2220.85 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2905.54 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2651.87 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Monroe 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 026
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4965.8527
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1295.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1578.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1454.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2388.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1578.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3246.91 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2096.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2843.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2255.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2698.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2388.14 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1454.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3224.74 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2255.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3237.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3237.5 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3246.91 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2819.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2808.11 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2604.87 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2819.92 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1295.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2843.4 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2096.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2538.61 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3224.74 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2604.87 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2808.11 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2698.13 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2538.61 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Monroe 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 026
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4631.9367
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1543.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1865.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1704.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2639.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1865.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3185.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2336.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2609.91 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2501.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1971.13 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2639.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 1704.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3161.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2501.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3169.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3169.52 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3185.96 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2751.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2744.17 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2512.06 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2751.87 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1543.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2609.91 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2336.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2435.83 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3161.24 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2512.06 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2744.17 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1971.13 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2435.83 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Monroe 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
G0 | -135.23 | 145.05 | -43.94 | 1295.13 | 1543.68
G1 | -67.94 | 306.02 | 106.92 | 1454.7 | 1704.02 | Season/Year: | WINTER 2009
G2 | 54.44 | 452.13 | 247.86 | 1578.47 | 1865.2 | Direction: | North-to-South (NS)
G3 | 107.64 | 966.58 | 790.51 | 2096.69 | 2336.94 | Case Loads: | Heavy Loads
G4 | 859.56 | 1198.13 | 947.85 | 2255.11 | 2501.61 | Outage: | 026
G5 | 1015.4 | 1355.27 | 1097.32 | 2388.14 | 2639.13 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 235.89 | 1160.83 | 1774.86 | 3224.74 | 3161.24 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1989.33 | 2851.92 | 2630.75 | 3237.5 | 3169.52 | Study Person: | FRP9899
G8 | 2719.68 | 2989.28 | 2765.15 | 3246.91 | 3185.96 | Source: | 026WINTER09v2NSH
G9 | 615.97 | 1529.04 | 2220.85 | 2808.11 | 2744.17
G10 | 1896.17 | 3079.52 | 3030.75 | 2819.92 | 2751.87
G11 | 3177.67 | 3103.38 | 3043.05 | 2843.4 | 2609.91
G12 | 1195.3 | 2094.67 | 2651.87 | 2538.61 | 2435.83
G13 | 2871.59 | 2944.41 | 2822.85 | 2604.87 | 2512.06
G14 | 3047.47 | 2970.57 | 2905.54 | 2698.13 | 1971.13
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 026 | Monroe 500/230kV Transformer Bank #1 (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6632.3233 | -135.23 | -67.94 | 54.44 | 107.64 | 859.56 | 1015.4 | 235.89 | 1989.33 | 2719.68 | 615.97 | 1896.17 | 3177.67 | 1195.3 | 2871.59 | 3047.47
35F | 6308.2633 | 145.05 | 306.02 | 452.13 | 966.58 | 1198.13 | 1355.27 | 1160.83 | 2851.92 | 2989.28 | 1529.04 | 3079.52 | 3103.38 | 2094.67 | 2944.41 | 2970.57
45F | 6026.656 | -43.94 | 106.92 | 247.86 | 790.51 | 947.85 | 1097.32 | 1774.86 | 2630.75 | 2765.15 | 2220.85 | 3030.75 | 3043.05 | 2651.87 | 2822.85 | 2905.54
60F | 4965.8527 | 1295.13 | 1454.7 | 1578.47 | 2096.69 | 2255.11 | 2388.14 | 3224.74 | 3237.5 | 3246.91 | 2808.11 | 2819.92 | 2843.4 | 2538.61 | 2604.87 | 2698.13
70F | 4631.9367 | 1543.68 | 1704.02 | 1865.2 | 2336.94 | 2501.61 | 2639.13 | 3161.24 | 3169.52 | 3185.96 | 2744.17 | 2751.87 | 2609.91 | 2435.83 | 2512.06 | 1971.13

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -135.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 475.17 | 472.76 | 6659.19 | -135.23 | 154.09 | FULL
G1 | -68.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 471.96 | 471.71 | 6587.2 | -67.94 | 187.62 | FULL
G2 | 53.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 471.28 | 471.2 | 6598.05 | 54.44 | 255.3 | FULL
G3 | 105.85 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 813.21 | 813.13 | 6654.14 | 107.64 | 361.1 | FULL
G4 | 859.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 482.67 | 482.46 | 6580.05 | 859.56 | 817.69 | FULL
G5 | 1015.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 483.14 | 483.09 | 6591.05 | 1015.4 | 906.94 | FULL
G6 | 235.8 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 815.19 | 815.12 | 6651.14 | 235.89 | 557.35 | FULL
G7 | 1994.75 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 813.7 | 813.64 | 6594.46 | 1989.33 | 1618.63 | FULL
G8 | 2730.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 491.56 | 491.42 | 6626.04 | 2719.68 | 2050.93 | FULL
G9 | 614.83 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 816.71 | 816.64 | 6655.05 | 615.97 | 990.17 | FULL
G10 | 1902.92 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 807.62 | 807.57 | 6609.72 | 1896.17 | 1755.33 | FULL
G11 | 3194.49 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -509.15 | -508.51 | 6669.7 | 3177.67 | 2509.11 | FULL
G12 | 1195.48 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 814.98 | 814.9 | 6670.51 | 1195.3 | 1480.51 | FULL
G13 | 2884.15 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 805.87 | 805.8 | 6656.16 | 2871.59 | 2469.78 | FULL
G14 | 3062.32 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -513.12 | -512.55 | 6682.39 | 3047.47 | 2573.4 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 144.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 466.55 | 466.37 | 6322.9 | 145.05 | 339.67 | FULL
G1 | 304.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 467.24 | 467.07 | 6250.58 | 306.02 | 432.71 | FULL
G2 | 451.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 467.5 | 467.33 | 6261.19 | 452.13 | 516.77 | FULL
G3 | 966.92 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 820.13 | 820.07 | 6317.1 | 966.58 | 904.72 | FULL
G4 | 1201.16 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 475.92 | 476.07 | 6248.08 | 1198.13 | 1039.24 | FULL
G5 | 1356.65 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 476.81 | 476.81 | 6262.05 | 1355.27 | 1128.14 | FULL
G6 | 1163.81 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 821.05 | 820.98 | 6319.79 | 1160.83 | 1137.9 | FULL
G7 | 2865.08 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 483.52 | 483.29 | 6287.88 | 2851.92 | 2145.14 | FULL
G8 | 3002.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 483.22 | 483.07 | 6307.01 | 2989.28 | 2219.49 | FULL
G9 | 1532 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 820.04 | 819.98 | 6336.39 | 1529.04 | 1558.2 | FULL
G10 | 3093.96 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -501.38 | -500.69 | 6321.69 | 3079.52 | 2467.82 | FULL
G11 | 3119.09 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -499.95 | -499.2 | 6338.13 | 3103.38 | 2483.43 | FULL
G12 | 2102.27 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 816.56 | 816.51 | 6365.27 | 2094.67 | 2031.08 | FULL
G13 | 2958.86 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -504.25 | -503.89 | 6334.38 | 2944.41 | 2521.35 | FULL
G14 | 2985.34 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -503.7 | -503.32 | 6351.51 | 2970.57 | 2537.65 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -44.97 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 434.08 | 433.98 | 6039.17 | -43.94 | 223.46 | FULL
G1 | 104.96 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 434.3 | 434.19 | 5967.63 | 106.92 | 309.31 | FULL
G2 | 246.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 434.42 | 434.3 | 5978.02 | 247.86 | 390.42 | FULL
G3 | 790.2 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 439.95 | 439.68 | 6032.27 | 790.51 | 795.61 | FULL
G4 | 950.05 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 440.46 | 440.23 | 5962.96 | 947.85 | 884.98 | FULL
G5 | 1098.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 440.78 | 440.85 | 5976.46 | 1097.32 | 969.77 | FULL
G6 | 1778.68 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 816.25 | 816.15 | 6045.12 | 1774.86 | 1506.93 | FULL
G7 | 2640.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 448.17 | 447.93 | 5997.53 | 2630.75 | 2012.21 | FULL
G8 | 2776.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 448.5 | 448.42 | 6016.71 | 2765.15 | 2083.85 | FULL
G9 | 2229.32 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 820.81 | 820.63 | 6071.63 | 2220.85 | 1968.66 | FULL
G10 | 3045.54 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -490.73 | -490.21 | 6037.5 | 3030.75 | 2448.98 | FULL
G11 | 3057.97 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -490.45 | -490.01 | 6053.62 | 3043.05 | 2438.25 | FULL
G12 | 2662.63 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 6.3 | 805.84 | 805.72 | 6104.94 | 2651.87 | 2361.23 | FULL
G13 | 2835.52 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -12.88 | -473.11 | -473.08 | 6048.76 | 2822.85 | 2457.93 | FULL
G14 | 2917.93 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -493.23 | -492.57 | 6067.52 | 2905.54 | 2490.26 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1297.6 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 440.86 | 440.99 | 4955.85 | 1295.13 | 1085.33 | FULL
G1 | 1456.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 441.96 | 442.07 | 4889.8 | 1454.7 | 1173.74 | FULL
G2 | 1581.78 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 441.11 | 441.19 | 4906.39 | 1578.47 | 1243.01 | FULL
G3 | 2102.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 445.27 | 445.1 | 4969.82 | 2096.69 | 1625.76 | FULL
G4 | 2262.2 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 446.04 | 446.08 | 4907.09 | 2255.11 | 1712.99 | FULL
G5 | 2396.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 446.22 | 446.33 | 4927.2 | 2388.14 | 1784.55 | FULL
G6 | 3241.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -470.57 | -471.05 | 5019.79 | 3224.74 | 2400.63 | FULL
G7 | 3254.14 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -470.69 | -471.03 | 4955.28 | 3237.5 | 2398.93 | FULL
G8 | 3264.47 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.87 | -468.28 | -468.7 | 4973.27 | 3246.91 | 2397.73 | FULL
G9 | 2821.48 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -474.64 | -473.8 | 5027.72 | 2808.11 | 2347.93 | FULL
G10 | 2833.22 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -474.1 | -473.24 | 4963.37 | 2819.92 | 2345.98 | FULL
G11 | 2855.92 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -477.34 | -476.49 | 4981.99 | 2843.4 | 2347.41 | FULL
G12 | 2548.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -12.88 | -460.83 | -460.99 | 5036.95 | 2538.61 | 2326.45 | FULL
G13 | 2615.41 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -12.88 | -462.57 | -462.55 | 4975.21 | 2604.87 | 2352.03 | FULL
G14 | 2709.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -476.81 | -476.02 | 4998.06 | 2698.13 | 2398.32 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1547.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 441.27 | 441.48 | 4624.16 | 1543.68 | 1236.84 | FULL
G1 | 1706.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 441.9 | 442.07 | 4560.55 | 1704.02 | 1326 | FULL
G2 | 1870.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 443.44 | 443.57 | 4579.37 | 1865.2 | 1415.77 | FULL
G3 | 2345.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 446.02 | 446.18 | 4643.19 | 2336.94 | 1769.58 | FULL
G4 | 2510.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 446.62 | 446.77 | 4582.07 | 2501.61 | 1860.68 | FULL
G5 | 2649.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 9.29 | 446.67 | 446.76 | 4603.23 | 2639.13 | 1934.19 | FULL
G6 | 3177.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -461.4 | -460.38 | 4685.05 | 3161.24 | 2362.87 | FULL
G7 | 3186.37 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -459.63 | -459.21 | 4621.04 | 3169.52 | 2359.68 | FULL
G8 | 3202.32 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -460 | -459.62 | 4639.17 | 3185.96 | 2362.28 | FULL
G9 | 2755.51 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -463.09 | -462.09 | 4692.86 | 2744.17 | 2310.73 | FULL
G10 | 2763.44 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.61 | -460.5 | -459.62 | 4629.35 | 2751.87 | 2307.22 | FULL
G11 | 2620.21 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.36 | -174.02 | -173.97 | 4640.09 | 2609.91 | 2217.18 | FULL
G12 | 2445.8 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -12.88 | -449.88 | -449.91 | 4701.24 | 2435.83 | 2264.24 | FULL
G13 | 2520.68 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -12.88 | -448.84 | -449.07 | 4641.02 | 2512.06 | 2299.46 | FULL
G14 | 1977.65 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.36 | -173.11 | -173.1 | 4636.66 | 1971.13 | 1963.54 | FULL
026WINTER09v2NSH