## 25F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3294.6447
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1486.96 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1656.71 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1705.58 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1762.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1656.71 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1980.88 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1682.11 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2109.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1811.54 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 814.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1762.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1705.58 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1961.03 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1811.54 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2027.4 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2027.4 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1980.88 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2168.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2226.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 882.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2168.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1486.96 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 775 | 2109.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1682.11 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 140 | 952.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1961.03 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 460 | 882.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2226.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 814.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 952.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2614.2333
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1769.49 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1679.44 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1723.65 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1797.44 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1679.44 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2013.76 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1889.82 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1624.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1841.62 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 313.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1797.44 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1723.65 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2105.39 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1841.62 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2057.27 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2057.27 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2013.76 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1693.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1737.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 376.98 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1693.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1769.49 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1624.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1889.82 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 446.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2105.39 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 376.98 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1737.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 313.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 446.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2375.6047
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1766.35 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1672.49 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1725.95 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1790.3 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1672.49 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2010.16 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1885.46 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1022 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1844.61 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -521.34 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1790.3 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1725.95 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2102.48 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1844.61 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2059.54 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2059.54 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2010.16 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1086.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1158.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -511.14 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1086.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1766.35 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1022 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1885.46 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | -456.18 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2102.48 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | -511.14 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1158.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -521.34 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -456.18 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2898.3193
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1615.57 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1517.06 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1575.68 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1647.34 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1517.06 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1863.49 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1735.31 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1299.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1694.84 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -214.35 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1647.34 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 1575.68 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1952.44 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1694.84 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1909.88 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1909.88 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1863.49 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1362.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1434.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -80.26 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1362.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1615.57 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1299.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1735.31 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | -54.88 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1952.44 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | -80.26 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1434.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -214.35 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -54.88 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 023
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3250.1567
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1274.85 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1456.29 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1485.48 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1567.2 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1456.29 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1784.12 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 1497.62 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1327.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 1620.87 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | -130.68 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1567.2 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1485.48 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 1784.56 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1620.87 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1823.49 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1823.49 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1784.12 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1395.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1471.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -32.93 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1395.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1274.85 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 775 | 1327.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1497.62 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 140 | 29.45 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1784.56 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 460 | -32.93 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1471.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -130.68 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 29.45 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
G0 | 1486.96 | 1769.49 | 1766.35 | 1615.57 | 1274.85
G1 | 1705.58 | 1723.65 | 1725.95 | 1575.68 | 1485.48 | Season/Year: | WINTER 2009
G2 | 1656.71 | 1679.44 | 1672.49 | 1517.06 | 1456.29 | Direction: | South-to-North (SN)
G3 | 1682.11 | 1889.82 | 1885.46 | 1735.31 | 1497.62 | Case Loads: | Light Loads
G4 | 1811.54 | 1841.62 | 1844.61 | 1694.84 | 1620.87 | Outage: | 023
G5 | 1762.18 | 1797.44 | 1790.3 | 1647.34 | 1567.2 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1961.03 | 2105.39 | 2102.48 | 1952.44 | 1784.56 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2027.4 | 2057.27 | 2059.54 | 1909.88 | 1823.49 | Study Person: | FRP9899
G8 | 1980.88 | 2013.76 | 2010.16 | 1863.49 | 1784.12 | Source: | 023WINTER09v1SNL
G9 | 2226.16 | 1737.05 | 1158.58 | 1434.53 | 1471.19
G10 | 2168.41 | 1693.8 | 1086.72 | 1362.84 | 1395.86
G11 | 2109.87 | 1624.72 | 1022 | 1299.53 | 1327.86
G12 | 952.36 | 446.26 | -456.18 | -54.88 | 29.45
G13 | 882.35 | 376.98 | -511.14 | -80.26 | -32.93
G14 | 814.42 | 313.01 | -521.34 | -214.35 | -130.68
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 023 | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3294.6447 | 1486.96 | 1705.58 | 1656.71 | 1682.11 | 1811.54 | 1762.18 | 1961.03 | 2027.4 | 1980.88 | 2226.16 | 2168.41 | 2109.87 | 952.36 | 882.35 | 814.42
35F | 2614.2333 | 1769.49 | 1723.65 | 1679.44 | 1889.82 | 1841.62 | 1797.44 | 2105.39 | 2057.27 | 2013.76 | 1737.05 | 1693.8 | 1624.72 | 446.26 | 376.98 | 313.01
45F | 2375.6047 | 1766.35 | 1725.95 | 1672.49 | 1885.46 | 1844.61 | 1790.3 | 2102.48 | 2059.54 | 2010.16 | 1158.58 | 1086.72 | 1022 | -456.18 | -511.14 | -521.34
60F | 2898.3193 | 1615.57 | 1575.68 | 1517.06 | 1735.31 | 1694.84 | 1647.34 | 1952.44 | 1909.88 | 1863.49 | 1434.53 | 1362.84 | 1299.53 | -54.88 | -80.26 | -214.35
70F | 3250.1567 | 1274.85 | 1485.48 | 1456.29 | 1497.62 | 1620.87 | 1567.2 | 1784.56 | 1823.49 | 1784.12 | 1471.19 | 1395.86 | 1327.86 | 29.45 | -32.93 | -130.68

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1487.8 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.71 | -147.73 | -147.69 | 3336.11 | 1486.96 | 0 | FULL
G1 | 1706.43 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -491.66 | -491.46 | 3276 | 1705.58 | 0 | FULL
G2 | 1657.34 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -494.62 | -494.54 | 3283.1 | 1656.71 | 0 | FULL
G3 | 1682.64 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.71 | -147.62 | -147.71 | 3337.53 | 1682.11 | 0 | FULL
G4 | 1812.09 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -490.58 | -490.35 | 3274.91 | 1811.54 | 0 | FULL
G5 | 1762.89 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -493.49 | -493.43 | 3282.48 | 1762.18 | 0 | FULL
G6 | 1961.5 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.71 | -147.41 | -147.43 | 3339.6 | 1961.03 | 0 | FULL
G7 | 2028.03 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -491.47 | -491.32 | 3274.23 | 2027.4 | 0 | FULL
G8 | 1981.7 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -494.45 | -494.38 | 3282.57 | 1980.88 | 0 | FULL
G9 | 2227.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -469.62 | -469.42 | 3341.84 | 2226.16 | 0 | FULL
G10 | 2168.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -471.13 | -471 | 3269.45 | 2168.41 | 0 | FULL
G11 | 2110.61 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -471.06 | -470.82 | 3280.53 | 2109.87 | 0 | FULL
G12 | 952.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -457.5 | -457.48 | 3319.26 | 952.36 | 0 | FULL
G13 | 883.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -457.19 | -457.17 | 3252.6 | 882.35 | 0 | FULL
G14 | 815.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -456.95 | -456.93 | 3269.46 | 814.42 | 0 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1769.98 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -478.38 | -478.3 | 2662.95 | 1769.49 | 0 | FULL
G1 | 1724.48 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -482.33 | -482.87 | 2590.3 | 1723.65 | 0 | FULL
G2 | 1680.14 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -485.34 | -485.66 | 2600.93 | 1679.44 | 0 | FULL
G3 | 1889.93 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -479.39 | -479.31 | 2662.5 | 1889.82 | 0 | FULL
G4 | 1842.23 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -483.19 | -483.69 | 2590.09 | 1841.62 | 0 | FULL
G5 | 1798.53 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -486.63 | -486.98 | 2601 | 1797.44 | 0 | FULL
G6 | 2106.59 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -481.38 | -481.3 | 2663.68 | 2105.39 | 0 | FULL
G7 | 2058.75 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -484.08 | -484.65 | 2590.63 | 2057.27 | 0 | FULL
G8 | 2014.61 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -487.14 | -487.26 | 2601.42 | 2013.76 | 0 | FULL
G9 | 1736.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -450.02 | -449.99 | 2645.04 | 1737.05 | 0 | FULL
G10 | 1693.6 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -455.97 | -455.67 | 2577.02 | 1693.8 | 0 | FULL
G11 | 1626.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -454.9 | -454.54 | 2590.18 | 1624.72 | 0 | FULL
G12 | 447.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -445.43 | -445.24 | 2648.18 | 446.26 | 0 | FULL
G13 | 377.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -445.32 | -445.33 | 2584.98 | 376.98 | 0 | FULL
G14 | 312.94 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -446 | -446.12 | 2604.6 | 313.01 | 0 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1766.81 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -463.36 | -463.98 | 2419.7 | 1766.35 | 0 | FULL
G1 | 1726.81 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -468.86 | -468.98 | 2347.27 | 1725.95 | 0 | FULL
G2 | 1673.12 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -469.77 | -470.15 | 2359.09 | 1672.49 | 0 | FULL
G3 | 1886.1 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -464.72 | -465.31 | 2419.51 | 1885.46 | 0 | FULL
G4 | 1845.49 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -469.73 | -469.82 | 2347.49 | 1844.61 | 0 | FULL
G5 | 1791.37 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -470.8 | -471.12 | 2359.46 | 1790.3 | 0 | FULL
G6 | 2104.06 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -465.71 | -466.27 | 2419.81 | 2102.48 | 0 | FULL
G7 | 2059.25 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -469.9 | -470.06 | 2348.33 | 2059.54 | 0 | FULL
G8 | 2011.11 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -472.22 | -472.24 | 2359.52 | 2010.16 | 0 | FULL
G9 | 1159.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -413.22 | -413.2 | 2397.4 | 1158.58 | 0 | FULL
G10 | 1087.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -412.49 | -412.47 | 2330.58 | 1086.72 | 0 | FULL
G11 | 1022.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -412.63 | -412.25 | 2346.68 | 1022 | 0 | FULL
G12 | -455.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -419.93 | -419.85 | 2426.59 | -456.18 | 0 | FULL
G13 | -512.17 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -420.53 | -420.6 | 2365.95 | -511.14 | 0 | FULL
G14 | -521.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -423.49 | -423.44 | 2386.69 | -521.34 | 0 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1616.12 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -436.32 | -436.93 | 2945.3 | 1615.57 | 0 | FULL
G1 | 1576.47 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -441.51 | -441.83 | 2871.99 | 1575.68 | 0 | FULL
G2 | 1518.81 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -442.36 | -442.54 | 2882.5 | 1517.06 | 0 | FULL
G3 | 1736.24 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -437.58 | -438.08 | 2944.61 | 1735.31 | 0 | FULL
G4 | 1695.13 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -442.27 | -442.48 | 2871.79 | 1694.84 | 0 | FULL
G5 | 1649.01 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -445.21 | -445.17 | 2882.14 | 1647.34 | 0 | FULL
G6 | 1953.26 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -438.31 | -438.76 | 2944.75 | 1952.44 | 0 | FULL
G7 | 1910.93 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -443.2 | -443.27 | 2872.6 | 1909.88 | 0 | FULL
G8 | 1863.6 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -445.68 | -445.52 | 2882.82 | 1863.49 | 0 | FULL
G9 | 1435.21 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -419.34 | -419.03 | 2927.27 | 1434.53 | 0 | FULL
G10 | 1363.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -418.16 | -417.79 | 2858.14 | 1362.84 | 0 | FULL
G11 | 1300.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -418.05 | -417.8 | 2872.24 | 1299.53 | 0 | FULL
G12 | -54.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -415.5 | -415.54 | 2942.42 | -54.88 | 0 | FULL
G13 | -80.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -417.9 | -417.89 | 2878.13 | -80.26 | 0 | FULL
G14 | -213.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -415.01 | -415.02 | 2898.09 | -214.35 | 0 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1274.74 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.71 | -147.21 | -147.25 | 3287.66 | 1274.85 | 0 | FULL
G1 | 1484.97 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -421.39 | -421.36 | 3224.36 | 1485.48 | 0 | FULL
G2 | 1456.76 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -428.15 | -428.23 | 3234.31 | 1456.29 | 0 | FULL
G3 | 1497.79 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.71 | -147.48 | -147.52 | 3290.25 | 1497.62 | 0 | FULL
G4 | 1621.59 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -425.09 | -424.97 | 3224.33 | 1620.87 | 0 | FULL
G5 | 1568.48 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -426.67 | -426.67 | 3234.69 | 1567.2 | 0 | FULL
G6 | 1785.25 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -3.71 | -147.44 | -147.49 | 3293.21 | 1784.56 | 0 | FULL
G7 | 1824.27 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.83 | -423.35 | -423.44 | 3225.29 | 1823.49 | 0 | FULL
G8 | 1784.64 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -21.83 | -427.22 | -427.2 | 3235.3 | 1784.12 | 0 | FULL
G9 | 1472.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -415.45 | -415.41 | 3283.68 | 1471.19 | 0 | FULL
G10 | 1396.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -413.59 | -413.55 | 3213.79 | 1395.86 | 0 | FULL
G11 | 1328.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.66 | -413 | -412.96 | 3226.88 | 1327.86 | 0 | FULL
G12 | 29.78 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -414.85 | -414.87 | 3295.83 | 29.45 | 0 | FULL
G13 | -32.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -415.26 | -415.3 | 3231.94 | -32.93 | 0 | FULL
G14 | -130.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.75 | -414.46 | -414.47 | 3250.83 | -130.68 | 0 | FULL
023WINTER09v1SNL