## Beam
CHAPTER 17. ESTIMATING FIRE RESISTANCE TIME OF UNPROTECTED
STEEL BEAMS (QUASI-STEADY-STATE APPROACH)
Version 1805.0
The following calculations estimate the fire resistance time for unprotected structural steel beams.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Beam and Insulation Selected.
All subsequent output values are calculated by the spreadsheet, and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| The Ratio of Heated Surface Area to Volume of Beam (both per unit length) (F/V) | [6 empty] | 79.5459 | m-1
| Flame Emissivity (ef) | [6 empty] | 0.3
| Specific Heat of Steel (cs) | [6 empty] | 600 | J/kg-K
| Density of Steel (rs) | [6 empty] | 7850 | kg/m3
| Convective heat Transfer Coefficient (hc) | [6 empty] | 25 | W/m2-K
| Stefan Boltzmann Constant | [6 empty] | 5.669e-08 | W/m2-K4
| Ambient Air Temperature (Ta) | [6 empty] | 25 | °C | 298.15 | K
| Constant (C1) | [6 empty] | 345
SECTIONAL FACTORS FOR STEEL BEAMS
| Structural Shape | F/V Ratio
| W Shapes | (m-1)
| 36x300 | 54.1974 |  | Emissivity
| 36x280 | 57.8391 |  | 0.3
| 36x260 | 62.0092 |  | 0.5
| 36x245 | 65.5749 |  | 0.7
| 36x230 | 69.7072 |  | User Specified (Enter Value)
| 36x210 | 68.9677
| 36x194 | 74.4543
| 36x182 | 78.9128
| 36x170 | 84.3071
| 36x160 | 89.3952
| 36x150 | 94.751
| 36x135 | 104.8712
| 33x241 | 63.4586
| 33x221 | 68.8825
| 33x201 | 75.386
| 33x152 | 88.4329
| 33x141 | 94.6349
| 33x130 | 102.3314
| 33x118 | 112.3919
| 30x211 | 67.0847
| 30x191 | 73.7294
| 30x173 | 81.007
| 30x132 | 92.125
| 30x124 | 97.8481
| 30x116 | 104.0372
| 30x108 | 111.77
| 30x99 | 121.2355
| 27x178 | 72.5862
| 27x161 | 79.6704
| 27x146 | 87.5915
| 27x114 | 98.3077
| 27x102 | 109.1798
| 27x94 | 117.7265
| 27x84 | 130.7785
| 24x162 | 72.1826
| 24x146 | 79.5459
| 24x131 | 88.2657
| 24x117 | 98.2192
| 24x104 | 109.8374
| 24x94 | 106.2921
| 24x84 | 118.4609
| 24x76 | 129.9388
| 24x68 | 144.0142
| 24x62 | 146.5346
| 24x55 | 163.7139
| 21x147 | 73.0989
| 21x132 | 80.8507
| 21x122 | 86.998
| 21x111 | 95.042
| 21x101 | 103.8287
| 21x93 | 97.1129
| 21x83 | 108.3811
| 21x73 | 121.6902
| 21x68 | 130.3346
| 21x62 | 141.7753
| 21x57 | 143.7126
| 21x50 | 162.0065
| 21x44 | 182.0715
| 18x119 | 78.9925
| 18x106 | 88.4624
| 18x97 | 96.0699
| 18x86 | 107.513
| 18x76 | 121.244
| 18x71 | 111.4003
| 18x65 | 120.728
| 18x60 | 130.4134
| 18x55 | 141.0275
| 18x50 | 154.6816
| 18x46 | 156.2555
| 18x40 | 177.549
| 18x35 | 201.8194
| 16x100 | 85.7638
| 16x89 | 95.4875
| 16x77 | 109.7746
| 16x67 | 125.055
| 16x57 | 125.0469
| 16x50 | 141.8662
| 16x45 | 155.9262
| 16x40 | 174.8132
| 16x36 | 193.4519
| 16x31 | 206.2828
| 16x26 | 242.8847
| 14x730 | 16.9145
| 14x665 | 18.1926
| 14x605 | 19.6618
| 14x550 | 21.221
| 14x500 | 22.9927
| 14x455 | 24.8311
| 14x426 | 26.3543
| 14x398 | 27.8653
| 14x370 | 29.6016
| 14x342 | 31.535
| 14x311 | 34.507
| 14x283 | 37.4465
| 14x257 | 40.8256
| 14x233 | 44.606
| 14x211 | 48.8189
| 14x193 | 52.8931
| 14x176 | 57.5578
| 14x159 | 63.5974
| 14x145 | 68.8746
| 14x132 | 73.2659
| 14x120 | 80.0674
| 14x109 | 87.8506
| 14x99 | 96.1185
| 14x90 | 105.0661
| 14x82 | 94.7332
| 14x74 | 104.114
| 14x68 | 112.9035
| 14x61 | 125.4014
| 14x53 | 129.4165
| 14x48 | 142.3745
| 14x43 | 158.4021
| 14x38 | 168.3422
| 14x34 | 187.5
| 14x30 | 210.5521
| 14x26 | 216.9962
| 14x22 | 254.9046
| 12x336 | 27.9914
| 12x305 | 30.3602
| 12x279 | 32.7171
| 12x252 | 35.6217
| 12x230 | 38.5065
| 12x210 | 41.6826
| 12x190 | 45.6143
| 12x170 | 50.2756
| 12x152 | 55.5937
| 12x136 | 61.6107
| 12x120 | 68.9032
| 12x106 | 77.2512
| 12x96 | 84.883
| 12x87 | 92.8965
| 12x79 | 101.921
| 12x72 | 111.505
| 12x65 | 122.5626
| 12x58 | 124.34
| 12x53 | 134.8047
| 12x50 | 128.234
| 12x45 | 141.9262
| 12x40 | 157.8306
| 12x35 | 168.4886
| 12x30 | 195.8202
| 12x26 | 223.6118
| 12x22 | 219.877
| 12x19 | 253.5023
| 12x16 | 296.822
| 12x14 | 334.3618
| 10x112 | 62.7707
| 10x100 | 69.4467
| 10x88 | 77.9269
| 10x77 | 88.3388
| 10x68 | 98.9173
| 10x60 | 111.4889
| 10x54 | 123.4177
| 10x49 | 134.7332
| 10x45 | 128.9444
| 10x39 | 147.7747
| 10x33 | 173.3743
| 10x30 | 168.2136
| 10x26 | 193.7463
| 10x22 | 225.1192
| 10x19 | 224.4515
| 10x17 | 250.6588
| 10x15 | 281.3934
| 10x12 | 347.4354
| 8x67 | 83.3367
| 8x58 | 94.7184
| 8x48 | 113.168
| 8x40 | 134.5649
| 8x35 | 151.7048
| 8x31 | 169.964
| 8x28 | 167.7643
| 8x24 | 193.8198
| 8x21 | 203.689
| 8x18 | 236.2953
| 8x15 | 246.2847
| 8x13 | 282.1522
| 8x10 | 362.5771
| 6x25 | 162.8441
| 6x20 | 200.8075
| 6x15 | 262.0821
| 6x16 | 200.4219
| 6x12 | 261.7278
| 6x9 | 341.9908
| 5x19 | 176.5968
| 5x16 | 206.4405
| 4x13 | 205
| User Specified Value | Enter Value
Select Beam
Scroll to desired beam size then Click on selection
EMISSIVITY VALUES FOR DIFFERENT CONSTRUCTION TYPES
|  |  | Emissivity | Select Flame Emissivity, ef
Type of Construction |  |  | ef
Scroll to desired construction type then Click on selection
Beam outside façade |  |  | 0.3
Floor girder with floor slab of concrete, only the
underside of the bottom flange being directly |  |  | 0.3
exposed to fire
Floor girder with floor slab on the top flange
Girder of I section for which the width-depth |  |  | 0.5
ratio is not less than 0.5
Floor girder with floor slab on the top flange
Girder of I section for which the width-depth |  |  | 0.7
ratio is less than 0.5
Floor girder with floor slab on the top flange
Box girder and lattice |  |  | 0.7
Beam exposed to fire on all sides |  |  | 0.7
User Specified Value |  |  | Enter Value
ESTIMATING FIRE RESISTANCE TIME OF UNPROTECTED STEEL BEAMS USING
QUASI-STEADY-STATE APPROACH
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 179.
DTs = F/V 1/rs cs (hc (Tf - Ts) + s e (Tf4 - Ts4)) Dt
| Where | DTs = temperature rise in steel (°F)
F/V = ratio of heated surface area to volume of beam (both per unit length) (m-1)
rs = density of steel (kg/m3)
cs = specific heat of steel (J/kg-K)
hc = convective heat transfer coefficient (W/m2-K)
s = Stefan Boltzmann constant (kW/m2-K4)
e = flame emissivity
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
The Maximum Allowable Time Step
| Dt = | 30 | sec
Calculate
For ASTM E 119 exposure, Tf at any time, t, is given by the following expression
| Tf = C1 LOG (0.133 t + 1) + Ta |  | (Refecrece: SFPE Handbook 3rd Edition, p. 4-223)
| Where | Tf = fire exposure temperature (°F)
|  | C2 = constant = 620 |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | t = time step (sec) |  |  | carbon steel structural members begin to fail. Predicted
|  | Ta = ambient air temperature (°F) |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
DTs1 = F/V 1/rscs (hc (C1 LOG (0.133 t1 + 1) +Ta) - Ts0) + s e ((C1 LOG (0.133 t1 + 1) +Ta)4 - Ts04)) Dt
| Where | t1 = Dt/2
Ts0 = initial steel temperature (°F)
DTs2 = F/V 1/rscs (hc (C1 LOG (0.133 t2 + 1) +Ta) - Ts) + s e ((C1 LOG (0.133 t2 + 1) +Ta)4 - Ts4)) Dt
| Where | t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
| time | Tf | DTS | TS
| (s) | (k) |  | (K)
| 30 | 656.474 | 6.071 | 304.221
| 60 | 753.3134 | 8.3895 | 312.6105
| 90 | 811.6513 | 9.9784 | 322.589
| 120 | 853.5337 | 11.2052 | 333.7942
| 150 | 886.2299 | 12.2058 | 346
| 180 | 913.0536 | 13.0478 | 359.0478
| 210 | 935.7965 | 13.7702 | 372.818
| 240 | 955.5379 | 14.3981 | 387.2161
| 270 | 972.9784 | 14.9484 | 402.1645
| 300 | 988.5988 | 15.4332 | 417.5977
| 330 | 1002.7434 | 15.8615 | 433.4591
| 360 | 1015.6672 | 16.24 | 449.6991
| 390 | 1027.5642 | 16.574 | 466.2731
| 420 | 1038.5856 | 16.8676 | 483.1408
| 450 | 1048.8515 | 17.1241 | 500.2649
| 480 | 1058.459 | 17.3461 | 517.6109
| 510 | 1067.4873 | 17.5356 | 535.1466
| 540 | 1076.0024 | 17.6945 | 552.8411
| 570 | 1084.0595 | 17.8241 | 570.6652
| 600 | 1091.7054 | 17.9255 | 588.5907
| 630 | 1098.9799 | 17.9998 | 606.5905
| 660 | 1105.9176 | 18.0477 | 624.6382
| 690 | 1112.5482 | 18.0698 | 642.708
| 720 | 1118.8978 | 18.0668 | 660.7748
| 750 | 1124.9891 | 18.0392 | 678.814
| 780 | 1130.8425 | 17.9875 | 696.8014
| 810 | 1136.4758 | 17.9121 | 714.7135
| 840 | 1141.9049 | 17.8136 | 732.5271
| 870 | 1147.1442 | 17.6924 | 750.2195
| 900 | 1152.2064 | 17.549 | 767.7685
| 930 | 1157.1032 | 17.3841 | 785.1525
| 960 | 1161.845 | 17.1982 | 802.3507
| 990 | 1166.4413 | 16.992 | 819.3427
| 1020 | 1170.9008 | 16.7663 | 836.1091
| 1050 | 1175.2315 | 16.522 | 852.6311
| 1080 | 1179.4404 | 16.26 | 868.891
| 1110 | 1183.5343 | 15.9811 | 884.8722
| 1140 | 1187.5194 | 15.6866 | 900.5588
| 1170 | 1191.4012 | 15.3776 | 915.9363
| 1200 | 1195.1849 | 15.0552 | 930.9915
| 1230 | 1198.8755 | 14.7207 | 945.7122
| 1260 | 1202.4773 | 14.3755 | 960.0878
| 1290 | 1205.9946 | 14.021 | 974.1087
| 1320 | 1209.4312 | 13.6584 | 987.7672
| 1350 | 1212.7907 | 13.2893 | 1001.0564
| 1380 | 1216.0766 | 12.915 | 1013.9715
| 1410 | 1219.2919 | 12.537 | 1026.5084
| 1440 | 1222.4397 | 12.1566 | 1038.665
| 1470 | 1225.5228 | 11.7752 | 1050.4401
| 1500 | 1228.5436 | 11.3941 | 1061.8342
| 1530 | 1231.5048 | 11.0145 | 1072.8487
| 1560 | 1234.4085 | 10.6378 | 1083.4865
| 1590 | 1237.2571 | 10.2649 | 1093.7513
| 1620 | 1240.0525 | 9.8969 | 1103.6482
| 1650 | 1242.7967 | 9.5348 | 1113.1831
| 1680 | 1245.4916 | 9.1795 | 1122.3626
| 1710 | 1248.1388 | 8.8318 | 1131.1944
| 1740 | 1250.7401 | 8.4922 | 1139.6866
| 1770 | 1253.297 | 8.1615 | 1147.8482
| 1800 | 1255.8109 | 7.8402 | 1155.6884
| 1830 | 1258.2834 | 7.5286 | 1163.2169
| 1860 | 1260.7158 | 7.2271 | 1170.444
| 1890 | 1263.1093 | 6.9359 | 1177.3799
| 1920 | 1265.4652 | 6.6552 | 1184.0352
| 1950 | 1267.7846 | 6.3852 | 1190.4204
| 1980 | 1270.0686 | 6.1258 | 1196.5462
| 2010 | 1272.3183 | 5.8771 | 1202.4232
| 2040 | 1274.5348 | 5.6389 | 1208.0621
| 2070 | 1276.7189 | 5.4111 | 1213.4732
| 2100 | 1278.8717 | 5.1936 | 1218.6668
| 2130 | 1280.994 | 4.9862 | 1223.653
| 2160 | 1283.0866 | 4.7885 | 1228.4415
| 2190 | 1285.1504 | 4.6005 | 1233.0419
| 2220 | 1287.1862 | 4.4217 | 1237.4636
| 2250 | 1289.1947 | 4.2518 | 1241.7154
| 2280 | 1291.1766 | 4.0906 | 1245.8061
| 2310 | 1293.1326 | 3.9378 | 1249.7439
| 2340 | 1295.0634 | 3.7929 | 1253.5368
| 2370 | 1296.9697 | 3.6557 | 1257.1925
| 2400 | 1298.852 | 3.5258 | 1260.7183
| 2430 | 1300.711 | 3.4029 | 1264.1212
| 2460 | 1302.5472 | 3.2867 | 1267.4079
| 2490 | 1304.3611 | 3.1767 | 1270.5846
| 2520 | 1306.1534 | 3.0728 | 1273.6574
| 2550 | 1307.9244 | 2.9746 | 1276.632
| 2580 | 1309.6748 | 2.8818 | 1279.5137
| 2610 | 1311.405 | 2.794 | 1282.3078
| 2640 | 1313.1154 | 2.7111 | 1285.0189
| 2670 | 1314.8065 | 2.6328 | 1287.6517
| 2700 | 1316.4787 | 2.5587 | 1290.2104
| 2730 | 1318.1325 | 2.4887 | 1292.6992
| 2760 | 1319.7682 | 2.4225 | 1295.1217
| 2790 | 1321.3863 | 2.3599 | 1297.4816
| 2820 | 1322.987 | 2.3006 | 1299.7822
| 2850 | 1324.5709 | 2.2445 | 1302.0267
| 2880 | 1326.1382 | 2.1914 | 1304.2181
| 2910 | 1327.6892 | 2.141 | 1306.3591
| 2940 | 1329.2244 | 2.0933 | 1308.4524
| 2970 | 1330.744 | 2.048 | 1310.5004
| 3000 | 1332.2483 | 2.005 | 1312.5054
| 3030 | 1333.7377 | 1.9642 | 1314.4696
Time | TS |  | Time | TS |  | Time | TS
(min) | (°F) |  | (min) | (°F) |  | (min) | (°F)
0.5 | 113.5278 |  | 17 | 1070.9263 | Failure of Beam | 34 | 1740.4418 | Failure of Beam
1 | 128.629 |  | 17.5 | 1100.666 | Failure of Beam | 34.5 | 1750.1818 | Failure of Beam
1.5 | 146.5901 |  | 18 | 1129.9339 | Failure of Beam | 35 | 1759.5302 | Failure of Beam
2 | 166.7595 |  | 18.5 | 1158.6999 | Failure of Beam | 35.5 | 1768.5053 | Failure of Beam
2.5 | 188.73 |  | 19 | 1186.9358 | Failure of Beam | 36 | 1777.1247 | Failure of Beam
3 | 212.216 |  | 19.5 | 1214.6154 | Failure of Beam | 36.5 | 1785.4055 | Failure of Beam
3.5 | 237.0024 |  | 20 | 1241.7147 | Failure of Beam | 37 | 1793.3645 | Failure of Beam
4 | 262.919 |  | 20.5 | 1268.212 | Failure of Beam | 37.5 | 1801.0178 | Failure of Beam
4.5 | 289.826 |  | 21 | 1294.088 | Failure of Beam | 38 | 1808.3809 | Failure of Beam
5 | 317.6058 |  | 21.5 | 1319.3257 | Failure of Beam | 38.5 | 1815.4689 | Failure of Beam
5.5 | 346.1564 |  | 22 | 1343.9109 | Failure of Beam | 39 | 1822.2962 | Failure of Beam
6 | 375.3884 |  | 22.5 | 1367.8316 | Failure of Beam | 39.5 | 1828.8765 | Failure of Beam
6.5 | 405.2216 |  | 23 | 1391.0786 | Failure of Beam | 40 | 1835.2229 | Failure of Beam
7 | 435.5834 |  | 23.5 | 1413.6452 | Failure of Beam | 40.5 | 1841.3482 | Failure of Beam
7.5 | 466.4068 |  | 24 | 1435.527 | Failure of Beam | 41 | 1847.2641 | Failure of Beam
8 | 497.6297 |  | 24.5 | 1456.7223 | Failure of Beam | 41.5 | 1852.9822 | Failure of Beam
8.5 | 529.1939 |  | 25 | 1477.2316 | Failure of Beam | 42 | 1858.5133 | Failure of Beam
9 | 561.044 |  | 25.5 | 1497.0577 | Failure of Beam | 42.5 | 1863.8676 | Failure of Beam
9.5 | 593.1274 |  | 26 | 1516.2057 | Failure of Beam | 43 | 1869.0547 | Failure of Beam
10 | 625.3933 |  | 26.5 | 1534.6824 | Failure of Beam | 43.5 | 1874.084 | Failure of Beam
10.5 | 657.793 |  | 27 | 1552.4968 | Failure of Beam | 44 | 1878.9641 | Failure of Beam
11 | 690.2787 |  | 27.5 | 1569.6596 | Failure of Beam | 44.5 | 1883.7031 | Failure of Beam
11.5 | 722.8044 |  | 28 | 1586.1827 | Failure of Beam | 45 | 1888.3088 | Failure of Beam
12 | 755.3246 |  | 28.5 | 1602.0799 | Failure of Beam | 45.5 | 1892.7885 | Failure of Beam
12.5 | 787.7951 |  | 29 | 1617.3659 | Failure of Beam | 46 | 1897.149 | Failure of Beam
13 | 820.1726 |  | 29.5 | 1632.0567 | Failure of Beam | 46.5 | 1901.3968 | Failure of Beam
13.5 | 852.4144 |  | 30 | 1646.169 | Failure of Beam | 47 | 1905.5379 | Failure of Beam
14 | 884.4788 |  | 30.5 | 1659.7205 | Failure of Beam | 47.5 | 1909.578 | Failure of Beam
14.5 | 916.3251 |  | 31 | 1672.7292 | Failure of Beam | 48 | 1913.5225 | Failure of Beam
15 | 947.9133 |  | 31.5 | 1685.2138 | Failure of Beam | 48.5 | 1917.3763 | Failure of Beam
15.5 | 979.2046 |  | 32 | 1697.1933 | Failure of Beam | 49 | 1921.1443 | Failure of Beam
16 | 1010.1613 | failure | 32.5 | 1708.6866 | Failure of Beam | 49.5 | 1924.8307 | Failure of Beam
16.5 | 1040.7469 | failure | 33 | 1719.7131 | Failure of Beam | 50 | 1928.4397 | Failure of Beam
17 | 1070.9263 | failure | 33.5 | 1730.2918 | Failure of Beam | 50.5 | 1931.9752 | Failure of Beam
The Failure Temperature for Steel Beams is Assumed at 1000 °F (538 °C)
The above calculations are based on principles developed in the Structural Design for Fire Safety by
Buchanan, 2001.
Calculations are based on certain assumptions and have inherent limitations. The results
of such calculations may or may not have reasonable predictive capabilities for a given
situation, and should only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision | [5 empty] | Date
1805.0 | Original issue with final text. | [5 empty] | January 2005
Note on I14: This default value (600.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on I15: This default value (7850.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on I17: This default value (5.669E-08) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on I19: This default value (345.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on I16: This default value (25.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Column
CHAPTER 17. ESTIMATING FIRE RESISTANCE TIME OF UNPROTECTED
STEEL COLUMNS (QUASI-STEADY-STATE APPROACH)
Version 1805.0
The following calculations estimate the fire resistance time for unprotected structural steel columns.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Column and Insulation Selected.
All subsequent output values are calculated by the spreadsheet, and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| The Ratio of Heated Surface Area to Volume of Column (both per unit length) (F/V) | [6 empty] | 140.726 | m-1
| Flame Emissivity (ef) | [6 empty] | 0.3
| Specific Heat of Steel (cs) | [6 empty] | 600 | J/kg-K
| Density of Steel (rs) | [6 empty] | 7850 | kg/m3
| Convective heat Transfer Coefficient (hc) | [6 empty] | 25 | W/m2-K
| Stefan Boltzmann Constant | [6 empty] | 5.669e-08 | W/m2-K4
| Ambient Air Temperature (Ta) | [6 empty] | 25 | °C | 298.15 | K
| Constant (C1) | [6 empty] | 345
SECTIONAL FACTORS FOR STEEL COLUMNS
| Structural Shape | F/V Ratio
| W Shapes | (m-1)
| 36x300 | 61.623
| 36x280 | 65.768 |  |  |  | Emmissivity
| 36x260 | 70.526 |  |  |  | 0.3
| 36x245 | 74.59 |  |  |  | 0.5
| 36x230 | 79.299 |  |  |  | 0.7
| 36x210 | 76.727 |  |  |  | User Specified (Enter Value)
| 36x194 | 82.822
| 36x182 | 87.782
| 36x170 | 93.78
| 36x160 | 99.447
| 36x150 | 105.417
| 36x135 | 116.722
| 33x241 | 72.265
| 33x221 | 78.455
| 33x201 | 85.875
| 33x152 | 98.619
| 33x141 | 105.552
| 33x130 | 114.163
| 33x118 | 125.417
| 30x211 | 76.676
| 30x191 | 84.284
| 30x173 | 92.62
| 30x132 | 102.797
| 30x124 | 109.19
| 30x116 | 116.119
| 30x108 | 124.78
| 30x99 | 135.374
| 27x178 | 83.189
| 27x161 | 91.315
| 27x146 | 100.407
| 27x114 | 110.142
| 27x102 | 122.323
| 27x94 | 131.925
| 27x84 | 146.59
| 24x162 | 82.875
| 24x146 | 91.357
| 24x131 | 101.411
| 24x117 | 112.869
| 24x104 | 126.242
| 24x94 | 119.176
| 24x84 | 132.838
| 24x76 | 145.74
| 24x68 | 161.574
| 24x62 | 161.763
| 24x55 | 180.738
| 21x147 | 84.5
| 21x132 | 93.473
| 21x122 | 100.586
| 21x111 | 109.899
| 21x101 | 120.066
| 21x93 | 109.256
| 21x83 | 121.918
| 21x73 | 136.88
| 21x68 | 146.614
| 21x62 | 159.503
| 21x57 | 159.154
| 21x50 | 179.495
| 21x44 | 201.757
| 18x119 | 91.628
| 18x106 | 102.641
| 18x97 | 111.466
| 18x86 | 124.77
| 18x76 | 140.726
| 18x71 | 125.852
| 18x65 | 136.373
| 18x60 | 147.302
| 18x55 | 159.327
| 18x50 | 174.755
| 18x46 | 173.928
| 18x40 | 197.618
| 18x35 | 224.753
| 16x100 | 99.724
| 16x89 | 111.063
| 16x77 | 127.709
| 16x67 | 145.509
| 16x57 | 141.732
| 16x50 | 160.801
| 16x45 | 176.751
| 16x40 | 198.152
| 16x36 | 219.395
| 16x31 | 230.134
| 16x26 | 271.079
| 14x730 | 20.19
| 14x665 | 21.738
| 14x605 | 23.514
| 14x550 | 25.401
| 14x500 | 27.548
| 14x455 | 29.777
| 14x426 | 31.613
| 14x398 | 33.448
| 14x370 | 35.552
| 14x342 | 37.912
| 14x311 | 41.498
| 14x283 | 45.061
| 14x257 | 49.155
| 14x233 | 53.739
| 14x211 | 58.852
| 14x193 | 63.782
| 14x176 | 69.452
| 14x159 | 76.796
| 14x145 | 83.166
| 14x132 | 88.207
| 14x120 | 96.429
| 14x109 | 105.819
| 14x99 | 115.824
| 14x90 | 126.638
| 14x82 | 111.282
| 14x74 | 122.3
| 14x68 | 132.657
| 14x61 | 147.385
| 14x53 | 149.758
| 14x48 | 164.796
| 14x43 | 183.383
| 14x38 | 192.14
| 14x34 | 214.055
| 14x30 | 240.491
| 14x26 | 242.722
| 14x22 | 285.236
| 12x336 | 33.325
| 12x305 | 36.176
| 12x279 | 39.034
| 12x252 | 42.531
| 12x230 | 46.005
| 12x210 | 49.831
| 12x190 | 54.554
| 12x170 | 60.173
| 12x152 | 66.586
| 12x136 | 73.846
| 12x120 | 82.644
| 12x106 | 92.671
| 12x96 | 101.86
| 12x87 | 111.543
| 12x79 | 122.421
| 12x72 | 133.97
| 12x65 | 147.298
| 12x58 | 147.522
| 12x53 | 160.029
| 12x50 | 149.874
| 12x45 | 165.921
| 12x40 | 184.539
| 12x35 | 193.563
| 12x30 | 225.023
| 12x26 | 257.012
| 12x22 | 244.362
| 12x19 | 281.811
| 12x16 | 330.174
| 12x14 | 371.934
| 10x112 | 75.234
| 10x100 | 83.293
| 10x88 | 93.531
| 10x77 | 106.09
| 10x68 | 118.858
| 10x60 | 134.037
| 10x54 | 148.41
| 10x49 | 162.073
| 10x45 | 152.685
| 10x39 | 175.111
| 10x33 | 205.649
| 10x30 | 194.089
| 10x26 | 223.597
| 10x22 | 260
| 10x19 | 252.613
| 10x17 | 282.297
| 10x15 | 317.103
| 10x12 | 391.476
| 8x67 | 99.884
| 8x58 | 113.644
| 8x48 | 135.813
| 8x40 | 161.72
| 8x35 | 182.371
| 8x31 | 204.44
| 8x28 | 198.95
| 8x24 | 229.937
| 8x21 | 237.371
| 8x18 | 275.591
| 8x15 | 281.886
| 8x13 | 323.163
| 8x10 | 414.982
| 6x25 | 195.456
| 6x20 | 241.184
| 6x15 | 315.316
| 6x16 | 233.895
| 6x12 | 306.088
| 6x9 | 399.871
| 5x19 | 212.343
| 5x16 | 248.503
| 4x13 | 247
| User Specified Value | Enter Value
Select Column
Scroll to desired column size then Click on selection
EMISSIVITY VALUES FOR DIFFERENT CONSTRUCTION TYPES
|  |  | Emissivity | Select Flame Emissivity, ef
Type of Construction |  |  | ef
Scroll to desired construction type then Click on selection
Column outside façade |  |  | 0.3
Floor girder with floor slab of concrete, only the
underside of the bottom flange being directly |  |  | 0.3
exposed to fire
Floor girder with floor slab on the top flange
Girder of I section for which the width-depth |  |  | 0.5
ratio is not less than 0.5
Floor girder with floor slab on the top flange
Girder of I section for which the width-depth |  |  | 0.7
ratio is less than 0.5
Floor girder with floor slab on the top flange
Box girder and lattice |  |  | 0.7
Column exposed to fire on all sides |  |  | 0.7
User Specificed Value |  |  | Enter Value
ESTIMATING FIRE RESISTANCE TIME OF UNPROTECTED STEEL COLUMNS USING
QUASI-STEADY-STATE APPROACH
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 179.
DTs = F/V 1/rscs (hc (Tf - Ts) + s e (Tf4 - Ts4)) Dt
| Where | DTs = temperature rise in steel (°F)
F/V = ratio of heated surface area to volume of column (both per unit length) (m-1)
rs = density of steel (kg/m3)
cs = specific heat of steel (J/kg-K)
hc = convective heat transfer coefficient (W/m2-K)
s = Stefan Boltzmann constant (kW/m2-K4)
e = flame emissivity
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
The Maximum Allowable Time Step
| Dt = | 30 | sec
Calculate
For ASTM E 119 exposure, Tf at any time, t, is given by the following expression
| Tf = C1 LOG (0.133 t + 1) + Ta |  | (Refecrece: SFPE Handbook 3rd Edition, p. 4-223)
| Where | Tf = fire exposure temperature (°F)
|  | C2 = constant = 620 |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | t = time step (sec) |  |  | carbon steel structural members begin to fail. Predicted
|  | Ta = ambient air temperature (°F) |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
DTs1 = F/V 1/rscs (hc (C1 LOG (0.133 t1 + 1) +Ta) - Ts0) + s e ((C1 LOG (0.133 t1 + 1) +Ta)4 - Ts04)) Dt
| Where | t1 = Dt/2
Ts0 = initial steel temperature (°F)
DTs2 = F/V 1/rscs (hc (C1 LOG (0.133 t2 + 1) +Ta) - Ts) + s e ((C1 LOG (0.133 t2 + 1) +Ta)4 - Ts4)) Dt
| Where | t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
| time | Tf | DTS | TS
| (s) | (k) |  | (K)
| 30 | 656.474 | 10.7403 | 308.8903
| 60 | 753.3134 | 14.7293 | 323.6196
| 90 | 811.6513 | 17.3847 | 341.0042
| 120 | 853.5337 | 19.3696 | 360.3738
| 150 | 886.2299 | 20.9301 | 381.3039
| 180 | 913.0536 | 22.1882 | 403.4921
| 210 | 935.7965 | 23.2145 | 426.7066
| 240 | 955.5379 | 24.0535 | 450.7601
| 270 | 972.9784 | 24.7349 | 475.4949
| 300 | 988.5988 | 25.2794 | 500.7743
| 330 | 1002.7434 | 25.7018 | 526.4762
| 360 | 1015.6672 | 26.0131 | 552.4892
| 390 | 1027.5642 | 26.2211 | 578.7103
| 420 | 1038.5856 | 26.332 | 605.0423
| 450 | 1048.8515 | 26.3506 | 631.393
| 480 | 1058.459 | 26.2809 | 657.6739
| 510 | 1067.4873 | 26.1263 | 683.8002
| 540 | 1076.0024 | 25.8899 | 709.6901
| 570 | 1084.0595 | 25.5751 | 735.2652
| 600 | 1091.7054 | 25.1853 | 760.4505
| 630 | 1098.9799 | 24.7244 | 785.1749
| 660 | 1105.9176 | 24.1966 | 809.3715
| 690 | 1112.5482 | 23.6069 | 832.9784
| 720 | 1118.8978 | 22.9607 | 855.9391
| 750 | 1124.9891 | 22.264 | 878.203
| 780 | 1130.8425 | 21.5233 | 899.7263
| 810 | 1136.4758 | 20.7455 | 920.4718
| 840 | 1141.9049 | 19.938 | 940.4099
| 870 | 1147.1442 | 19.1082 | 959.5181
| 900 | 1152.2064 | 18.2636 | 977.7817
| 930 | 1157.1032 | 17.4115 | 995.1931
| 960 | 1161.845 | 16.5589 | 1011.7521
| 990 | 1166.4413 | 15.7127 | 1027.4648
| 1020 | 1170.9008 | 14.879 | 1042.3437
| 1050 | 1175.2315 | 14.0632 | 1056.4069
| 1080 | 1179.4404 | 13.2702 | 1069.6771
| 1110 | 1183.5343 | 12.5042 | 1082.1813
| 1140 | 1187.5194 | 11.7685 | 1093.9498
| 1170 | 1191.4012 | 11.0657 | 1105.0155
| 1200 | 1195.1849 | 10.3977 | 1115.4132
| 1230 | 1198.8755 | 9.7658 | 1125.179
| 1260 | 1202.4773 | 9.1705 | 1134.3495
| 1290 | 1205.9946 | 8.612 | 1142.9615
| 1320 | 1209.4312 | 8.0899 | 1151.0515
| 1350 | 1212.7907 | 7.6034 | 1158.6549
| 1380 | 1216.0766 | 7.1514 | 1165.8063
| 1410 | 1219.2919 | 6.7326 | 1172.539
| 1440 | 1222.4397 | 6.3455 | 1178.8844
| 1470 | 1225.5228 | 5.9882 | 1184.8727
| 1500 | 1228.5436 | 5.6592 | 1190.5319
| 1530 | 1231.5048 | 5.3566 | 1195.8885
| 1560 | 1234.4085 | 5.0786 | 1200.9672
| 1590 | 1237.2571 | 4.8235 | 1205.7907
| 1620 | 1240.0525 | 4.5894 | 1210.3801
| 1650 | 1242.7967 | 4.3748 | 1214.7549
| 1680 | 1245.4916 | 4.178 | 1218.9329
| 1710 | 1248.1388 | 3.9976 | 1222.9305
| 1740 | 1250.7401 | 3.832 | 1226.7625
| 1770 | 1253.297 | 3.6801 | 1230.4425
| 1800 | 1255.8109 | 3.5405 | 1233.983
| 1830 | 1258.2834 | 3.4121 | 1237.3951
| 1860 | 1260.7158 | 3.2939 | 1240.689
| 1890 | 1263.1093 | 3.1849 | 1243.8739
| 1920 | 1265.4652 | 3.0843 | 1246.9583
| 1950 | 1267.7846 | 2.9913 | 1249.9496
| 1980 | 1270.0686 | 2.9051 | 1252.8547
| 2010 | 1272.3183 | 2.825 | 1255.6797
| 2040 | 1274.5348 | 2.7506 | 1258.4303
| 2070 | 1276.7189 | 2.6812 | 1261.1115
| 2100 | 1278.8717 | 2.6164 | 1263.7278
| 2130 | 1280.994 | 2.5557 | 1266.2835
| 2160 | 1283.0866 | 2.4987 | 1268.7822
| 2190 | 1285.1504 | 2.4451 | 1271.2274
| 2220 | 1287.1862 | 2.3947 | 1273.622
| 2250 | 1289.1947 | 2.347 | 1275.969
| 2280 | 1291.1766 | 2.3019 | 1278.2709
| 2310 | 1293.1326 | 2.2591 | 1280.53
| 2340 | 1295.0634 | 2.2184 | 1282.7484
| 2370 | 1296.9697 | 2.1797 | 1284.928
| 2400 | 1298.852 | 2.1427 | 1287.0707
| 2430 | 1300.711 | 2.1074 | 1289.1781
| 2460 | 1302.5472 | 2.0736 | 1291.2517
| 2490 | 1304.3611 | 2.0411 | 1293.2928
| 2520 | 1306.1534 | 2.01 | 1295.3028
Time | TS |  | Time | TS |  | Time | TS
(min) | (°F) |  | (min) | (°F) |  | (min) | (°F)
0.5 | 121.9325 |  | 14.5 | 1293.0626 | Failure of Column | 28.5 | 1767.2049 | Failure of Column
1 | 148.4452 |  | 15 | 1325.937 | Failure of Column | 29 | 1774.1025 | Failure of Column
1.5 | 179.7376 |  | 15.5 | 1357.2776 | Failure of Column | 29.5 | 1780.7266 | Failure of Column
2 | 214.6029 |  | 16 | 1387.0837 | Failure of Column | 30 | 1787.0994 | Failure of Column
2.5 | 252.277 |  | 16.5 | 1415.3666 | Failure of Column | 30.5 | 1793.2412 | Failure of Column
3 | 292.2158 |  | 17 | 1442.1487 | Failure of Column | 31 | 1799.1702 | Failure of Column
3.5 | 334.0019 |  | 17.5 | 1467.4625 | Failure of Column | 31.5 | 1804.9031 | Failure of Column
4 | 377.2981 |  | 18 | 1491.3488 | Failure of Column | 32 | 1810.4549 | Failure of Column
4.5 | 421.8209 |  | 18.5 | 1513.8564 | Failure of Column | 32.5 | 1815.8393 | Failure of Column
5 | 467.3238 |  | 19 | 1535.0397 | Failure of Column | 33 | 1821.0684 | Failure of Column
5.5 | 513.5871 |  | 19.5 | 1554.9579 | Failure of Column | 33.5 | 1826.1535 | Failure of Column
6 | 560.4106 |  | 20 | 1573.6738 | Failure of Column | 34 | 1831.1046 | Failure of Column
6.5 | 607.6086 |  | 20.5 | 1591.2522 | Failure of Column | 34.5 | 1835.9307 | Failure of Column
7 | 655.0062 |  | 21 | 1607.7591 | Failure of Column | 35 | 1840.6401 | Failure of Column
7.5 | 702.4373 |  | 21.5 | 1623.2608 | Failure of Column | 35.5 | 1845.2403 | Failure of Column
8 | 749.743 |  | 22 | 1637.8226 | Failure of Column | 36 | 1849.738 | Failure of Column
8.5 | 796.7703 |  | 22.5 | 1651.5088 | Failure of Column | 36.5 | 1854.1392 | Failure of Column
9 | 843.3721 |  | 23 | 1664.3814 | Failure of Column | 37 | 1858.4496 | Failure of Column
9.5 | 889.4073 |  | 23.5 | 1676.5001 | Failure of Column | 37.5 | 1862.6742 | Failure of Column
10 | 934.7409 |  | 24 | 1687.9219 | Failure of Column | 38 | 1866.8176 | Failure of Column
10.5 | 979.2448 |  | 24.5 | 1698.7008 | Failure of Column | 38.5 | 1870.884 | Failure of Column
11 | 1022.7987 | Failure of Column | 25 | 1708.8874 | Failure of Column | 39 | 1874.8771 | Failure of Column
11.5 | 1065.2911 | Failure of Column | 25.5 | 1718.5293 | Failure of Column | 39.5 | 1878.8005 | Failure of Column
12 | 1106.6203 | Failure of Column | 26 | 1727.6709 | Failure of Column | 40 | 1882.6573 | Failure of Column
12.5 | 1146.6954 | Failure of Column | 26.5 | 1736.3532 | Failure of Column | 40.5 | 1886.4506 | Failure of Column
13 | 1185.4373 | Failure of Column | 27 | 1744.6142 | Failure of Column | 41 | 1890.1831 | Failure of Column
13.5 | 1222.7793 | Failure of Column | 27.5 | 1752.4888 | Failure of Column | 41.5 | 1893.8571 | Failure of Column
14 | 1258.6677 | Failure of Column | 28 | 1760.0093 | Failure of Column | 42 | 1897.4751 | Failure of Column
The Failure Temperature for Steel Beams is Assumed at 1000 °F (538 °C)
The above calculations are based on principles developed in the Structural Design for Fire Safety by
Buchanan, 2001.
Calculations are based on certain assumptions and have inherent limitations. The results
of such calculations may or may not have reasonable predictive capabilities for a given
situation, and should only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision | [5 empty] | Date
1805.0 | Original issue with final text. | [5 empty] | January 2005
Note on I14: This default value (600) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on I15: This default value (7850) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on I17: This default value (5.669E-08) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on I19: This default value (345.0) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on I16: This default value (25) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Data
SECTIONAL FACTORS FOR STEEL MEMBERS
| BEAMS |  | COLUMNS
| Structural Shape | F/V Ratio | Structural Shape | F/V Ratio
| W Shapes | (m-1) | W Shapes | (m-1)
| 36x300 | 54.1974 | 36x300 | 61.623
| 36x280 | 57.8391 | 36x280 | 65.768
| 36x260 | 62.0092 | 36x260 | 70.526
| 36x245 | 65.5749 | 36x245 | 74.59
| 36x230 | 69.7072 | 36x230 | 79.299
| 36x210 | 68.9677 | 36x210 | 76.727
| 36x194 | 74.4543 | 36x194 | 82.822
| 36x182 | 78.9128 | 36x182 | 87.782
| 36x170 | 84.3071 | 36x170 | 93.78
| 36x160 | 89.3952 | 36x160 | 99.447
| 36x150 | 94.751 | 36x150 | 105.417
| 36x135 | 104.8712 | 36x135 | 116.722
| 33x241 | 63.4586 | 33x241 | 72.265
| 33x221 | 68.8825 | 33x221 | 78.455
| 33x201 | 75.386 | 33x201 | 85.875
| 33x152 | 88.4329 | 33x152 | 98.619
| 33x141 | 94.6349 | 33x141 | 105.552
| 33x130 | 102.3314 | 33x130 | 114.163
| 33x118 | 112.3919 | 33x118 | 125.417
| 30x211 | 67.0847 | 30x211 | 76.676
| 30x191 | 73.7294 | 30x191 | 84.284
| 30x173 | 81.007 | 30x173 | 92.62
| 30x132 | 92.125 | 30x132 | 102.797
| 30x124 | 97.8481 | 30x124 | 109.19
| 30x116 | 104.0372 | 30x116 | 116.119
| 30x108 | 111.77 | 30x108 | 124.78
| 30x99 | 121.2355 | 30x99 | 135.374
| 27x178 | 72.5862 | 27x178 | 83.189
| 27x161 | 79.6704 | 27x161 | 91.315
| 27x146 | 87.5915 | 27x146 | 100.407
| 27x114 | 98.3077 | 27x114 | 110.142
| 27x102 | 109.1798 | 27x102 | 122.323
| 27x94 | 117.7265 | 27x94 | 131.925
| 27x84 | 130.7785 | 27x84 | 146.59
| 24x162 | 72.1826 | 24x162 | 82.875
| 24x146 | 79.5459 | 24x146 | 91.357
| 24x131 | 88.2657 | 24x131 | 101.411
| 24x117 | 98.2192 | 24x117 | 112.869
| 24x104 | 109.8374 | 24x104 | 126.242
| 24x94 | 106.2921 | 24x94 | 119.176
| 24x84 | 118.4609 | 24x84 | 132.838
| 24x76 | 129.9388 | 24x76 | 145.74
| 24x68 | 144.0142 | 24x68 | 161.574
| 24x62 | 146.5346 | 24x62 | 161.763
| 24x55 | 163.7139 | 24x55 | 180.738
| 21x147 | 73.0989 | 21x147 | 84.5
| 21x132 | 80.8507 | 21x132 | 93.473
| 21x122 | 86.998 | 21x122 | 100.586
| 21x111 | 95.042 | 21x111 | 109.899
| 21x101 | 103.8287 | 21x101 | 120.066
| 21x93 | 97.1129 | 21x93 | 109.256
| 21x83 | 108.3811 | 21x83 | 121.918
| 21x73 | 121.6902 | 21x73 | 136.88
| 21x68 | 130.3346 | 21x68 | 146.614
| 21x62 | 141.7753 | 21x62 | 159.503
| 21x57 | 143.7126 | 21x57 | 159.154
| 21x50 | 162.0065 | 21x50 | 179.495
| 21x44 | 182.0715 | 21x44 | 201.757
| 18x119 | 78.9925 | 18x119 | 91.628
| 18x106 | 88.4624 | 18x106 | 102.641
| 18x97 | 96.0699 | 18x97 | 111.466
| 18x86 | 107.513 | 18x86 | 124.77
| 18x76 | 121.244 | 18x76 | 140.726
| 18x71 | 111.4003 | 18x71 | 125.852
| 18x65 | 120.728 | 18x65 | 136.373
| 18x60 | 130.4134 | 18x60 | 147.302
| 18x55 | 141.0275 | 18x55 | 159.327
| 18x50 | 154.6816 | 18x50 | 174.755
| 18x46 | 156.2555 | 18x46 | 173.928
| 18x40 | 177.549 | 18x40 | 197.618
| 18x35 | 201.8194 | 18x35 | 224.753
| 16x100 | 85.7638 | 16x100 | 99.724
| 16x89 | 95.4875 | 16x89 | 111.063
| 16x77 | 109.7746 | 16x77 | 127.709
| 16x67 | 125.055 | 16x67 | 145.509
| 16x57 | 125.0469 | 16x57 | 141.732
| 16x50 | 141.8662 | 16x50 | 160.801
| 16x45 | 155.9262 | 16x45 | 176.751
| 16x40 | 174.8132 | 16x40 | 198.152
| 16x36 | 193.4519 | 16x36 | 219.395
| 16x31 | 206.2828 | 16x31 | 230.134
| 16x26 | 242.8847 | 16x26 | 271.079
| 14x730 | 16.9145 | 14x730 | 20.19
| 14x665 | 18.1926 | 14x665 | 21.738
| 14x605 | 19.6618 | 14x605 | 23.514
| 14x550 | 21.221 | 14x550 | 25.401
| 14x500 | 22.9927 | 14x500 | 27.548
| 14x455 | 24.8311 | 14x455 | 29.777
| 14x426 | 26.3543 | 14x426 | 31.613
| 14x398 | 27.8653 | 14x398 | 33.448
| 14x370 | 29.6016 | 14x370 | 35.552
| 14x342 | 31.535 | 14x342 | 37.912
| 14x311 | 34.507 | 14x311 | 41.498
| 14x283 | 37.4465 | 14x283 | 45.061
| 14x257 | 40.8256 | 14x257 | 49.155
| 14x233 | 44.606 | 14x233 | 53.739
| 14x211 | 48.8189 | 14x211 | 58.852
| 14x193 | 52.8931 | 14x193 | 63.782
| 14x176 | 57.5578 | 14x176 | 69.452
| 14x159 | 63.5974 | 14x159 | 76.796
| 14x145 | 68.8746 | 14x145 | 83.166
| 14x132 | 73.2659 | 14x132 | 88.207
| 14x120 | 80.0674 | 14x120 | 96.429
| 14x109 | 87.8506 | 14x109 | 105.819
| 14x99 | 96.1185 | 14x99 | 115.824
| 14x90 | 105.0661 | 14x90 | 126.638
| 14x82 | 94.7332 | 14x82 | 111.282
| 14x74 | 104.114 | 14x74 | 122.3
| 14x68 | 112.9035 | 14x68 | 132.657
| 14x61 | 125.4014 | 14x61 | 147.385
| 14x53 | 129.4165 | 14x53 | 149.758
| 14x48 | 142.3745 | 14x48 | 164.796
| 14x43 | 158.4021 | 14x43 | 183.383
| 14x38 | 168.3422 | 14x38 | 192.14
| 14x34 | 187.5 | 14x34 | 214.055
| 14x30 | 210.5521 | 14x30 | 240.491
| 14x26 | 216.9962 | 14x26 | 242.722
| 14x22 | 254.9046 | 14x22 | 285.236
| 12x336 | 27.9914 | 12x336 | 33.325
| 12x305 | 30.3602 | 12x305 | 36.176
| 12x279 | 32.7171 | 12x279 | 39.034
| 12x252 | 35.6217 | 12x252 | 42.531
| 12x230 | 38.5065 | 12x230 | 46.005
| 12x210 | 41.6826 | 12x210 | 49.831
| 12x190 | 45.6143 | 12x190 | 54.554
| 12x170 | 50.2756 | 12x170 | 60.173
| 12x152 | 55.5937 | 12x152 | 66.586
| 12x136 | 61.6107 | 12x136 | 73.846
| 12x120 | 68.9032 | 12x120 | 82.644
| 12x106 | 77.2512 | 12x106 | 92.671
| 12x96 | 84.883 | 12x96 | 101.86
| 12x87 | 92.8965 | 12x87 | 111.543
| 12x79 | 101.921 | 12x79 | 122.421
| 12x72 | 111.505 | 12x72 | 133.97
| 12x65 | 122.5626 | 12x65 | 147.298
| 12x58 | 124.34 | 12x58 | 147.522
| 12x53 | 134.8047 | 12x53 | 160.029
| 12x50 | 128.234 | 12x50 | 149.874
| 12x45 | 141.9262 | 12x45 | 165.921
| 12x40 | 157.8306 | 12x40 | 184.539
| 12x35 | 168.4886 | 12x35 | 193.563
| 12x30 | 195.8202 | 12x30 | 225.023
| 12x26 | 223.6118 | 12x26 | 257.012
| 12x22 | 219.877 | 12x22 | 244.362
| 12x19 | 253.5023 | 12x19 | 281.811
| 12x16 | 296.822 | 12x16 | 330.174
| 12x14 | 334.3618 | 12x14 | 371.934
| 10x112 | 62.7707 | 10x112 | 75.234
| 10x100 | 69.4467 | 10x100 | 83.293
| 10x88 | 77.9269 | 10x88 | 93.531
| 10x77 | 88.3388 | 10x77 | 106.09
| 10x68 | 98.9173 | 10x68 | 118.858
| 10x60 | 111.4889 | 10x60 | 134.037
| 10x54 | 123.4177 | 10x54 | 148.41
| 10x49 | 134.7332 | 10x49 | 162.073
| 10x45 | 128.9444 | 10x45 | 152.685
| 10x39 | 147.7747 | 10x39 | 175.111
| 10x33 | 173.3743 | 10x33 | 205.649
| 10x30 | 168.2136 | 10x30 | 194.089
| 10x26 | 193.7463 | 10x26 | 223.597
| 10x22 | 225.1192 | 10x22 | 260
| 10x19 | 224.4515 | 10x19 | 252.613
| 10x17 | 250.6588 | 10x17 | 282.297
| 10x15 | 281.3934 | 10x15 | 317.103
| 10x12 | 347.4354 | 10x12 | 391.476
| 8x67 | 83.3367 | 8x67 | 99.884
| 8x58 | 94.7184 | 8x58 | 113.644
| 8x48 | 113.168 | 8x48 | 135.813
| 8x40 | 134.5649 | 8x40 | 161.72
| 8x35 | 151.7048 | 8x35 | 182.371
| 8x31 | 169.964 | 8x31 | 204.44
| 8x28 | 167.7643 | 8x28 | 198.95
| 8x24 | 193.8198 | 8x24 | 229.937
| 8x21 | 203.689 | 8x21 | 237.371
| 8x18 | 236.2953 | 8x18 | 275.591
| 8x15 | 246.2847 | 8x15 | 281.886
| 8x13 | 282.1522 | 8x13 | 323.163
| 8x10 | 362.5771 | 8x10 | 414.982
| 6x25 | 162.8441 | 6x25 | 195.456
| 6x20 | 200.8075 | 6x20 | 241.184
| 6x15 | 262.0821 | 6x15 | 315.316
| 6x16 | 200.4219 | 6x16 | 233.895
| 6x12 | 261.7278 | 6x12 | 306.088
| 6x9 | 341.9908 | 6x9 | 399.871
| 5x19 | 176.5968 | 5x19 | 212.343
| 5x16 | 206.4405 | 5x16 | 248.503
| 4x13 | 205 | 4x13
| User Specified Value | Enter Value | User Specified Value | Enter Value