## Sheet1
2002-04-04 |  |  |  | 8 GeV linac cryogenic heat load summary
compiled by Tom Peterson | [5 empty] | Heat load (Watts)
(No uncertainty margin or overcapacity factor is included here. These are just "best estimates".)
Item |  | Low beta (805 MHz) |  |  |  | Medium beta (805 MHz) |  |  |  | High beta (805 MHz) |  |  |  | TESLA (1207.5 MHz) |  |  | Notes
| qty | 2.1 K | 6 - 8 K | 50 - 59 K | qty | 2.1 K | 6 K - 8 K | 50 - 59 K | qty | 2.1 K | 6 - 8 K | 50 - 59 K | qty | 2.1 K | 6 - 8 K | 50 - 59 K
STATIC HEAT
Module, each | 1 | 4 | 13 | 78 | 1 | 4 | 13 | 78 | 1 | 4 | 13 | 78 | 1 | 4 | 13 | 78 | All: TTF measured
Modules, total | 2 | 8 | 26 | 156 | 3 | 12 | 39 | 234 | 7 | 28 | 91 | 546 | 36 | 144 | 468 | 2808
Input coupler, each | 1 | 0.82 | 2.79 | 9.8 | 1 | 0.82 | 2.79 | 9.8 | 1 | 0.82 | 2.79 | 9.8
Input couplers, module | 8 | 6.56 | 22.32 | 78.4 | 8 | 6.56 | 22.32 | 78.4 | 8 | 6.56 | 22.32 | 78.4 | 8 | 0.44 | 1.37 | 14.32 | 1207.5 MHz: TESLA TDR static x 2/3
Input couplers, total | 2 | 13.12 | 44.64 | 156.8 | 3 | 19.68 | 66.96 | 235.2 | 7 | 45.92 | 156.24 | 548.8 | 36 | 15.84 | 49.32 | 515.52 | 805 MHz: Roger Rabehl Calc
HTS lead pair | 1 | 0.1 | 0 | 13 | 1 | 0.1 | 0 | 13 | 1 | 0.1 | 0 | 13 | 1 | 0.1 | 0 | 13 | TESLA TDR 100 amp HTS lead numbers
HTS lead pairs, module | 9 | 0.9 | 0 | 117 | 5 | 0.5 | 0 | 65 | 3 | 0.3 | 0 | 39 | 2 | 0.2 | 0 | 26 | One pair per quad
HTS lead pairs, total | 18 | 1.8 | 0 | 234 | 15 | 1.5 | 0 | 195 | 21 | 2.1 | 0 | 273 | 72 | 7.2 | 0 | 936
Total Static Heat |  | 22.92 | 70.64 | 546.8 |  | 33.18 | 105.96 | 664.2 |  | 76.02 | 247.24 | 1367.8 |  | 167.04 | 517.32 | 4259.52
DYNAMIC HEATING
Module, each | 1 | 5.8 | 0 | 0 | 1 | 5.8 | 0 | 0 | 1 | 5.8 | 0 | 0 | 1 | 6.7 | 0 | 0 | 1207.5 MHz: TESLA x 2 x 2/3
Modules, total | 2 | 11.6 | 0 | 0 | 3 | 17.4 | 0 | 0 | 7 | 40.6 | 0 | 0 | 36 | 241.2 | 0 | 0 | 805 MHz: EES model
HOM per module |  | 2.72 | 6.93 | 37.5 |  | 2.72 | 6.93 | 37.5 |  | 2.72 | 6.93 | 37.5 |  | 2.72 | 6.93 | 37.5 | All: TESLA TDR (static + 2 x dyn) x 2/3
HOM total | 2 | 5.44 | 13.86 | 75 | 3 | 8.16 | 20.79 | 112.5 | 7 | 19.04 | 48.51 | 262.5 | 36 | 97.92 | 249.48 | 1350
TOTAL HEAT
Input coupler, each | 1 | 0.85 | 2.85 | 9.94 | 1 | 0.85 | 2.85 | 9.94 | 1 | 0.85 | 2.85 | 9.94
Input couplers, module | 8 | 6.8 | 22.8 | 79.52 | 8 | 6.8 | 22.8 | 79.52 | 8 | 6.8 | 22.8 | 79.52 | 8 | 0.69 | 2.95 | 93.52 | TESLA: TDR (static + 2 x dynamic) x 2/3
Input couplers, total | 2 | 13.6 | 45.6 | 159.04 | 3 | 20.4 | 68.4 | 238.56 | 7 | 47.6 | 159.6 | 556.64 | 36 | 24.84 | 106.2 | 3366.72 | 805 MHz: Roger Rabehl calc (+ SNS info)
Module, each |  | 16.6 | 35.8 | 157.52 |  | 16.6 | 35.8 | 157.52 |  | 16.6 | 35.8 | 157.52 |  | 11.39 | 15.95 | 171.52
Modules, total |  | 40.44 | 85.46 | 624.04 |  | 59.46 | 128.19 | 780.06 |  | 137.34 | 299.11 | 1638.14 |  | 515.16 | 823.68 | 8460.72
OTHER STUFF
Debuncher module | 1 | 4 | 13 | 78 |  | TTF, static only
Test stand | 1 | 10 | 20 | 200 |  | guestimate
Feed box | 1 | 10 | 40 | 300 |  | guestimate
Transfer lines | 250 m | 1.5 | 37 | 500 |  | Bill S. CKM est scaled
End boxes | 4 | 2 | 30 | 300 |  | guestimate
System total static heat |  | 326.66 | 1081.16 | 8216.32
System Total Heat |  | 779.9 | 1476.44 | 12880.96