## summary data
Plant name | Unit name | Boiler/NOx type | PM control | SOx control | name of fuel 1 | average Hg in fuel (ppmw) | name of fuel 2 | average Hg in fuel (ppmw) | Fuel in test | T control inlet (C) | Cl in test coal (ppm) | Hg in test coal (ppm) | Hg out furnace/ Hg in coal | lb Hg/TBtu out furnace | F factor lb Hg/TBtu out furnace | tested control | location | fr.remove coal-stack | fremove control | lb Hg/TBtu out control | %rel. deviation lb Hg/TBtu out control | F factor lb Hg/TBtu out control | % rel deviation F factor lb Hg/TBtu out control | particulateF factor lb Hg/TBtu out control | oxidized F factor lb Hg/TBtu out control | elemental F factor lb Hg/TBtu out control | inlet last control temp (C) | stack temp (C) | lb Hg/TWH from coal | lb Hg/TWH from concentration | lb Hg/MWH from coal | lb Hg/MWH from concentration
AES Cayuga (NY) (formerly NYSEG Milliken) | 2 | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | BITUMINOUS | 0.3186 |  |  | BITUMINOUS | 137.3704 | 881.6667 | 0.1065 |  |  |  | SO2/WETSCRUB | no bypass | 0.7205 | 0.6861 | 2.1612 | 15.09% | 2.0652 | 12.8% | 0.0091197 | 0.14647 | 1.9096 | 137.3704 | 50.1 | 22.9088 | 21.8912 | 2.2909e-05 | 2.1891e-05
AES Hawaii, Inc. | A | FBC/SNCR | BAGHOUSE | FBC | SUBBITUMINOUS | 0.0279 | TIRES | 0.0211 | SUBBITUMINOUS | 136.5333 | 45.6667 | 0.0267 | 0.551 | 1.1256 | 0.9854 | PM/BAGHOUSE | no bypass | 0.788 | 0.5252 | 0.4452 | 12.92% | 0.4606 | 13.14% | 0.001161 | 0.014928 | 0.44451 | 136.5333 | 133.5333 | 4.7191 | 4.8824 | 4.7191e-06 | 4.8824e-06
Antelope Valley Station | B1 | CONV/PC/NOX/DRY | BAGHOUSE | SDA | LIGNITE | 0.0658 |  |  | LIGNITE | 153 | 107 | 0.062 | 0.5942 | 3.5496 | 5.9733 | SO2/SDA | no bypass | 0.6574 | 0.3333 | 2.0791 | 168.9% | 4.0042 | 324.4% | 0.012775 | 0.32363 | 3.6678 | 153 | 84 | 22.0385 | 42.4446 | 2.2039e-05 | 4.2445e-05
Bailly | 7 | CYCLONE/NONOX/WET | ESP- CS | WETSCRUB | BITUMINOUS - LOW SULFUR | 0.0254 | BITUMINOUS - HIGH SULFUR | 0.06 | BITUMINOUS | 172.9 | 646 | 0.07 |  |  |  | SO2/WETSCRUB | no bypass | 0.5861 | 0.4795 | 2.2305 | 11.41% | 2.2306 | 10.86% | 0.0015394 | 0.25246 | 1.9766 | 172.9 | 54.2 | 23.6433 | 23.6444 | 2.3643e-05 | 2.3644e-05
Bay Front Plant Generating | 5 | CYCLONE/NONOX/WET | MECH | COMP COAL | BITUMINOUS | 0.0289 | PETROLEUM COKE | 0.0087 | BITUMINOUS | 134 | 127 | 0.06 | 2.022 | 9.5606 | 2.3927 | PM/MECH | no bypass | -0.4737 | -0.5707 | 6.9873 | 197.2% | 3.5792 | 81.67% | 0.60615 | 1.6561 | 1.3169 | 134 | 133.6667 | 74.0655 | 37.9396 | 7.4066e-05 | 3.794e-05
Big Bend | BB03 | CONV/TURBO/NOX/WET | ESP- CS | WETSCRUB | SUBBITUMINOUS | 0.0348 | BITUMINOUS | 0.1035 | BITUMINOUS | 155.3333 | 1766.6667 | 0.1383 |  |  |  | SO2/WETSCRUB | no bypass | 0.8235 | 0.6852 | 1.8593 | 21.93% | 1.5652 | 19.91% | 0 | 0.13434 | 1.4309 | 155.3333 | 52 | 19.7086 | 16.5912 | 1.9709e-05 | 1.6591e-05
Big Brown | 1 | CONV/PC/NONOX/DRY | ESP- CS/BAGHOUSE | NONE | LIGNITE | 0.1319 |  |  | LIGNITE | 184.6667 | 133.3333 | 0.288 | 0.7928 | 25.8997 | 27.9212 | PM/ESP- CS/BAGHOUSE | no bypass | 0.1002 | -0.0808 | 29.3912 | 97.32% | 30.0889 | 90.59% | 0.041331 | 12.6207 | 17.4269 | 184.6667 | 167.3333 | 311.5474 | 318.943 | 0.00031155 | 0.00031894
Brayton Point | 1 | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | BITUMINOUS | 0.0654 |  |  | BITUMINOUS | 153.6667 | 566.6667 | 0.0633 | 1.3004 | 5.7178 | 4.4348 | PM/ESP- CS | no bypass | 0.2456 | 0.2748 | 3.3877 | 31.34% | 3.2 | 30.4% | 0.54784 | 2.4042 | 0.24794 | 153.6667 | 143 | 35.9097 | 33.9201 | 3.591e-05 | 3.392e-05
Brayton Point | 3 | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | BITUMINOUS | 0.0654 |  |  | BITUMINOUS | 121.6667 | 966.6667 | 0.08 | 1.1622 | 6.6184 | 4.9119 | PM/ESP- CS | no bypass | 0.3111 | 0.2519 | 3.8926 | 93.15% | 3.6979 | 100.8% | 0.40187 | 2.1687 | 1.1273 | 121.6667 | 124.6667 | 41.2616 | 39.1978 | 4.1262e-05 | 3.9198e-05
Bruce Mansfield | 1 | CONV/PC/NOX/DRY | PARTSCRUB | NONE | PETROLEUM COKE | 0.01 | BITUMINOUS | 0.133 | BITUMINOUS | 140.6667 | 766.6667 | 0.0927 | 1.0925 | 7.395 | 8.0849 | PM/PARTSCRUB | no bypass | 0.0799 | 0.1207 | 6.2589 | 48.26% | 7.0985 | 65.39% | 0.12709 | 1.3949 | 5.5765 | 140.6667 | 52.3333 | 66.3445 | 75.2443 | 6.6344e-05 | 7.5244e-05
Charles R. Lowman | 2 | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | BITUMINOUS | 0.09 |  |  | BITUMINOUS | 146.3333 | 366.6667 | 0.0803 |  |  |  | SO2/WETSCRUB | after bypass | 0.8397 | 0.7324 | 1.001 | 229% | 0.9706 | 221.4% |  |  |  | 146.3333 | 122 | 10.6106 | 10.2884 | 1.0611e-05 | 1.0288e-05
Cholla | 2 | CONV/PC/NONOX/DRY | MECH/PARTSCRUB | WETSCRUB | SUBBITUMINOUS | 0.0582 | BITUMINOUS | 0.0429 | SUBBITUMINOUS | 136.6667 | 50 | 0.04 | 0.7384 | 2.6512 | 3.1632 | PM/MECH/PARTSCRUB | no bypass | 0.2436 | -0.0435 | 2.6906 | 22.31% | 3.1864 | 24.75% | 0 | 0.11729 | 3.0691 | 136.6667 | 86.6667 | 28.5204 | 33.7759 | 2.852e-05 | 3.3776e-05
Cholla | 3 | CONV/PC/NONOX/DRY | ESP- HS | NONE | SUBBITUMINOUS | 0.0582 | BITUMINOUS | 0.0429 | SUBBITUMINOUS | 359 | 50 | 0.0367 | 0.2595 | 0.794 | 0.9056 | PM/ESP- HS | no bypass | 0.642 | -0.3627 | 1.0763 | 46.51% | 1.2066 | 49.76% | 0 | 0.21394 | 0.99266 | 359 | 157.6667 | 11.4088 | 12.79 | 1.1409e-05 | 1.279e-05
Clay Boswell | 2 | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | SUBBITUMINOUS | 0.0701 |  |  | SUBBITUMINOUS | 175.6667 | 50 | 0.0567 | 0.892 | 4.016 | 3.6689 | PM/BAGHOUSE | no bypass | 0.8603 | 0.8257 | 0.6863 | 39.47% | 0.6633 | 34.47% | 0.020414 | 0.52711 | 0.11578 | 175.6667 | 167.6667 | 7.2748 | 7.031 | 7.2748e-06 | 7.031e-06
Clay Boswell | 3 | CONV/PC/NOX/DRY | PARTSCRUB | WETSCRUB/COMP COAL | SUBBITUMINOUS | 0.0701 |  |  | SUBBITUMINOUS | 143.6667 | 50 | 0.063 | 1.0915 | 5.6463 | 4.4349 | PM/PARTSCRUB | no bypass | 0.0017 | 0.0874 | 5.147 | 9.705% | 4.0454 | 15.42% | 0.0013245 | 0.041206 | 4.0029 | 143.6667 | 51 | 54.5583 | 42.8813 | 5.4558e-05 | 4.2881e-05
Clay Boswell | 4 | CONV/PC/NOX/DRY | PARTSCRUB | WETSCRUB | SUBBITUMINOUS | 0.0701 |  |  | SUBBITUMINOUS | 143.6667 | 50 | 0.066 | 0.7233 | 3.9282 | 3.6996 | PM/PARTSCRUB | no bypass | 0.114 | -0.2191 | 4.8364 | 24.14% | 4.455 | 34.75% | 0.11761 | 0.26881 | 4.0686 | 143.6667 | 68 | 51.2659 | 47.2231 | 5.1266e-05 | 4.7223e-05
Cliffside | 1 | CONV/PC/NONOX/DRY | ESP- HS | NONE | BITUMINOUS | 0.0523 |  |  | BITUMINOUS | 342.4333 | 1400 | 0.06 | 1.9574 | 8.4317 | 6.4487 | PM/ESP- HS | no bypass | -0.1243 | 0.3041 | 4.9826 | 109.6% | 4.3223 | 108% | 0.1433 | 2.1641 | 2.0149 | 342.4333 | 194.4667 | 52.8157 | 45.8165 | 5.2816e-05 | 4.5816e-05
Clifty Creek | 6 | CONV/PC/NOX/WET | ESP- HS | COMP COAL | SUBBITUMINOUS | 0.0711 | BITUMINOUS | 0.1463 | SUBBITUMINOUS/BITUMINOUS | 383 | 441 | 0.08 | 1.83 | 11.6477 | 10.4083 | PM/ESP- HS | no bypass | -0.3049 | 0.3403 | 8.3071 | 40.37% | 6.8745 | 52.57% | 0.18525 | 3.3834 | 3.3058 | 383 | 167.3333 | 88.0554 | 72.8698 | 8.8055e-05 | 7.287e-05
Clover Power Station | 2 | CONV/PC/NOX/DRY | BAGHOUSE | WETSCRUB | BITUMINOUS | 0.0978 |  |  | BITUMINOUS | 139 | 519.9091 | 0.1594 |  |  |  | SO2/WETSCRUB | no bypass | 0.9671 | 0.7633 | 0.3387 | 20.13% | 0.3529 | 20.95% | 0.023925 | 0.1914 | 0.13757 | 139 | 50.2 | 3.5902 | 3.7407 | 3.5902e-06 | 3.7407e-06
Colstrip | 3 | CONV/PC/NOX/DRY | PARTSCRUB | WETSCRUB | SUBBITUMINOUS | 0.0555 |  |  | SUBBITUMINOUS | 139.3333 | 66.6667 | 0.0653 | 1.0864 | 6.7042 | 6.1489 | PM/PARTSCRUB | no bypass | 0.1472 | -0.0784 | 5.1853 | 306.4% | 5.7264 | 340.9% | 0.087337 | 0.30277 | 5.3363 | 139.3333 | 89 | 54.9643 | 60.7 | 5.4964e-05 | 6.07e-05
Columbia | 1 | CONV/PC/NOX/DRY | ESP- HS | COMP COAL | SUBBITUMINOUS | 0.0575 |  |  | SUBBITUMINOUS | 406 | 314 | 0.1 | 1.6265 | 13.351 | 11.8709 | PM/ESP- HS | no bypass | -0.2522 | 0.1195 | 10.2732 | 22.91% | 10.3097 | 24.68% | 0.0034316 | 1.8045 | 8.5018 | 406 | 154 | 108.8961 | 109.283 | 0.0001089 | 0.00010928
Comanche | 2 | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | SUBBITUMINOUS | 0.0767 |  |  | SUBBITUMINOUS | 144.8148 | 50 | 0.0922 | 0.8542 | 6.6021 | 7.0101 | PM/BAGHOUSE | no bypass | 0.6577 | 0.6259 | 2.6611 | 44.9% | 2.5931 | 42.2% | 0.01944 | 2.3172 | 0.2565 | 144.8148 | 151.4815 | 28.2077 | 27.4869 | 2.8208e-05 | 2.7487e-05
Coronado | U1B | CONV/PC/NOX/WET | ESP- HS | WETSCRUB | SUBBITUMINOUS | 0.0569 |  |  | SUBBITUMINOUS | 138 | 116.6667 | 0.035 |  |  |  | SO2/WETSCRUB | after control | 0.3061 | -0.1524 | 2.1357 | 21.93% | 2.4468 | 12.94% | 0.050908 | 0.050769 | 2.3451 | 138 | 48 | 22.6385 | 25.9361 | 2.2638e-05 | 2.5936e-05
Coyote | 1 | CYCLONE/NONOX/WET | BAGHOUSE | SDA | LIGNITE | 0.1348 |  |  | LIGNITE | 172 | 100 | 0.1107 | 1.4073 | 13.5502 | 12.8692 | SO2/SDA | no bypass | 0.1211 | 0.3824 | 7.355 | 627.6% | 7.9523 | 677.4% | 0.073258 | 0.16857 | 7.7105 | 172 | 102.3 | 77.9632 | 84.2946 | 7.7963e-05 | 8.4295e-05
Craig | C1 | CONV/PC/NOX/DRY | ESP- HS | WETSCRUB | SUBBITUMINOUS | 0.0254 | BITUMINOUS | 0.0367 | SUBBITUMINOUS | 121 | 266.6667 | 0.0227 |  |  |  | SO2/WETSCRUB | after bypass | 0.2367 | 0.2819 | 1.3834 | 9.249% | 1.4456 | 8.377% |  |  |  | 121 | 62 | 14.6641 | 15.3234 | 1.4664e-05 | 1.5323e-05
Craig | C3 | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SUBBITUMINOUS | 0.0254 | BITUMINOUS | 0.0367 | SUBBITUMINOUS | 139 | 116.6667 | 0.01 | 1.3182 | 1.0437 | 1.0972 | SO2/SDA | no bypass | 0.1281 | 0.336 | 0.6897 | 1.974% | 0.7248 | 3.407% | 0.0025372 | 0.025372 | 0.69689 | 139 | 81.9 | 7.3108 | 7.6829 | 7.3108e-06 | 7.6829e-06
Dunkirk | 2 | CONV/PC/NOX/DRY | ESP- HS | COMP COAL | BITUMINOUS | 0.0902 |  |  | BITUMINOUS | 304.7667 | 872 | 0.13 | 1.1636 | 10.8768 | 8.3305 | PM/ESP- HS | no bypass | 0.1019 | 0.1873 | 8.3976 | 195.4% | 6.803 | 144.5% | 0.15023 | 4.2746 | 2.3782 | 304.7667 | 294.8 | 89.0147 | 72.1119 | 8.9015e-05 | 7.2112e-05
Dwayne Collier Battle Cogeneration Facility | 2B | STOKER/NOX/DRY | BAGHOUSE | SDA | BITUMINOUS | 0.0767 |  |  | BITUMINOUS | 167.6667 | 1700 | 0.03 | 0.7344 | 1.5869 | 1.7035 | SO2/SDA | no bypass | 0.952 | 0.9366 | 0.1037 | 1.015% | 0.1074 | 1.047% | 0.022511 | 0.018985 | 0.065905 | 167.6667 | 85.7 | 1.0992 | 1.1384 | 1.0992e-06 | 1.1384e-06
Gaston | 1 | CONV/PC/NOX/DRY | ESP- HS | NONE | BITUMINOUS | 0.1342 |  |  | BITUMINOUS | 336.3333 | 333.3333 | 0.0593 | 1.3715 | 5.9456 | 5.2148 | PM/ESP- HS | no bypass | -0.3998 | -0.1719 | 6.1698 | 103.5% | 6.0738 | 75.34% | 0.55078 | 3.6455 | 1.8775 | 336.3333 | 126.6667 | 65.4 | 64.3824 | 6.54e-05 | 6.4382e-05
George Neal South | 4 | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | SUBBITUMINOUS | 0.08 |  |  | SUBBITUMINOUS | 152 | 191 | 0.09 | 0.852 | 6.2152 | 7.4666 | PM/ESP- CS | no bypass | 0.2194 | -0.096 | 5.7757 | 66.12% | 7.7269 | 74.68% | 0.030327 | 3.2082 | 4.4883 | 152 | 141.3333 | 61.2225 | 81.9053 | 6.1223e-05 | 8.1905e-05
Gibson Generating Station (0300) | 3 | CONV/PC/NOX/DRY | ESP- CS | NONE | BITUMINOUS | 0.0772 |  |  | BITUMINOUS | 156 | 1866.6667 | 0.1183 | 3.1616 | 32.3115 | 30.6737 | PM/ESP- CS | no bypass | -2.0104 | 0.0495 | 30.7445 | 323.9% | 29.0614 | 205.2% | 0.0068601 | 24.9348 | 4.1197 | 156 | 155 | 325.8924 | 308.0515 | 0.00032589 | 0.00030805
Gibson Generating Station (1099) | 3 | CONV/PC/NOX/DRY | ESP- CS | NONE | BITUMINOUS | 0.0772 |  |  | BITUMINOUS | 161 | 2100 | 0.139 | 1.566 | 17.3947 | 16.4719 | PM/ESP- CS | no bypass | -0.1688 | 0.3572 | 12.9877 | 404.6% | 9.7452 | 163.6% | 0.022816 | 6.1032 | 3.6192 | 161 | 171.6667 | 137.6699 | 103.2993 | 0.00013767 | 0.0001033
GRDA | 2 | CONV/PC/NOX/DRY | ESP- CS | SDA | SUBBITUMINOUS | 0.0557 | BITUMINOUS | 0.0771 | SUBBITUMINOUS/BITUMINOUS | 155.7333 | 398.6667 | 0.1 | 0.9573 | 7.8983 | 8.6306 | SO2/SDA | no bypass | -0.0097 | -0.0283 | 8.3264 | 113.8% | 8.6918 | 59.53% | 0.011696 | 0.76023 | 7.9199 | 155.7333 | 84.1 | 88.26 | 92.1333 | 8.826e-05 | 9.2133e-05
Intermountain | 2SGA | CONV/PC/NOX/DRY | BAGHOUSE | WETSCRUB | BITUMINOUS | 0.0391 | PETROLEUM COKE | 0.0117 | BITUMINOUS | 151 | 200 | 0.0233 |  |  |  | SO2/WETSCRUB | no bypass | 0.8384 | 0.7453 | 0.2849 | 11.47% | 0.2466 | 9.848% | 0.0073119 | 0.045799 | 0.19349 | 151 | 48.7 | 3.0199 | 2.614 | 3.0199e-06 | 2.614e-06
Jack Watson | 4 | CONV/PC/NOX/DRY | ESP- CS | NONE | BITUMINOUS | 0.0918 | SUBBITUMINOUS | 0.1558 | BITUMINOUS | 149.6667 | 760.6667 | 0.0537 | 1.0654 | 4.3276 | 4.1634 | PM/ESP- CS | no bypass | 0.2447 | 0.2923 | 3.0657 | 49.32% | 2.9333 | 24.16% | 0.025585 | 2.0258 | 0.88195 | 149.6667 | 152.3333 | 32.4965 | 31.093 | 3.2496e-05 | 3.1093e-05
Jim Bridger | BW 74 | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | SUBBITUMINOUS | 0.0501 | BITUMINOUS | 0.048 | SUBBITUMINOUS | 146 | 50 | 0.0733 |  |  |  | SO2/WETSCRUB | no bypass | 0.1949 | 0.096 | 4.9038 | 36.88% | 4.704 | 35.38% | 0.034009 | 0.17798 | 4.492 | 146 | 53.7 | 51.9804 | 49.8625 | 5.198e-05 | 4.9863e-05
Kline Township Cogen Facility | GEN1 | FBC/NONOX | BAGHOUSE | FBC | WASTE ANTHRACITE | 0.1733 |  |  | WASTE BITUMINOUS | 187.6667 | 266.6667 | 0.3333 | 0.2675 | 17.3101 | 32.0152 | PM/BAGHOUSE | no bypass | 0.9995 | 0.9975 | 0.0326 | 0.09292% | 0.0816 | 0.2597% | 0.0024521 | 0.030787 | 0.048361 | 187.6667 | 173.6667 | 0.34556 | 0.86496 | 3.4556e-07 | 8.6496e-07
La Cygne | 1 | CYCLONE/NOX/WET | PARTSCRUB | WETSCRUB | SUBBITUMINOUS | 0.0523 | BITUMINOUS | 0.1249 | SUBBITUMINOUS | 144 | 300 | 0.1033 |  |  | 7.092 | PM/PARTSCRUB | no bypass | 0.427 | 0.2215 | 5.0527 | 105.1% | 5.514 | 132.3% | 0.12167 | 0.30729 | 5.085 | 144 | 72.6667 | 53.5587 | 58.4485 | 5.3559e-05 | 5.8449e-05
Laramie River Station | 1 | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | SUBBITUMINOUS | 0.0521 |  |  | SUBBITUMINOUS | 138.1333 | 77 | 0.1193 |  |  |  | SO2/WETSCRUB | after bypass | 0.7338 | 0.6074 | 2.6154 | 42.08% | 3.0184 | 48.59% |  |  |  | 138.1333 | 63.7 | 27.7233 | 31.9951 | 2.7723e-05 | 3.1995e-05
Laramie River Station | 3 | CONV/PC/NOX/DRY | ESP- CS | SDA | SUBBITUMINOUS | 0.0521 |  |  | SUBBITUMINOUS | 138.5 | 74 | 0.1247 | 0.5406 | 5.6025 | 6.2128 | SO2/SDA | no bypass | 0.7038 | -0.7848 | 3.0504 | 33.68% | 3.3411 | 57.5% | -0.01326 | -0.27219 | 3.6265 | 138.5 | 78.5 | 32.3343 | 35.4157 | 3.2334e-05 | 3.5416e-05
Lawrence | 4 | CONV/PC/NONOX/DRY | PARTSCRUB | WETSCRUB | SUBBITUMINOUS | 0.0683 | BITUMINOUS | 0.0795 | SUBBITUMINOUS | 166 | 266.6667 | 0.0477 | 1.0345 | 4.0213 | 4.3987 | PM/PARTSCRUB | no bypass | -0.2317 | -0.1742 | 4.755 | 10.16% | 5.1181 | 21.49% | 0.13486 | 0.36604 | 4.6172 | 166 | 67.3333 | 50.4031 | 54.252 | 5.0403e-05 | 5.4252e-05
Leland Olds Station | 2 | CYCLONE/NONOX/WET | ESP- CS | NONE | LIGNITE | 0.0717 |  |  | LIGNITE | 201.6667 | 90.6667 | 0.0405 | 1.2793 | 5.137 | 4.8266 | PM/ESP- CS | no bypass | -0.1279 | 0.0487 | 4.0512 | 135.8% | 4.0233 | 75.75% | 0.0017005 | 0.68444 | 3.3372 | 201.6667 | 182 | 42.9428 | 42.6471 | 4.2943e-05 | 4.2647e-05
Lewis & Clark | B1 | CONV/PC/NOX/DRY | PARTSCRUB | NONE | LIGNITE | 0.0967 |  |  | LIGNITE | 198.6667 | 100 | 0.1193 | 1.4342 | 16.1501 | 16.9607 | PM/PARTSCRUB | no bypass | 0.1995 | 0.3277 | 9.1641 | 99.15% | 10.8315 | 76.09% | 0.016411 | 0.32292 | 10.4922 | 198.6667 | 60 | 97.1397 | 114.8141 | 9.714e-05 | 0.00011481
Limestone | LIM1 | CONV/PC/NOX/WET | ESP- CS | WETSCRUB | LIGNITE | 0.146 |  |  | LIGNITE | 161.6667 | 50 | 0.139 |  |  |  | SO2/WETSCRUB | after control | -0.075 | 0.5102 | 13.8843 | 84.81% | 13.6612 | 46.14% | 0.11943 | 1.7118 | 11.83 | 161.6667 | 59.7 | 147.1739 | 144.809 | 0.00014717 | 0.00014481
Logan Generating Plant | GEN 1 | CONV/PC/NOX/SCR/DRY | BAGHOUSE | SDA | BITUMINOUS | 0.1727 |  |  | BITUMINOUS | 147.3333 | 1500 | 0.18 | 0.9117 | 11.9526 | 12.0912 | SO2/SDA | no bypass | 0.9784 | 0.9752 | 0.2728 | 26.7% | 0.2801 | 27.42% | 0.012733 | 0.027034 | 0.24033 | 147.3333 | 87 | 2.8917 | 2.9691 | 2.8917e-06 | 2.9691e-06
Mecklenburg Cogeneration Facility | GEN 1 | CONV/PC/NOX/DRY | BAGHOUSE | SDA | BITUMINOUS | 0.0932 |  |  | BITUMINOUS | 147.9333 | 1892.6667 | 0.0967 | 1.2365 | 8.353 | 9.9299 | SO2/SDA | no bypass | 0.9851 | 0.9881 | 0.1029 | 1.59% | 0.1062 | 1.62% | 0.010541 | 0.041768 | 0.053891 | 147.9333 | 74.6 | 1.0907 | 1.1257 | 1.0907e-06 | 1.1257e-06
Meramec | 4 | CONV/PC/NOX/DRY | ESP- CS | NONE | SUBBITUMINOUS | 0.0539 | BITUMINOUS | 0.0896 | SUBBITUMINOUS/BITUMINOUS | 169.6667 | 3620 | 0.091 | 1.0291 | 6.8262 | 6.6269 | PM/ESP- CS | no bypass | 0.7116 | 0.744 | 1.9267 | 74.11% | 1.7255 | 64.43% | 0.003054 | 1.0719 | 0.6505 | 169.6667 | 158.3333 | 20.4231 | 18.2903 | 2.0423e-05 | 1.829e-05
Monticello | 1 | CONV/PC/NONOX/DRY | ESP- CS/BAGHOUSE | NONE | LIGNITE | 0.1754 | SUBBITUMINOUS | 0.0732 | LIGNITE | 181 | 166.6667 | 0.3717 | 0.9671 | 44.0972 | 43.9689 | PM/ESP- CS/BAGHOUSE | no bypass | -0.2037 | -0.2126 | 56.0352 | 2779% | 55.8686 | 2770% | 0.092215 | 47.477 | 8.2994 | 181 | 165.3333 | 593.9743 | 592.2084 | 0.00059397 | 0.00059221
Monticello | 3 | CONV/PC/NONOX/DRY | ESP- CS | WETSCRUB | LIGNITE | 0.1754 | SUBBITUMINOUS | 0.0732 | LIGNITE | 176.3333 | 133.3333 | 0.415 |  |  |  | SO2/WETSCRUB | after bypass | 0.6513 | 0.4757 | 16.7222 | 249.4% | 18.3232 | 510.8% |  |  |  | 176.3333 | 89.3 | 177.2557 | 194.2263 | 0.00017726 | 0.00019423
Montrose | 1 | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | SUBBITUMINOUS | 0.0422 |  |  | SUBBITUMINOUS | 158.3333 | 133.3333 | 0.0997 | 0.189 | 1.7922 | 6.4935 | PM/ESP- CS | no bypass | 0.3572 | 0.0933 | 6.1366 | 35.67% | 5.8573 | 21.81% | 0.0027286 | 1.7884 | 4.0662 | 158.3333 | 167.2333 | 65.0481 | 62.0875 | 6.5048e-05 | 6.2088e-05
Navajo | 3 | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | BITUMINOUS | 0.0374 |  |  | BITUMINOUS | 155 | 150 | 0.0303 |  |  |  | SO2/WETSCRUB | no bypass | -0.2046 | 0.2095 | 2.7208 | 4.829% | 2.7359 | 3.185% | 0.021363 | 0.025636 | 2.6889 | 155 | 49 | 28.8405 | 29.0006 | 2.8841e-05 | 2.9001e-05
Nelson Dewey | 1 | CYCLONE/NONOX/WET | ESP- HS | COMP COAL | SUBBITUMINOUS | 0.0805 |  |  | SUBBITUMINOUS/PETCOKE | 257 | 129 | 0.06 | 0.433 | 1.9965 | 1.9973 | PM/ESP- HS | no bypass | 0.5557 | -0.0897 | 2.0488 | 33.5% | 2.1349 | 41.46% | 0.020735 | 0.16028 | 1.9539 | 257 | 260 | 21.7173 | 22.63 | 2.1717e-05 | 2.263e-05
Newton | 2 | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | BITUMINOUS | 0.057 | SUBBITUMINOUS | 0.0546 | SUBBITUMINOUS | 161 | 178 | 0.0707 | 1.301 | 8.3088 | 7.6144 | PM/ESP- CS | no bypass | -0.1916 | 0.0823 | 7.6305 | 80.97% | 6.9877 | 58.74% | 0.002375 | 1.425 | 5.5603 | 161 | 167.3333 | 80.8835 | 74.0698 | 8.0883e-05 | 7.407e-05
Platte | 1 | CONV/PC/NOX/WET | ESP- HS | COMP COAL | SUBBITUMINOUS | 0.0608 |  |  | SUBBITUMINOUS | 413.6333 | 180.6667 | 0.09 | 1.7623 | 12.1933 | 10.3553 | PM/ESP- HS | no bypass | -0.6753 | -0.0293 | 11.4905 | 304.7% | 10.6121 | 285.6% | 0.018163 | 0.89394 | 9.7 | 413.6333 | 154.7667 | 121.7995 | 112.4885 | 0.0001218 | 0.00011249
Polk Power | 1 | COAL GAS | COAL GAS | COAL GAS | BITUMINOUS | 0.0858 | SUBBITUMINOUS | 0.036 | BITUMINOUS | 171.3333 | 1066.6667 | 0.1 | 0.6601 | 5.2289 | 5.4713 | no control | no bypass | 0.3399 | 0 | 5.2289 | 37.4% | 5.4713 | 30.59% | 0.0071396 | 0.39506 | 5.0691 | 171.3333 |  | 55.4265 | 57.9959 | 5.5426e-05 | 5.7996e-05
Port Washington | 4 | CONV/PC/NONOX/DRY | ESP- CS | SORBENT INJ | BITUMINOUS | 0.0954 |  |  | BITUMINOUS | 405.6333 | 1215.3333 | 0.09 | 2.0011 | 12.88 | 12.2227 | SO2/SORBENT INJ | no bypass | 0.0118 | 0.4489 | 6.359 | 30.82% | 6.6916 | 26.67% | 0.011 | 4.492 | 2.1886 | 405.6333 | 205.9 | 67.4055 | 70.9311 | 6.7406e-05 | 7.0931e-05
Presque Isle | 5 | CONV/PC/NONOX/WET | ESP- CS | COMP COAL | BITUMINOUS/PETROLEUM COKE | 0.03 | SUBBITUMINOUS | 0.0508 | BITUMINOUS/PETCOKE | 172.2222 | 190.3072 | 0.0429 | 1.4292 | 4.7905 | 3.766 | PM/ESP- CS | no bypass | 0.6282 | 0.662 | 1.2424 | 7.641% | 1.2622 | 7.452% | 0.0076189 | 0.5384 | 0.71618 | 172.2222 | 171.8518 | 13.1695 | 13.3793 | 1.3169e-05 | 1.3379e-05
Presque Isle | 6 | CONV/PC/NONOX/WET | ESP- CS | COMP COAL | BITUMINOUS/PETROLEUM COKE | 0.03 | SUBBITUMINOUS | 0.0508 | BITUMINOUS/PETCOKE | 153.3333 | 196.7475 | 0.0393 | 1.2009 | 3.4866 | 2.6811 | PM/ESP- CS | no bypass | 0.5802 | 0.5452 | 1.2333 | 19.98% | 1.2217 | 16.03% | 0.020808 | 0.61775 | 0.58314 | 153.3333 | 151.6667 | 13.073 | 12.95 | 1.3073e-05 | 1.295e-05
Presque Isle | 9 | CONV/PC/NOX/WET | ESP- HS | COMP COAL | BITUMINOUS/PETROLEUM COKE | 0.03 | SUBBITUMINOUS | 0.0508 | SUBBITUMINOUS | 381.6667 | 223.4861 | 0.0682 | 0.9047 | 5.1091 | 4.8944 | PM/ESP- HS | no bypass | 0.0993 | -0.0363 | 5.0896 | 19.2% | 5.0738 | 21.27% | 0.0018257 | 0.42675 | 4.6452 | 381.6667 | 195.7407 | 53.9499 | 53.7824 | 5.395e-05 | 5.3782e-05
R. D. Morrow Sr. Generating plant | 2 | CONV/PC/NOX/DRY | ESP- HS | WETSCRUB | BITUMINOUS | 0.1958 |  |  | BITUMINOUS | 166.3333 | 833.3333 | 0.05 |  |  |  | SO2/WETSCRUB | after bypass | 0.4567 | 0.7575 | 2.0909 | 21.94% | 2.1269 | 19.37% |  |  |  | 166.3333 | 86.3 | 22.1636 | 22.5452 | 2.2164e-05 | 2.2545e-05
R.M. Heskett Station | B2 | FBC/NONOX | ESP- CS | FBC | LIGNITE | 0.0881 |  |  | LIGNITE | 162.3333 | 100 | 0.0863 | 0.8195 | 6.5466 | 7.3244 | PM/ESP- CS | no bypass | 0.5614 | 0.4036 | 3.5095 | 52.46% | 3.9768 | 44.28% | 0.055164 | 0.4895 | 3.4321 | 162.3333 | 157.6667 | 37.2008 | 42.1542 | 3.7201e-05 | 4.2154e-05
Rawhide | 101 | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SUBBITUMINOUS | 0.0469 |  |  | SUBBITUMINOUS | 170.9333 | 126.6667 | 0.0733 | 1.9758 | 12.1599 | 11.6487 | SO2/SDA | no bypass | -0.2564 | 0.3183 | 7.6658 | 51.74% | 7.763 | 64.33% | 0.072445 | 0.57956 | 7.111 | 170.9333 | 104 | 81.2576 | 82.288 | 8.1258e-05 | 8.2288e-05
Salem Harbor | 3 | CONV/PC/NOX/SNCR/DRY | ESP- CS | COMP COAL | BITUMINOUS | 0.0571 |  |  | BITUMINOUS | 125.6667 | 100 | 0.0267 | 1.701 | 3.1869 | 3.2345 | PM/ESP- CS | no bypass | 0.8298 | 0.8988 | 0.3291 | 13.6% | 0.3348 | 16.05% | 0.058892 | 0.099735 | 0.17617 | 125.6667 | 128.6667 | 3.4885 | 3.5489 | 3.4885e-06 | 3.5489e-06
Sam Seymour | 3 | CONV/PC/NONOX/DRY | ESP- CS | WETSCRUB | SUBBITUMINOUS | 0.0852 |  |  | SUBBITUMINOUS | 149.6667 | 20 | 0.1227 |  |  |  | SO2/WETSCRUB | after control | 0.5624 | -0.2032 | 4.4806 | 49.23% | 8.6353 | 48.86% | 0.049762 | 0.19573 | 8.3898 | 149.6667 | 55.7 | 47.4945 | 91.5344 | 4.7494e-05 | 9.1534e-05
San Juan | 2 | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | SUBBITUMINOUS | 0.0918 |  |  | SUBBITUMINOUS | 142.9 | 166.6667 | 0.0537 |  |  |  | SO2/WETSCRUB | after control | 0.1747 | 0.3683 | 4.0847 | 110.1% | 4.2854 | 104.2% | 0.044727 | 0.27116 | 3.9695 | 142.9 | 47.9 | 43.2979 | 45.4253 | 4.3298e-05 | 4.5425e-05
Scrubgrass Generating Company L. P. | GEN1 | FBC/NONOX | BAGHOUSE | FBC | WASTE BITUMINOUS | 0.7029 |  |  | WASTE BITUMINOUS | 161 | 600 | 0.5267 | 0.6937 | 43.8616 | 92.5118 | PM/BAGHOUSE | no bypass | 0.9992 | 0.9989 | 0.0485 | 0.3032% | 0.0936 | 1.119% | 0.001971 | 0.036658 | 0.054971 | 161 | 157 | 0.5141 | 0.99216 | 5.141e-07 | 9.9216e-07
SEI - Birchwood Power Facility | 1 | CONV/PC/NOX/SCR/DRY | BAGHOUSE | SDA | BITUMINOUS | 0.147 |  |  | BITUMINOUS | 134 | 917.3333 | 0.11 | 0.93 | 8.1477 | 8.6933 | SO2/SDA | no bypass | 0.972 | 0.9736 | 0.2444 | 15.1% | 0.2379 | 15.15% | 0.0092053 | 0.12226 | 0.10644 | 134 | 90 | 2.5906 | 2.5217 | 2.5906e-06 | 2.5217e-06
Shawnee Fossil Plant | 3 | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | BITUMINOUS | 0.0482 | SUBBITUMINOUS | 0.1064 | BITUMINOUS/SUBBITUMINOUS | 157.6667 | 166.6667 | 0.0283 | 1.5706 | 3.2737 | 3.3073 | PM/BAGHOUSE | no bypass | 0.4974 | 0.682 | 1.0443 | 7.259% | 1.0507 | 7.306% | 0.062542 | 0.44137 | 0.54679 | 157.6667 | 151.3333 | 11.0696 | 11.1374 | 1.107e-05 | 1.1137e-05
Sherburne County Generating Plant | #3 | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SUBBITUMINOUS | 0.0528 |  |  | SUBBITUMINOUS | 147.3333 | 102 | 0.0767 | 1.3605 | 8.9438 | 7.9042 | SO2/SDA | no bypass | -0.097 | 0.0446 | 7.1935 | 91.79% | 7.5401 | 131.7% | 0.12765 | 0.14546 | 7.267 | 147.3333 | 80.3 | 76.2513 | 79.9252 | 7.6251e-05 | 7.9925e-05
St Clair Power Plant | 4 | CONV/PC/NONOX/DRY | ESP- CS | COMP COAL | SUBBITUMINOUS | 0.0344 | BITUMINOUS | 0.0875 | SUBBITUMINOUS/BITUMINOUS | 139.6667 | 333.3333 | 0.0613 | 0.9373 | 4.5648 | 4.8819 | PM/ESP- CS | no bypass | 0.3649 | 0.2023 | 3.1025 | 58.42% | 3.9076 | 79.64% | 0.060075 | 0.979 | 2.8685 | 139.6667 | 140 | 32.8866 | 41.4206 | 3.2887e-05 | 4.1421e-05
Stanton Station | 1 | CONV/PC/NOX/DRY | ESP- CS | NONE | LIGNITE | 0.0883 |  |  | LIGNITE | 164.9667 | 50.3333 | 0.0823 | 0.5415 | 3.2952 | 6.6754 | PM/ESP- CS | no bypass | 0.4409 | -0.0357 | 3.9569 | 27.18% | 6.9024 | 16.75% | 0.013621 | 0.24957 | 6.6392 | 164.9667 | 166.4667 | 41.9432 | 73.1656 | 4.1943e-05 | 7.3166e-05
Stanton Station | 10 | CONV/PC/NOX/DRY | BAGHOUSE | SDA | LIGNITE | 0.0883 |  |  | LIGNITE | 176 | 28.3333 | 0.0835 | 1.1531 | 8.7844 | 6.3462 | SO2/SDA | no bypass | -0.0701 | 0.0147 | 8.1445 | 15.43% | 6.2517 | 15.2% | 0.004437 | 0.13607 | 6.1112 | 176 | 93.3 | 86.3319 | 66.2682 | 8.6332e-05 | 6.6268e-05
Stockton Cogen Company | GEN1 | FBC/SNCR | BAGHOUSE | FBC | BITUMINOUS | 0.0404 | PETROLEUM COKE | 0.0293 | BITUMINOUS/PETCOKE | 148.3333 | 583.3333 | 0.027 | 1.4795 | 3.2006 | 1.7032 | PM/BAGHOUSE | no bypass | 0.8927 | 0.9182 | 0.2308 | 3.6% | 0.1316 | 1.002% | 0.055818 | 0.036669 | 0.039113 | 148.3333 | 146 | 2.4465 | 1.395 | 2.4465e-06 | 1.395e-06
TNP-One | U2 | FBC/NONOX | BAGHOUSE | FBC | LIGNITE | 0.031 |  |  | LIGNITE | 180.6667 | 133.3333 | 0.2547 | 0.9477 | 25.8893 | 25.8212 | PM/BAGHOUSE | no bypass | 0.592 | 0.5698 | 10.8506 | 357.3% | 10.8596 | 337.8% | 0.041354 | 7.7691 | 3.0492 | 180.6667 | 175.3333 | 115.0166 | 115.112 | 0.00011502 | 0.00011511
Valley | 2 | CONV/PC/NOX/DRY | BAGHOUSE | NONE | BITUMINOUS/PETROLEUM COKE | 0.0475 |  |  | BITUMINOUS/PETCOKE | 156.6667 | 127.6667 | 0.0124 | 1.8615 | 1.6095 | 1.5799 | PM/BAGHOUSE | no bypass | -1.086 | -0.0675 | 1.8514 | 20.93% | 1.663 | 20.05% | 0.037466 | 1.3053 | 0.32027 | 156.6667 | 158.4333 | 19.6249 | 17.6278 | 1.9625e-05 | 1.7628e-05
Valmont | 5 | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | BITUMINOUS | 0.0388 |  |  | BITUMINOUS | 147 | 38.6667 | 0.0079 | 2.1637 | 1.3706 | 0.9228 | PM/BAGHOUSE | no bypass | 0.7733 | 0.8652 | 0.1481 | 5.778% | 0.1268 | 4.436% | 0.0041528 | 0.10161 | 0.021041 | 147 | 140 | 1.5699 | 1.3441 | 1.5699e-06 | 1.3441e-06
W. H. Sammis | 1 | CONV/PC/NONOX/DRY | BAGHOUSE | NONE | BITUMINOUS | 0.1009 |  |  | BITUMINOUS | 158 | 1233.3333 | 0.106 | 1.764 | 14.0602 | 10.7427 | PM/BAGHOUSE | no bypass | 0.8716 | 0.9221 | 1.0109 | 6.058% | 0.8291 | 3.126% | 0.036849 | 0.38077 | 0.41148 | 158 | 150.6667 | 10.7156 | 8.7885 | 1.0716e-05 | 8.7885e-06
Wabash River Generating Station | 1 + 1A | COAL GAS | COAL GAS | COAL GAS | BITUMINOUS | 0.0786 | PETROLEUM COKE | 0.0225 | BITUMINOUS | 176.1 | 600 | 0.0673 | 0.6747 | 3.6393 | 5.3343 | out of generator | no bypass | 0.3253 | 0 | 3.6393 | 31.67% | 5.3343 | 37.46% | 0.04771 | 0.54539 | 4.7412 | 176.1 |  | 38.5767 | 56.5437 | 3.8577e-05 | 5.6544e-05
Widows Creek Fossil Plant | 6 | CONV/PC/NONOX/DRY | ESP- CS | COMP COAL | BITUMINOUS | 0.0846 |  |  | BITUMINOUS | 160.3333 | 333.3333 | 0.0247 | 1.5506 | 2.9701 | 2.8976 | PM/ESP- CS | no bypass | 0.2991 | 0.5216 | 1.3695 | 32.49% | 1.3986 | 36.96% | 0.0649 | 0.81612 | 0.51758 | 160.3333 | 157 | 14.5167 | 14.8252 | 1.4517e-05 | 1.4825e-05
Wyodak | BW 91 | CONV/PC/NOX/DRY | ESP- CS | SDA | SUBBITUMINOUS | 0.0633 |  |  | SUBBITUMINOUS | 160 | 25 | 0.04 | 4.1729 | 13.6164 | 12.5126 | SO2/SDA | no bypass | -1.44 | 0.4349 | 8.0526 | 5.688% | 7.0701 | 2.667% | 0.013578 | 0.11525 | 6.9413 | 160 | 81.7 | 85.3577 | 74.9432 | 8.5358e-05 | 7.4943e-05
* the value of MWH was estimated with an efficiency of 0.322115 for power conversion.
efficiency factor | 0.32211 | 10.6
Tbtu/TWH | 3.4144
Note on N35: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N37: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N40: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N26: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N24: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N20: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N12: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N7: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N5: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N2: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N45: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N50: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N52: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N61: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N65: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N66: The furnace exit was not tested. The entrance to the last control and the exit of the last control was tested.
Note on N39: Inlet flow rate of gas missing.
Note on O39: Inlet flow rate of gas missing.
Note on T56: No control device after combustion.
Note on T79: No control device after combustion.
Note on V1: The percent relative deviation is the ratio of the standard deviation to the average, expressed as a percentage.
Note on W40: Hg concentrations measured after recombination with bypass. Values corrected for control exit.
Note on W26: Hg concentrations measured after recombination with bypass. Values corrected for control exit.
Note on W50: Hg concentrations measured after recombination with bypass. Values corrected for control exit.
Note on W61: Hg concentrations measured after recombination with bypass. Values corrected for control exit.
Note on Y12: Hg speciation measured after recombination with bypass. Values not available for speciation from control exit.
Note on Y26: Hg speciation measured after recombination with bypass. Values not available for speciation from control exit.
Note on Y40: Hg speciation measured after recombination with bypass. Values not available for speciation from control exit.
Note on Y50: Hg speciation measured after recombination with bypass. Values not available for speciation from control exit.
Note on Y61: Hg speciation measured after recombination with bypass. Values not available for speciation from control exit.
Note on W12: Hg concentrations measured after recombination with bypass. Values corrected for control exit.

## definitions
You may search these terms through the use of the find or [Ctrl][f] keys.
The monthly mercury tests by coal type are reported for all units at the facility. The unit tested at the facility may burn one or more of the types of coal types that were tested for mercury. You should manually match the type of fuel during the emissions test to the types of coals measured during the year for comparison purposes. | d
NOTES FOR CALCULATIONS
Some FGD units were operated with an active bypass of the control device during the testing. For units with a bypass around the unit (some of the furnace gas was vented to the stack without treatment by the control device) the measured data were used to estimate the concentration and flow rates as if all of the gas were treated by the control device.
For units with multiple control devices in series, only the last control device was tested. Those units with multiple controls in series had no direct measurements of the furnace exit gas before the first control, and those calculations of the exiting furnace gas are reported as zero in the detail data and are blank in the summary data.
Mercury concentrations that are reported as non-detect are estimated as one half the quantification limit.
In a few cases the fraction removed is negative. These negative numbers are reported as calculated on the same basis as the other numbers, without setting the fraction to zero removal. A removal that is less than zero is a physical impossibility and should be viewed as an artifact of the test program.
The mercury loading factors (lb Hg/TBtu) are calculated by two methods, (1) the mercury rate divided by the heating rate of the coal and (2) the concentration of Hg multiplied by an F factor and corrected for oxygen content. The F factor method is thought to be more accurate because of potential problems in reporting coal feed rates and flue gas flow rates.
The two methods for evaluating the mercury loading factors (lb Hg/TBtu) may produce significantly different results. When this difference occurs, the reason is often due to test report inaccuracies of the flow rates of the gas entering the control device. In the case of Montrose, the flow rate into the control device was reported as one fourth of the total flow rate of gas, and the loading based upon this lower flow gas flow rate was also one fourth of the loading based upon concentration (F factor). Possibly three fourths of the flow was diverted to other control units.
In some of the units (Valmont, Craig Unit 3), the mercury concentrations reported for the coal analysis were less than the mercury concentrations reported during the yearly tests. In the case of Valmont, the mass balances of the mercury out of the furnace would have been better if the typical or yearly average values were used. In the case of Craig Unit 3 the mass balances are better with the reported test mercury concentrations in the coal. The reported concentrations for the test data are used for the calculations, with the possible exception of Polk (see the comment for Polk under detail data).
Speciation values were obtained for the runs that reported Hg measured as particulate, oxidized, and elemental directly downstream of the tested unit. In these cases, the fraction of Hg in the speciation was calculated as the average value of the species for the three runs, divided by the average value of the sum of all species for the three runs. The lb Hg/TBtu for each species was the product of the value for the lb total Hg/TBtu and the fraction of Hg for the species.
Speciation values were reported for Hg downstream of the tested unit. In some cases, the speciation values were measured after the return and mixing of gas that bypassed the control device. Estimation of the speciation values by material balance is believed to be in error and is not reported in the data set. Negative values for the particulate and oxidized Hg were calculated and are thought to be in error due to measurement artifacts upstream of the control device or speciation rearrangement during the bypass duct flow.
COAL TESTING TERMS__________________________________________________________
MONTH = The month of the testing, 1 is January, 2 is Feb., etc.
number measurements = The number of mercury concentrations reported for the month.
number nondetects = The number of mercury concentrations reported that were below the quantitation limit.
average Hg in fuel (ppmw) = The monthly average for the fuel type, parts per million by weight.
percent relative deviation (PRD) = The ratio of the standard deviation to the average, expressed as a percentage.
standard deviation (ppmw) = The standard deviation of the monthly mercury concentrations.
highest (ppmw) = The greatest value of the mercury content reported for the month.
lowest (ppmw) = The least value of the mercury content reported for the month.
MISCELLANEOUS TERMS________________________________________________________
Tested control = The name of the tested mercury control device(s).
LOCATION = The position of the exit sample port with respect to the bypass vent where one exists. After control means that the control exit was sampled before the return of the bypass gas. After bypass means that the control exit was sampled after the return of the bypass gas.
name of fuel = In the column heading, this term refers to the fuel type that was tested on a monthly basis.
fuel in test = The fuel type that was burned during the emissions test.
SPECIATION = Refers to the type of mercury that is present: as elemental, as oxidized, or as
sorbed on particulate matter.
ELEMENTAL MERCURY = Mercury that is present in the elemental or unoxidized form in the duct or stack gas stream.
OXIDIZED MERCURY = Mercury that is present in a compound form with chlorine, oxygen, or other
oxidants in the duct or stack gas stream.
PARTICULATE MERCURY= Mercury that is sorbed on the particulate matter in the duct or the stack gas
stream.
UNIT NAME = Most facilities have multiple units. This is the assigned name for the unit that was tested.
average Hg in fuel (ppmw) = The average mercury concentration measured in the fuel (from 1999 year testing).
Cl in test coal (ppmw) = The average chlorine for the coal during the emissions test.
Hg in test coal (ppmw) = The average mercury for the coal during the emissions test.
Hg out furnace/ Hg in coal = The ratio of the mercury in the exiting furnace gas to the mercury in the coal.
This number is expected to equal approximately one.
lb Hg/TBtu out furnace = The pounds of mercury leaving the furnace per trillion Btu in the coal. Estimated from the measured concentrations and flow rates of coal and gas.
F factor lb Hg/TBtu out furnace = The exit concentration in the furnace gas multiplied by a conversion Fuel Factor (F) and corrected for the oxygen concentration in the gas. The Fuel Factor was 9840 dscf/106 Btu. The oxygen correction was 20.9/(20.9-O), where O is the percent oxygen in the combustion gas.
fr.remove coal-stack = The fraction of the mercury in the coal that is removed before exiting the stack.
This estimate assumes that all of the gas is treated by the control device. (corrected for bypass)
fremove control = The fraction of the mercury in the treated gas that is removed by the control device that was tested.
lb Hg/TBtu out control = The pounds of mercury leaving the control per trillion Btu in the coal. Estimated from
the measured concentrations and flow rates of coal and gas.
F factor lb Hg/TBtu out control = The exit Hg concentration from the control device multiplied by a conversion fuel factor (F) and corrected for the oxygen concentration in the gas.
particulate F factor lb Hg/TBtu out control = The concentration of Hg sorbed on particulate that is measured exiting the control device multiplied by a conversion fuel factor (F) and corrected for the oxygen concentration in the gas.
oxidized F factor lb Hg/TBtu out control = The concentration of oxidized Hg that is measured exiting from the control device multiplied by a conversion fuel factor (F) and corrected for the oxygen concentration in the gas.
elemental F factor lb Hg/TBtu out control = The concentration of elemental Hg that is measured exiting from the control device multiplied by a conversion fuel factor (F) and corrected for the oxygen concentration in the gas.
Inlet last control temp (C) = The temperature in Celsius of the gas entering the control device.
stack temp (C) = The temperature in Celsius of the gas exiting the control device. In most cases this is
measured in the stack.
lb Hg/TWH from coal = The Hg emissions (lb Hg) per electric power generation rate (TWH, tera watt hour) from the coal. The fuel rate and heat content is used for the energy rate from coal combustion. Assumes a power conversion efficiency of 0.322. lb Hg/TWH is one million times greater than lb Hg/MWH.
lb Hg/TWH from concentration = The Hg emissions (lb Hg) per electric power generation rate (TWH, tera watt hour) from the coal. The oxygen concentration is used to estimate the energy rate using the F factor. Assumes a power conversion efficiency of 0.322.
lb Hg/MWH from coal = The Hg emissions (lb Hg) per electric power generation rate (MWH, mega watt hour) from the coal. The fuel rate and heat content is used for the energy rate from coal combustion. Assumes a power conversion efficiency of 0.322.
lb Hg/MWH from concentration = The Hg emissions (lb Hg) per electric power generation rate (MWH, mega watt hour) from the coal. The oxygen concentration is used to estimate the energy rate using the F factor. Assumes an energy efficiency conversion to electricity of 0.322.
EMISSION MODIFICATION FACTOR = A fraction with a range of 1.0 - 0.0 that represents the ratio of the mercury discharged from a control device to the mercury present in the control device entrance. If a control device has little effect on the mercury removal, the emission modification factor will beapproximately 1.0. If the control device removes 90% of the mercury, the emission modification factor will be 0.1.
EMF = Abbreviation for Emission Modification Factor
PERCENT REMOVAL = the percent of the mercury that is removed by the control device. In general,
the percent removal is presented as one number that represents the combined effect of the fuel,
the boiler type, the NOX control, the particulate control, and the SOX control.
FURNACE/BOILER = Terms used to describe the combustion device used to convert coal into carbon dioxide and water with the chemical release of heat used to create steam for power generation. The furnace combusts fuel; the boiler converts water to steam.
SOX = Oxides of sulfur. These include precursors of sulfuric acid, formed by reaction with water
in the atmosphere.
NOX = Oxides of nitrogen. These include precursors of nitric acid, formed by reaction with water
in the atmosphere.
PM = Particulate material. Coal contains some minerals that are not consumed in the combustion
process, but remain as ash or particulate material potentially discharged in the stack gas.
FUEL TYPE______________________________________________________________________________
ANTHRACITE = Anthracite coal is a combustible rock composed of organic and mineral materials
that has formed over time by vegetative decay and mineral deposition. The properties of
coal vary depending on the type of vegetative matter and the formation conditions
(reference ASTM D 388-82). In general, anthracite coal has a higher heating content
(Btu/lb) than bituminous coal.
BITUMINOUS = Bituminous coal is a combustible rock composed of organic and mineral materials
that has formed over time by vegetative decay and mineral deposition. The properties of
coal vary depending on the type of vegetative matter and the formation conditions (reference
ASTM D 388-82). Bituminous Coal has a higher heating content (Btu/lb) than Subbituminous
coal.
BITUMINOUS - HIGH SULFUR = Assumed to be a bituminous coal. This
extra nomenclature was sought by certain units participating in the 1999 Electric Utility
Steam Generating Unit Mercury Emissions Information Collection Effort (EU/ICE) in order to
keep their higher and lower sulfur fuels separate.
BITUMINOUS - LOW SULFUR = Assumed to be a bituminous coal. This
extra nomenclature was sought by certain units participating in the 1999 EU/ICE in order to
keep their higher and lower sulfur fuels separate.
SUBBITUMINOUS = Subbituminous coal is a combustible rock composed of organic and mineral
materials that has formed over time by vegetative decay and mineral deposition. The
properties of coal vary depending on the type of vegetative matter and the formation
conditions (reference ASTM D 388-82). Subbituminous coal has a higher heating content
(Btu/lb) than lignite coal.
LIGNITE = Lignite coal is a combustible rock composed of organic and mineral materials that
has formed over time by vegetative decay and mineral deposition. The properties of coal
vary depending on the type of vegetative matter and the formation conditions (reference ASTM
D 388-82). Lignite coal has the lowest higher heating content (Btu/lb) of the four major
coal rankings.
PETROLEUM COKE = Petroleum coke (also called petcoke) is a carbonaceous by-product of the petroleum refining process and is burned as a supplemental fuel with coal.
WASTE BITUMINOUS = Waste bituminous coal reclaimed from mine waste piles.
WASTE SUBBITUMINOUS = Waste subbituminous coal reclaimed from mine waste piles.
WASTE ANTHRACITE = Waste anthracite coal reclaimed from mine waste piles.
TIRES = Tire derived fuel (TDF), that refers to the use of scrap tires as a substitute for a fossil fuel. As with petroleum coke it is burned as a supplemental fuel with coal.
FURNACE TYPE__________________________________________________________________________
CONV/PC = Conventional, pulverized coal-firing furnace. In pulverized-coal-fired boiler
systems, coal is pulverized in a mill to the consistency of talcum powder (i.e., at least 70
percent of the particles will pass through a 200-mesh sieve). The pulverized coal is
generally entrained in primary air before being fed through the burners to the combustion
chamber, where it is fired in suspension.
FBC = Fluidized-bed combustor. In an FBC, combustion occurs when coal, together with inert
material (e.g., sand, silica, alumina, or ash) and/or a sorbent such as limestone, are
suspended through the action of primary combustion air distributed below the combustor
floor. "Fluidized" refers to the state of the bed of material (fuel or fuel and inert
material [or sorbent]) as gas passes through the bed.
COAL GAS = Integrated Coal Gasification Combined Cycle Units. At a coal gasification power
plant the coal-fired boiler unit is replaced with a coal gasification unit coupled with a
gas turbine combustor and heat recovery boiler. The solid coal is gasified by a process in
which a coal/water slurry is reacted at high temperature and pressure with oxygen (or air)
and steam in a vessel (the gasifier) to produce a combustible gas. This combustible gas is
composed of a mixture of carbon dioxide and hydrogen and is often referred to as a synthetic
gas or syngas.
CYCLONE = Cyclone firing uses several water-cooled horizontal burners that produce
high-temperature flames that circulate in a cyclonic pattern. The burner design and
placement cause the ash to become a molten slag that is collected below the furnace.
STOKER = Stoker-fired furnace. In stoker furnaces, coal is burned on a bed at the bottom of
the furnace. The bed of coal burns on a grate. Heated air passes upward through openings
in the grate.
TURBO = Turbo-fired. This furnace is a specialized form of a conventional coal-fired furnace.
WET or DRY = Furnaces are classified as either dry or wet bottom, depending on the ash
removal technique. Dry bottom furnaces fire coals with high ash fusion temperatures, and
dry ash removal techniques are used. In wet bottom (slag tap) furnaces, coal with a low
ash fusion temperature is used, and molten ash is drained from the bottom of the furnace.
NOX control technology_______________________________________________________
NOX = Combustion NOX controls. A variety of combustion control practices can be used
including low NOx burners, overfire air, off-stoichiometric firing, selective or biased
burner firing, reburning, and burners-out-of- service. Control of NOX can also be achieved
through staged combustion (also called air staging).
NONOX = No combustion NOX controls on the furnace.
SCR = Selective Catalytic Reduction (a post combustion, add-on, NOX control device). The
selective catalytic reduction (SCR) process uses a catalyst with ammonia gas (NH3) to reduce
the NO and NO2 in the flue gas to molecular nitrogen and water.
SNCR = Selective Noncatalytic Reduction (a post combustion, add-on, NOX control device).
The selective noncatalytic reduction (SNCR) process is based on the same basic chemistry of
reducing the NO and NO2 in the flue gas to molecular nitrogen and water as the SCR but does
not require the use of a catalyst to prompt these reactions.
Sulfur Dioxide control technology_______________________________________________________
WETSCRUB = A flue gas desulfurization wet scrubber (FGD, [lime or limestone]), in which
flue gas containing SO2 is brought into contact with a limestone-water slurry. The SO2 is
absorbed into the slurry and reacts with limestone to form an insoluble sludge.
COMP COAL = Compliance coal has a specifically desired low sulfur content to bring emissions
into compliance with SO2 regulations. Compliance coal may be obtained through the mining of
lower-sulfur coals, coal washing, and/or coal blending.
SDA = Dry lime/spray dryer adsorber followed by a baghouse. In an SDA, flue gas is
contacted with fine spray droplets of hydrated lime slurry in a spray dryer vessel. The SO2
is absorbed in the slurry and reacts with the hydrated lime reagent to form solid calcium
sulfite and calcium sulfate as in a wet lime scrubber. The water is evaporated by the heat
of the flue gas. The dried solids are entrained in the flue gas, along with fly ash, and
are collected in a baghouse.
SDAESP = Dry lime/spray dryer adsorber followed by a cold-side ESP.
FBC = In an SO2 control context, FBC refers to the use of a sorbent such as limestone in the
furnace's fluidized bed for SO2 control.
SORBENT INJ = Dry injection process, dry powdered lime (or another suitable sorbent) is
directly injected into the ductwork upstream of a PM control device.
SORBESP = A dry injection process (mentioned above) located before a cold-side ESP.
Particulate matter control technology______________________________________________
ESP- CS = Electrostatic precipitator (cold-side, meaning this ESP is installed at a
location downstream of the air preheater). The ESP operates by imparting an electrical charge
to incoming particles, then attracting the particles to oppositely charged plates for
collection. The collected particles are periodically dislodged in sheets or agglomerates by
rapping or otherwise vibrating the plates.
BAGHOUSE = Baghouse (fabric filter) that collects PM by placing a fabric barrier in the
flue gas path. Gas passes freely through the fabric, but particles are trapped and retained
for periodic removal.
MECH/BAGHOUSE = A mechanical collector followed by a fabric filter.
ESP- HS = Electrostatic precipitator (hot-side, meaning this ESP is installed at a location
upstream of the air preheater). Operates by imparting an electrical charge to incoming
particles, then attracting the particles to oppositely charged plates for collection. The
collected particles are periodically dislodged in sheets or agglomerates by rapping or
otherwise vibrating the plates.
ESP- CS/BAGHOUSE = A cold-side ESP followed by a fabric filter.
MECH = Mechanical collector (assumed to be a cyclone collector in this database).
Flue gas entering a cylinder tangentially to the wall is imparted with a circular motion
around the cylinder's axis. Particles in the gas stream are forced toward the wall by
centrifugal force, then downward through a conical discharge at the bottom of the cylinder.
MECH/ESP- CS = A mechanical collector followed by a cold-side ESP.
PARTSCRUB = Particulate scrubber. Particulate scrubbers operate by shattering streams of
water into small droplets that collide with and trap solid particles contained in the flue
gas or by forcing the gases into intimate contact with water films. The particle-laden
droplets or water films coalesce and are collected in a sump at the bottom of the scrubber.
PARTSCRUB/ESP- CS = A cold-side ESP followed by a particulate scrubber.
MECH/PARTSCRUB = A mechanical collector followed by a particulate scrubber.
MECH/BAGHOUSE/ESP- HS = A mechanical collector followed by a hot-side ESP followed by a
fabric filter.
ESP- HS/ESP- CS = A hot-side ESP followed by a cold-side ESP.
ESP- HS/BAGHOUSE = A hot-side ESP followed by a fabric filter.
ESP- CS/ESP- CS = Two cold-side ESPs in series. The first cold-side ESP is less efficient
and requires a particle polisher for the second, more efficient cold-side ESP.

## detail data
Polk Power |  | 1
Boiler/NOx type: | COAL GAS
Particulate control: | NONE
SO2 control: | NONE
Test on entire line boiler to control exit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.05 | 0 | 0.05 | 0.05
2 | 3 | 0 | 0.0567 | 0.0058 | 0.06 | 0.05
3 | 3 | 0 | 0.0533 | 0.0115 | 0.06 | 0.04
7 | 3 | 0 | 0.0967 | 0.0115 | 0.11 | 0.09
9 | 3 | 0 | 0.0833 | 0.0115 | 0.09 | 0.07
10 | 3 | 0 | 0.11 | 0.01 | 0.12 | 0.1
11 | 3 | 0 | 0.1333 | 0.0404 | 0.18 | 0.11
12 | 3 | 0 | 0.1033 | 0.0115 | 0.11 | 0.09
Yearly totals/averages | 24 | 0 | 0.0858 | 0.0323 | 0.18 | 0.04
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
4 | 3 | 0 | 0.02 | 0 | 0.02 | 0.02
5 | 3 | 0 | 0.0367 | 0.0115 | 0.05 | 0.03
6 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
7 | 3 | 0 | 0.0367 | 0.0058 | 0.04 | 0.03
8 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
Yearly totals/averages | 15 | 0 | 0.036 | 0.0106 | 0.05 | 0.02
plant Polk Power | test period | 11/1/1999 | 11/2/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Polk Power | 1 | BITUMINOUS | 0.1 | 0.6169 | 5.156 | 5.8216
Polk Power | 2 | BITUMINOUS | 0.1 | 0.6333 | 4.8966 | 5.3356
Polk Power | 3 | BITUMINOUS | 0.1 | 0.7301 | 5.634 | 5.2566
Averages |  |  | 0.1 | 0.6601 | 5.2289 | 5.4713
Wabash River Generating Station |  | 1 + 1A
Boiler/NOx type: | COAL GAS
Particulate control: | NONE
SO2 control: | NONE
Test on entire line boiler to control exit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 7 | 0 | 0.0651 | 0.0301 | 0.132 | 0.047
2 | 6 | 0 | 0.0723 | 0.0156 | 0.103 | 0.059
3 | 7 | 0 | 0.0499 | 0.0236 | 0.091 | 0.024
4 | 4 | 0 | 0.0713 | 0.0181 | 0.097 | 0.056
5 | 5 | 0 | 0.0746 | 0.0267 | 0.104 | 0.049
6 | 9 | 0 | 0.0899 | 0.0283 | 0.127 | 0.053
7 | 7 | 0 | 0.0827 | 0.0314 | 0.152 | 0.058
8 | 9 | 0 | 0.0754 | 0.0197 | 0.106 | 0.048
9 | 7 | 0 | 0.086 | 0.0177 | 0.117 | 0.064
10 | 6 | 0 | 0.0932 | 0.0369 | 0.16 | 0.054
11 | 6 | 0 | 0.091 | 0.0475 | 0.186 | 0.06
12 | 6 | 0 | 0.0892 | 0.0838 | 0.257 | 0.025
Yearly totals/averages | 79 | 0 | 0.0786 | 0.0352 | 0.257 | 0.024
Fuel number2 | PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
5 | 1 | 0 | 0.071 | 0 | 0.071 | 0.071
9 | 3 | 0 | 0.0063 | 0.0059 | 0.013 | 0.002
Yearly totals/averages | 4 | 0 | 0.0225 | 0.0327 | 0.071 | 0.002
plant Wabash | test period | 10/11/1999 | 10/12/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Wabash | 1 | BITUMINOUS | 0.064 | 0.7153 | 3.7068 | 5.32
Wabash | 2 | BITUMINOUS | 0.068 | 0.607 | 3.2943 | 4.967
Wabash | 3 | BITUMINOUS | 0.07 | 0.7016 | 3.9167 | 5.7157
Averages |  |  | 0.0673 | 0.6747 | 3.6393 | 5.3343
Brayton Point |  | 1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.045 | 0.0058 | 0.05 | 0.04
2 | 3 | 0 | 0.08 | 0.0346 | 0.1 | 0.04
3 | 3 | 0 | 0.0567 | 0.0115 | 0.07 | 0.05
4 | 3 | 0 | 0.0567 | 0.0306 | 0.09 | 0.03
5 | 4 | 0 | 0.0448 | 0.0301 | 0.081 | 0.008
6 | 3 | 0 | 0.039 | 0.0615 | 0.11 | 0.003
7 | 9 | 0 | 0.0636 | 0.0223 | 0.11 | 0.03
8 | 9 | 0 | 0.0702 | 0.0226 | 0.103 | 0.042
9 | 3 | 0 | 0.0467 | 0.0389 | 0.073 | 0.002
10 | 3 | 0 | 0.0567 | 0.0511 | 0.106 | 0.004
11 | 3 | 0 | 0.0787 | 0.0468 | 0.131 | 0.041
12 | 5 | 0 | 0.1186 | 0.0663 | 0.206 | 0.052
Yearly totals/averages | 52 | 0 | 0.0654 | 0.0386 | 0.206 | 0.002
plant Brayton 1 | test period | 8/30/1999 | 9/2/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Brayton 1 | 1 | BITUMINOUS | 0.08 | 0.931 | 5.4427 | 4.2082
Brayton 1 | 2 | BITUMINOUS | 0.05 | 1.7127 | 6.2254 | 4.7876
Brayton 1 | 3 | BITUMINOUS | 0.06 | 1.2574 | 5.4852 | 4.3087
Averages |  |  | 0.0633 | 1.3004 | 5.7178 | 4.4348
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Brayton 1 | 1 | PM/ESP- CS | no bypass | 0.3605 | 0.158 | 3.7385 | 3.5442 | 144
Brayton 1 | 2 | PM/ESP- CS | no bypass | 0.095 | 0.3551 | 3.2894 | 3.0877 | 144
Brayton 1 | 3 | PM/ESP- CS | no bypass | 0.2813 | 0.3113 | 3.1353 | 2.9681 | 141
Averages |  | PM/ESP- CS | no bypass | 0.2456 | 0.2748 | 3.3877 | 3.2 | 143
Brayton Point |  | 3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.045 | 0.0058 | 0.05 | 0.04
2 | 3 | 0 | 0.08 | 0.0346 | 0.1 | 0.04
3 | 3 | 0 | 0.0567 | 0.0115 | 0.07 | 0.05
4 | 3 | 0 | 0.0567 | 0.0306 | 0.09 | 0.03
5 | 4 | 0 | 0.0448 | 0.0301 | 0.081 | 0.008
6 | 3 | 0 | 0.039 | 0.0615 | 0.11 | 0.003
7 | 9 | 0 | 0.0636 | 0.0223 | 0.11 | 0.03
8 | 9 | 0 | 0.0702 | 0.0226 | 0.103 | 0.042
9 | 3 | 0 | 0.0467 | 0.0389 | 0.073 | 0.002
10 | 3 | 0 | 0.0567 | 0.0511 | 0.106 | 0.004
11 | 3 | 0 | 0.0787 | 0.0468 | 0.131 | 0.041
12 | 5 | 0 | 0.1186 | 0.0663 | 0.206 | 0.052
Yearly totals/averages | 52 | 0 | 0.0654 | 0.0386 | 0.206 | 0.002
plant Brayton 3 | test period | 8/30/1999 | 9/2/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Brayton 3 | 1 | BITUMINOUS | 0.1 | 0.9115 | 6.7412 | 5.2658
Brayton 3 | 2 | BITUMINOUS | 0.07 | 1.1222 | 5.7832 | 3.9964
Brayton 3 | 3 | BITUMINOUS | 0.07 | 1.4531 | 7.3308 | 5.4735
Averages |  |  | 0.08 | 1.1622 | 6.6184 | 4.9119
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Brayton 3 | 1 | PM/ESP- CS | no bypass | 0.4951 | 0.3584 | 3.734 | 3.3797 | 127
Brayton 3 | 2 | PM/ESP- CS | no bypass | 0.4081 | 0.2786 | 3.0506 | 2.887 | 126
Brayton 3 | 3 | PM/ESP- CS | no bypass | 0.0301 | 0.1187 | 4.8932 | 4.8269 | 121
Averages |  | PM/ESP- CS | no bypass | 0.3111 | 0.2519 | 3.8926 | 3.6979 | 124.7
Gibson Generating Station |  | 3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | NONE
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 14 | 0 | 0.0939 | 0.0464 | 0.187 | 0.045
2 | 18 | 0 | 0.0898 | 0.0432 | 0.184 | 0.047
3 | 19 | 0 | 0.0758 | 0.0419 | 0.164 | 0.018
4 | 19 | 0 | 0.0761 | 0.043 | 0.164 | 0.02
5 | 26 | 0 | 0.0792 | 0.0475 | 0.17 | 0.016
6 | 23 | 0 | 0.0772 | 0.0454 | 0.17 | 0.023
7 | 27 | 0 | 0.0758 | 0.0529 | 0.207 | 0.025
8 | 26 | 0 | 0.0668 | 0.0469 | 0.19 | 0.022
9 | 24 | 0 | 0.0698 | 0.0466 | 0.169 | 0.024
10 | 26 | 0 | 0.0737 | 0.0516 | 0.198 | 0.024
11 | 24 | 0 | 0.0835 | 0.0565 | 0.199 | 0.022
12 | 21 | 0 | 0.0757 | 0.0458 | 0.174 | 0.027
Yearly totals/averages | 267 | 0 | 0.0772 | 0.0474 | 0.207 | 0.016
plant Gibson 0300 | test period | 3/28/2000 | 3/30/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Gibson0300 | 1 | BITUMINOUS | 0.117 | 2.7811 | 27.9545 | 27.3399
Gibson0300 | 2 | BITUMINOUS | 0.115 | 3.1675 | 31.3207 | 30.3232
Gibson0300 | 3 | BITUMINOUS | 0.123 | 3.5363 | 37.6593 | 34.3581
Averages |  |  | 0.1183 | 3.1616 | 32.3115 | 30.6737
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Gibson0300 | 1 | PM/ESP- CS | no bypass | -1.856 | -0.0396 | 28.7071 | 28.475 | 154
Gibson0300 | 2 | PM/ESP- CS | no bypass | -1.9382 | 0.0985 | 29.0534 | 27.3746 | 154
Gibson0300 | 3 | PM/ESP- CS | no bypass | -2.2371 | 0.0895 | 34.4729 | 31.3345 | 157
Averages |  | PM/ESP- CS | no bypass | -2.0104 | 0.0495 | 30.7445 | 29.0614 | 155
Gibson Generating Station |  | 3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | NONE
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 14 | 0 | 0.0939 | 0.0464 | 0.187 | 0.045
2 | 18 | 0 | 0.0898 | 0.0432 | 0.184 | 0.047
3 | 19 | 0 | 0.0758 | 0.0419 | 0.164 | 0.018
4 | 19 | 0 | 0.0761 | 0.043 | 0.164 | 0.02
5 | 26 | 0 | 0.0792 | 0.0475 | 0.17 | 0.016
6 | 23 | 0 | 0.0772 | 0.0454 | 0.17 | 0.023
7 | 27 | 0 | 0.0758 | 0.0529 | 0.207 | 0.025
8 | 26 | 0 | 0.0668 | 0.0469 | 0.19 | 0.022
9 | 24 | 0 | 0.0698 | 0.0466 | 0.169 | 0.024
10 | 26 | 0 | 0.0737 | 0.0516 | 0.198 | 0.024
11 | 24 | 0 | 0.0835 | 0.0565 | 0.199 | 0.022
12 | 21 | 0 | 0.0757 | 0.0458 | 0.174 | 0.027
Yearly totals/averages | 267 | 0 | 0.0772 | 0.0474 | 0.207 | 0.016
plant Gibson1099 | test period | 10/13/1999 | 10/15/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Gibson1099 | 1 | BITUMINOUS | 0.134 | 1.3154 | 14.0676 | 13.2244
Gibson1099 | 2 | BITUMINOUS | 0.142 | 2.1803 | 24.6306 | 23.6145
Gibson1099 | 3 | BITUMINOUS | 0.141 | 1.2022 | 13.4858 | 12.5768
Averages |  |  | 0.139 | 1.566 | 17.3947 | 16.4719
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Gibson1099 | 1 | PM/ESP- CS | no bypass | 0.1298 | 0.3891 | 9.3061 | 8.0797 | 171
Gibson1099 | 2 | PM/ESP- CS | no bypass | -0.0921 | 0.5849 | 12.3374 | 9.8055 | 171
Gibson1099 | 3 | PM/ESP- CS | no bypass | -0.544 | 0.0977 | 17.3196 | 11.3506 | 173
Averages |  | PM/ESP- CS | no bypass | -0.1688 | 0.3572 | 12.9877 | 9.7452 | 171.7
Jack Watson |  | 4
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | NONE
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 11 | 0 | 0.0945 | 0.043 | 0.16 | 0.03
2 | 21 | 0 | 0.0919 | 0.0528 | 0.19 | 0.01
3 | 16 | 0 | 0.095 | 0.0495 | 0.24 | 0.03
4 | 12 | 0 | 0.1008 | 0.0247 | 0.13 | 0.05
5 | 17 | 0 | 0.0935 | 0.0146 | 0.12 | 0.07
6 | 18 | 0 | 0.1056 | 0.0162 | 0.15 | 0.08
7 | 16 | 0 | 0.09 | 0.0132 | 0.12 | 0.07
8 | 5 | 0 | 0.064 | 0.0114 | 0.08 | 0.05
9 | 7 | 0 | 0.0629 | 0.0229 | 0.1 | 0.04
10 | 11 | 0 | 0.0864 | 0.0294 | 0.13 | 0.01
11 | 10 | 0 | 0.093 | 0.0183 | 0.12 | 0.05
12 | 5 | 0 | 0.082 | 0.0045 | 0.09 | 0.08
Yearly totals/averages | 149 | 0 | 0.0918 | 0.0328 | 0.24 | 0.01
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 27 | 0 | 0.15 | 0 | 0.15 | 0.15
2 | 35 | 0 | 0.17 | 0 | 0.17 | 0.17
3 | 9 | 0 | 0.19 | 0 | 0.19 | 0.19
6 | 9 | 0 | 0.18 | 0 | 0.18 | 0.18
7 | 19 | 0 | 0.11 | 0 | 0.11 | 0.11
Yearly totals/averages | 99 | 0 | 0.1558 | 0.0255 | 0.19 | 0.11
plant Watson | test period | 1/19/2000 | 1/20/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Watson | 1 | BITUMINOUS | 0.05 | 1.2211 | 4.6679 | 4.1228
Watson | 2 | BITUMINOUS | 0.052 | 1.1151 | 4.4331 | 4.5387
Watson | 3 | BITUMINOUS | 0.059 | 0.8599 | 3.8819 | 3.8288
Averages |  |  | 0.0537 | 1.0654 | 4.3276 | 4.1634
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Watson | 1 | PM/ESP- CS | no bypass | 0.0492 | 0.2213 | 3.6347 | 3.2096 | 157
Watson | 2 | PM/ESP- CS | no bypass | 0.3053 | 0.377 | 2.7618 | 2.8282 | 150
Watson | 3 | PM/ESP- CS | no bypass | 0.3796 | 0.2786 | 2.8005 | 2.7621 | 150
Averages |  | PM/ESP- CS | no bypass | 0.2447 | 0.2923 | 3.0657 | 2.9333 | 152.3
Widows Creek Fossil Plant |  | 6
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 11 | 1 | 0.0751 | 0.0312 | 0.12 | 0.0064
2 | 5 | 0 | 0.094 | 0.0297 | 0.14 | 0.06
3 | 7 | 0 | 0.0871 | 0.0229 | 0.12 | 0.06
4 | 12 | 0 | 0.0974 | 0.0518 | 0.2086 | 0.0427
5 | 16 | 0 | 0.1039 | 0.0461 | 0.1732 | 0.0169
6 | 13 | 0 | 0.095 | 0.0384 | 0.1494 | 0.0325
7 | 11 | 0 | 0.0821 | 0.0273 | 0.1305 | 0.0283
8 | 14 | 0 | 0.0661 | 0.0314 | 0.1388 | 0.0279
9 | 16 | 0 | 0.083 | 0.0299 | 0.1383 | 0.0214
10 | 23 | 0 | 0.0765 | 0.0387 | 0.1403 | 0.0134
11 | 13 | 0 | 0.0739 | 0.0406 | 0.1278 | 0.017
12 | 15 | 0 | 0.0901 | 0.0485 | 0.1892 | 0.0255
Yearly totals/averages | 156 | 1 | 0.0846 | 0.0389 | 0.2086 | 0.0064
plant Widow | test period | 10/19/1999 | 10/21/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Widow | 1 | BITUMINOUS | 0.029 | 1.3946 | 3.2014 | 3.1156
Widow | 2 | BITUMINOUS | 0.024 | 1.4749 | 2.7775 | 2.8278
Widow | 3 | BITUMINOUS | 0.021 | 1.7824 | 2.9314 | 2.7494
Averages |  |  | 0.0247 | 1.5506 | 2.9701 | 2.8976
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Widow | 1 | PM/ESP- CS | no bypass | 0.2844 | 0.4411 | 1.6426 | 1.7438 | 162
Widow | 2 | PM/ESP- CS | no bypass | 0.2271 | 0.49 | 1.4556 | 1.4432 | 158
Widow | 3 | PM/ESP- CS | no bypass | 0.3858 | 0.6336 | 1.0101 | 1.0087 | 151
Averages |  | PM/ESP- CS | no bypass | 0.2991 | 0.5216 | 1.3695 | 1.3986 | 157
Presque Isle |  | 5
Boiler/NOx type: | CONV/PC/NONOX/WET
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.043 | 0.0087 | 0.048 | 0.033
2 | 4 | 0 | 0.0523 | 0.016 | 0.071 | 0.032
3 | 5 | 0 | 0.0408 | 0.0097 | 0.051 | 0.029
4 | 3 | 0 | 0.0273 | 0.0021 | 0.029 | 0.025
5 | 5 | 0 | 0.0282 | 0.0246 | 0.072 | 0.014
6 | 4 | 0 | 0.0127 | 0.0041 | 0.016 | 0.0076
7 | 4 | 0 | 0.0284 | 0.0298 | 0.072 | 0.0091
8 | 4 | 0 | 0.0225 | 0.0066 | 0.029 | 0.015
9 | 5 | 0 | 0.0442 | 0.0427 | 0.12 | 0.019
10 | 4 | 0 | 0.017 | 0.0062 | 0.022 | 0.008
11 | 5 | 0 | 0.0208 | 0.0055 | 0.027 | 0.015
12 | 4 | 0 | 0.0215 | 0.0048 | 0.026 | 0.015
Yearly totals/averages | 50 | 0 | 0.03 | 0.0208 | 0.12 | 0.0076
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.056 | 0.0074 | 0.067 | 0.051
2 | 4 | 0 | 0.0455 | 0.0055 | 0.051 | 0.039
3 | 5 | 0 | 0.0536 | 0.0084 | 0.063 | 0.044
4 | 4 | 0 | 0.0588 | 0.005 | 0.063 | 0.052
5 | 5 | 0 | 0.036 | 0.007 | 0.043 | 0.027
6 | 4 | 0 | 0.0423 | 0.0083 | 0.049 | 0.031
7 | 4 | 0 | 0.031 | 0.0088 | 0.039 | 0.022
8 | 4 | 0 | 0.0608 | 0.0266 | 0.1 | 0.041
9 | 5 | 0 | 0.0576 | 0.0108 | 0.07 | 0.046
10 | 4 | 0 | 0.0418 | 0.0069 | 0.049 | 0.033
11 | 5 | 0 | 0.0698 | 0.0159 | 0.088 | 0.048
12 | 4 | 0 | 0.0538 | 0.0096 | 0.063 | 0.042
Yearly totals/averages | 52 | 0 | 0.0508 | 0.015 | 0.1 | 0.022
plant Presque Isle 5 | test period | 7/12/1999 | 7/20/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Presque Isle 5 | 1 | BITUMINOUS/ PETCOKE | 0.0454 | 1.2798 | 4.5496 | 3.7132
Presque Isle 5 | 2 | BITUMINOUS/ PETCOKE | 0.04 | 1.4604 | 4.5675 | 3.461
Presque Isle 5 | 3 | BITUMINOUS/ PETCOKE | 0.0433 | 1.5474 | 5.2543 | 4.1238
Averages |  |  | 0.0429 | 1.4292 | 4.7905 | 3.766
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Presque Isle 5 | 1 | PM/ESP- CS | no bypass | 0.6615 | 0.6529 | 1.2035 | 1.2889 | 171.1
Presque Isle 5 | 2 | PM/ESP- CS | no bypass | 0.5746 | 0.6187 | 1.3304 | 1.3197 | 172.8
Presque Isle 5 | 3 | PM/ESP- CS | no bypass | 0.6486 | 0.7144 | 1.1932 | 1.178 | 171.7
Averages |  | PM/ESP- CS | no bypass | 0.6282 | 0.662 | 1.2424 | 1.2622 | 171.9
Presque Isle |  | 6
Boiler/NOx type: | CONV/PC/NONOX/WET
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.043 | 0.0087 | 0.048 | 0.033
2 | 4 | 0 | 0.0523 | 0.016 | 0.071 | 0.032
3 | 5 | 0 | 0.0408 | 0.0097 | 0.051 | 0.029
4 | 3 | 0 | 0.0273 | 0.0021 | 0.029 | 0.025
5 | 5 | 0 | 0.0282 | 0.0246 | 0.072 | 0.014
6 | 4 | 0 | 0.0127 | 0.0041 | 0.016 | 0.0076
7 | 4 | 0 | 0.0284 | 0.0298 | 0.072 | 0.0091
8 | 4 | 0 | 0.0225 | 0.0066 | 0.029 | 0.015
9 | 5 | 0 | 0.0442 | 0.0427 | 0.12 | 0.019
10 | 4 | 0 | 0.017 | 0.0062 | 0.022 | 0.008
11 | 5 | 0 | 0.0208 | 0.0055 | 0.027 | 0.015
12 | 4 | 0 | 0.0215 | 0.0048 | 0.026 | 0.015
Yearly totals/averages | 50 | 0 | 0.03 | 0.0208 | 0.12 | 0.0076
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.056 | 0.0074 | 0.067 | 0.051
2 | 4 | 0 | 0.0455 | 0.0055 | 0.051 | 0.039
3 | 5 | 0 | 0.0536 | 0.0084 | 0.063 | 0.044
4 | 4 | 0 | 0.0588 | 0.005 | 0.063 | 0.052
5 | 5 | 0 | 0.036 | 0.007 | 0.043 | 0.027
6 | 4 | 0 | 0.0423 | 0.0083 | 0.049 | 0.031
7 | 4 | 0 | 0.031 | 0.0088 | 0.039 | 0.022
8 | 4 | 0 | 0.0608 | 0.0266 | 0.1 | 0.041
9 | 5 | 0 | 0.0576 | 0.0108 | 0.07 | 0.046
10 | 4 | 0 | 0.0418 | 0.0069 | 0.049 | 0.033
11 | 5 | 0 | 0.0698 | 0.0159 | 0.088 | 0.048
12 | 4 | 0 | 0.0538 | 0.0096 | 0.063 | 0.042
Yearly totals/averages | 52 | 0 | 0.0508 | 0.015 | 0.1 | 0.022
plant Presque Isle 6 | test period | 7/14/1999 | 7/16/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Presque Isle 6 | 1 | BITUMINOUS/ PETCOKE | 0.0264 | 1.6215 | 3.3675 | 2.5272
Presque Isle 6 | 2 | BITUMINOUS/ PETCOKE | 0.0485 | 0.9567 | 3.6275 | 2.8263
Presque Isle 6 | 3 | BITUMINOUS/ PETCOKE | 0.0432 | 1.0243 | 3.4649 | 2.6898
Averages |  |  | 0.0393 | 1.2009 | 3.4866 | 2.6811
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Presque Isle 6 | 1 | PM/ESP- CS | no bypass | 0.4498 | 0.5454 | 1.1426 | 1.1494 | 151.7
Presque Isle 6 | 2 | PM/ESP- CS | no bypass | 0.6143 | 0.5029 | 1.4623 | 1.4055 | 151.1
Presque Isle 6 | 3 | PM/ESP- CS | no bypass | 0.6763 | 0.5873 | 1.0948 | 1.1103 | 152.2
Averages |  | PM/ESP- CS | no bypass | 0.5802 | 0.5452 | 1.2333 | 1.2217 | 151.7
Salem Harbor |  | 3
Boiler/NOx type: | CONV/PC/NOX/SNCR/DRY
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0833 | 0.0321 | 0.12 | 0.06
2 | 3 | 0 | 0.07 | 0.0265 | 0.1 | 0.05
3 | 3 | 0 | 0.0567 | 0.0208 | 0.08 | 0.04
4 | 3 | 0 | 0.0567 | 0.0115 | 0.07 | 0.05
5 | 1 | 0 | 0.08 | 0 | 0.08 | 0.08
6 | 3 | 0 | 0.0763 | 0.0228 | 0.09 | 0.05
7 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
8 | 3 | 0 | 0.074 | 0.0242 | 0.1 | 0.052
9 | 3 | 0 | 0.0047 | 0.0006 | 0.005 | 0.004
10 | 3 | 0 | 0.0867 | 0.0153 | 0.1 | 0.07
11 | 3 | 0 | 0.0467 | 0.0058 | 0.05 | 0.04
12 | 3 | 0 | 0.0227 | 0.0038 | 0.027 | 0.02
Yearly totals/averages | 34 | 0 | 0.0571 | 0.029 | 0.12 | 0.004
plant Salem | test period | 8/23/1999 | 8/25/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Salem | 1 | BITUMINOUS | 0.03 | 1.5998 | 3.4555 | 3.5757
Salem | 2 | BITUMINOUS | 0.02 | 2.0977 | 3.0291 | 3.1102
Salem | 3 | BITUMINOUS | 0.03 | 1.4054 | 3.0759 | 3.0175
Averages |  |  | 0.0267 | 1.701 | 3.1869 | 3.2345
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Salem | 1 | PM/ESP- CS | no bypass | 0.7752 | 0.8547 | 0.4856 | 0.5198 | 128
Salem | 2 | PM/ESP- CS | no bypass | 0.8337 | 0.9252 | 0.2401 | 0.2326 | 128
Salem | 3 | PM/ESP- CS | no bypass | 0.8805 | 0.9165 | 0.2615 | 0.252 | 130
Averages |  | PM/ESP- CS | no bypass | 0.8298 | 0.8988 | 0.3291 | 0.3348 | 128.7
Cliffside |  | 1
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- HS
SO2 control: | NONE
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.05 | 0.0212 | 0.074 | 0.034
2 | 3 | 0 | 0.0673 | 0.0058 | 0.074 | 0.064
3 | 3 | 0 | 0.0513 | 0.0168 | 0.066 | 0.033
4 | 3 | 0 | 0.0467 | 0.0208 | 0.07 | 0.03
5 | 4 | 0 | 0.0525 | 0.0263 | 0.09 | 0.03
6 | 4 | 0 | 0.05 | 0.0082 | 0.06 | 0.04
7 | 3 | 0 | 0.06 | 0.0115 | 0.069 | 0.047
8 | 3 | 0 | 0.032 | 0.0026 | 0.035 | 0.03
9 | 3 | 0 | 0.0557 | 0.0235 | 0.076 | 0.03
10 | 3 | 0 | 0.047 | 0.0277 | 0.079 | 0.031
11 | 3 | 0 | 0.0607 | 0.0241 | 0.086 | 0.038
12 | 3 | 0 | 0.0553 | 0.0015 | 0.057 | 0.054
Yearly totals/averages | 38 | 0 | 0.0523 | 0.0175 | 0.09 | 0.03
plant Cliffside | test period | 9/1/1999 | 9/2/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Cliffside | 1 | BITUMINOUS | 0.07 | 1.3271 | 6.7304 | 5.1663
Cliffside | 2 | BITUMINOUS | 0.05 | 2.1514 | 8.1609 | 5.932
Cliffside | 3 | BITUMINOUS | 0.06 | 2.3936 | 10.4039 | 8.2477
Averages |  |  | 0.06 | 1.9574 | 8.4317 | 6.4487
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Cliffside | 1 | PM/ESP- HS | no bypass | -0.1503 | 0.0086 | 5.8337 | 5.1265 | 195.1
Cliffside | 2 | PM/ESP- HS | no bypass | 0.0127 | 0.4786 | 3.7453 | 3.0953 | 196.6
Cliffside | 3 | PM/ESP- HS | no bypass | -0.2352 | 0.4251 | 5.3688 | 4.745 | 191.7
Averages |  | PM/ESP- HS | no bypass | -0.1243 | 0.3041 | 4.9826 | 4.3223 | 194.5
Dunkirk |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- HS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0343 | 0.0304 | 0.068 | 0.009
2 | 6 | 0 | 0.0828 | 0.0212 | 0.119 | 0.061
3 | 3 | 0 | 0.0553 | 0.0075 | 0.064 | 0.051
4 | 3 | 0 | 0.083 | 0.007 | 0.091 | 0.078
5 | 3 | 0 | 0.0937 | 0.0178 | 0.114 | 0.081
6 | 3 | 0 | 0.081 | 0.0201 | 0.1 | 0.06
7 | 3 | 0 | 0.1253 | 0.0031 | 0.128 | 0.122
8 | 3 | 0 | 0.1157 | 0.005 | 0.121 | 0.111
9 | 3 | 0 | 0.0783 | 0.0133 | 0.087 | 0.063
10 | 3 | 0 | 0.1313 | 0.0006 | 0.132 | 0.131
11 | 3 | 0 | 0.1113 | 0.0163 | 0.13 | 0.1
12 | 3 | 0 | 0.098 | 0.0373 | 0.121 | 0.055
Yearly totals/averages | 39 | 0 | 0.0902 | 0.0307 | 0.132 | 0.009
plant Dunkirk | test period | 10/12/1999 | 10/13/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Dunkirk | 1 | BITUMINOUS | 0.13 | 1.1493 | 10.7435 | 8.2962
Dunkirk | 2 | BITUMINOUS | 0.13 | 1.0312 | 9.56 | 7.6228
Dunkirk | 3 | BITUMINOUS | 0.13 | 1.3104 | 12.3271 | 9.0725
Averages |  |  | 0.13 | 1.1636 | 10.8768 | 8.3305
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Dunkirk | 1 | PM/ESP- HS | no bypass | -0.0424 | 0.0502 | 9.7439 | 7.8828 | 293.4
Dunkirk | 2 | PM/ESP- HS | no bypass | 0.3359 | 0.3232 | 6.1566 | 5.1609 | 295.2
Dunkirk | 3 | PM/ESP- HS | no bypass | 0.0122 | 0.1886 | 9.2924 | 7.3652 | 295.8
Averages |  | PM/ESP- HS | no bypass | 0.1019 | 0.1873 | 8.3976 | 6.803 | 294.8
Gaston |  | 1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- HS
SO2 control: | NONE
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 30 | 0 | 0.1343 | 0.0799 | 0.21 | 0.01
2 | 29 | 0 | 0.1459 | 0.0668 | 0.22 | 0.01
3 | 33 | 0 | 0.1518 | 0.0853 | 0.26 | 0.01
4 | 5 | 0 | 0.076 | 0.0662 | 0.18 | 0.01
5 | 16 | 0 | 0.1875 | 0.0809 | 0.25 | 0.02
6 | 11 | 0 | 0.1436 | 0.1529 | 0.37 | 0.01
7 | 10 | 0 | 0.099 | 0.0664 | 0.18 | 0.01
8 | 4 | 0 | 0.07 | 0.0606 | 0.15 | 0.01
9 | 5 | 0 | 0.098 | 0.0522 | 0.16 | 0.06
10 | 6 | 0 | 0.0433 | 0.0197 | 0.07 | 0.02
11 | 6 | 0 | 0.0933 | 0.0393 | 0.15 | 0.05
12 | 4 | 0 | 0.13 | 0.0294 | 0.16 | 0.09
Yearly totals/averages | 159 | 0 | 0.1342 | 0.0849 | 0.37 | 0.01
plant Gaston | test period | 11/10/1999 | 11/11/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Gaston | 1 | BITUMINOUS | 0.054 | 1.4928 | 5.9447 | 5.5736
Gaston | 2 | BITUMINOUS | 0.067 | 1.0907 | 5.4944 | 4.9047
Gaston | 3 | BITUMINOUS | 0.057 | 1.531 | 6.3977 | 5.1659
Averages |  |  | 0.0593 | 1.3715 | 5.9456 | 5.2148
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Gaston | 1 | PM/ESP- HS | no bypass | -0.2691 | -0.0019 | 5.0541 | 5.5912 | 128
Gaston | 2 | PM/ESP- HS | no bypass | -0.4092 | -0.4137 | 7.0988 | 6.9419 | 124
Gaston | 3 | PM/ESP- HS | no bypass | -0.5211 | -0.1 | 6.3566 | 5.6881 | 128
Averages |  | PM/ESP- HS | no bypass | -0.3998 | -0.1719 | 6.1698 | 6.0738 | 126.7
Bruce Mansfield |  | 1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | PARTSCRUB
SO2 control: | NONE
Test on last control unit
Fuel number1 | PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 1 | 1 | 0.01 | 0 | 0.01 | 0.01
2 | 1 | 1 | 0.01 | 0 | 0.01 | 0.01
3 | 1 | 1 | 0.01 | 0 | 0.01 | 0.01
Yearly totals/averages | 3 | 3 | 0.01 | 0 | 0.01 | 0.01
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 41 | 0 | 0.1522 | 0.055 | 0.42 | 0.08
2 | 38 | 0 | 0.1195 | 0.0509 | 0.32 | 0.07
3 | 26 | 0 | 0.1027 | 0.0367 | 0.16 | 0.05
4 | 34 | 0 | 0.1506 | 0.0914 | 0.5 | 0.1
5 | 23 | 0 | 0.1396 | 0.0533 | 0.33 | 0.1
6 | 27 | 2 | 0.1452 | 0.0533 | 0.22 | 0.01
7 | 39 | 0 | 0.1385 | 0.0797 | 0.44 | 0.08
8 | 27 | 0 | 0.1619 | 0.1006 | 0.46 | 0.07
9 | 41 | 0 | 0.122 | 0.0205 | 0.18 | 0.1
10 | 48 | 0 | 0.1044 | 0.0272 | 0.23 | 0.05
11 | 62 | 0 | 0.1284 | 0.0475 | 0.33 | 0.08
12 | 52 | 0 | 0.144 | 0.0505 | 0.32 | 0.08
Yearly totals/averages | 458 | 2 | 0.133 | 0.0596 | 0.5 | 0.01
plant Mansfield | test period | 9/20/1999 | 9/22/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Mansfield | 1 | BITUMINOUS | 0.096 | 0.9755 | 7.1144 | 7.6566
Mansfield | 2 | BITUMINOUS | 0.079 | 1.4175 | 8.1871 | 9.0885
Mansfield | 3 | BITUMINOUS | 0.103 | 0.8846 | 6.8835 | 7.5096
Averages |  |  | 0.0927 | 1.0925 | 7.395 | 8.0849
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Mansfield | 1 | PM/PARTSCRUB | no bypass | 0.2142 | 0.1468 | 5.7306 | 6.5333 | 52
Mansfield | 2 | PM/PARTSCRUB | no bypass | -0.156 | 0.1402 | 6.6765 | 7.8147 | 53
Mansfield | 3 | PM/PARTSCRUB | no bypass | 0.1814 | 0.0751 | 6.3695 | 6.9473 | 52
Averages |  | PM/PARTSCRUB | no bypass | 0.0799 | 0.1207 | 6.2589 | 7.0985 | 52.3
Port Washington |  | 4
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- CS
SO2 control: | SORBENT INJ
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.0593 | 0.0223 | 0.078 | 0.034
2 | 4 | 0 | 0.0558 | 0.0145 | 0.077 | 0.045
3 | 5 | 0 | 0.087 | 0.0062 | 0.092 | 0.078
4 | 4 | 0 | 0.0873 | 0.0222 | 0.1 | 0.054
5 | 4 | 0 | 0.082 | 0.0063 | 0.087 | 0.074
6 | 5 | 0 | 0.0808 | 0.0079 | 0.091 | 0.072
7 | 4 | 0 | 0.106 | 0.0238 | 0.13 | 0.077
8 | 5 | 0 | 0.13 | 0.0071 | 0.14 | 0.12
9 | 4 | 0 | 0.115 | 0.0129 | 0.13 | 0.1
10 | 4 | 0 | 0.1008 | 0.0127 | 0.11 | 0.083
11 | 5 | 0 | 0.126 | 0.0114 | 0.14 | 0.11
12 | 1 | 0 | 0.13 | 0 | 0.13 | 0.13
Yearly totals/averages | 49 | 0 | 0.0954 | 0.0272 | 0.14 | 0.034
plant Washington | test period | 11/17/1999 | 11/17/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Washington | 1 | BITUMINOUS | 0.09 | 1.9086 | 12.2475 | 11.4572
Washington | 2 | BITUMINOUS | 0.09 | 2.1861 | 14.1071 | 13.4726
Washington | 3 | BITUMINOUS | 0.09 | 1.9086 | 12.2855 | 11.7382
Averages |  |  | 0.09 | 2.0011 | 12.88 | 12.2227
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Washington | 1 | SO2/SORBENT INJ | no bypass | -0.0169 | 0.4068 | 6.5258 | 6.8012 | 204.5
Washington | 2 | SO2/SORBENT INJ | no bypass | 0.0697 | 0.5262 | 6.0034 | 6.3876 | 206.3
Washington | 3 | SO2/SORBENT INJ | no bypass | -0.0173 | 0.4137 | 6.5479 | 6.886 | 206.8
Averages |  | SO2/SORBENT INJ | no bypass | 0.0118 | 0.4489 | 6.359 | 6.6916 | 205.9
W. H. Sammis |  | 1
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | NONE
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 27 | 0 | 0.1033 | 0.0279 | 0.14 | 0.04
2 | 80 | 0 | 0.1051 | 0.0319 | 0.17 | 0.01
3 | 69 | 0 | 0.1059 | 0.0365 | 0.23 | 0.04
4 | 30 | 0 | 0.1103 | 0.0347 | 0.17 | 0.05
5 | 17 | 0 | 0.0782 | 0.0288 | 0.12 | 0.03
6 | 14 | 0 | 0.1043 | 0.0399 | 0.17 | 0.04
7 | 27 | 0 | 0.0822 | 0.0323 | 0.15 | 0.01
8 | 37 | 0 | 0.0984 | 0.0278 | 0.15 | 0.04
9 | 28 | 0 | 0.1025 | 0.0246 | 0.17 | 0.05
10 | 48 | 0 | 0.0977 | 0.022 | 0.13 | 0.04
11 | 14 | 0 | 0.1 | 0.0604 | 0.24 | 0.04
12 | 27 | 0 | 0.1019 | 0.0208 | 0.14 | 0.05
Yearly totals/averages | 418 | 0 | 0.1009 | 0.0324 | 0.24 | 0.01
plant Sammis | test period | 9/22/1999 | 9/24/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Sammis | 1 | BITUMINOUS | 0.081 | 1.936 | 12.8517 | 9.2273
Sammis | 2 | BITUMINOUS | 0.12 | 1.718 | 15.1655 | 11.764
Sammis | 3 | BITUMINOUS | 0.117 | 1.638 | 14.1633 | 11.2367
Averages |  |  | 0.106 | 1.764 | 14.0602 | 10.7427
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Sammis | 1 | PM/BAGHOUSE | no bypass | 0.8412 | 0.9118 | 1.0544 | 0.814 | 153
Sammis | 2 | PM/BAGHOUSE | no bypass | 0.8826 | 0.9265 | 1.0367 | 0.865 | 149
Sammis | 3 | PM/BAGHOUSE | no bypass | 0.8911 | 0.9281 | 0.9417 | 0.8082 | 150
Averages |  | PM/BAGHOUSE | no bypass | 0.8716 | 0.9221 | 1.0109 | 0.8291 | 150.7
Valmont |  | 5
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0403 | 0.0248 | 0.058 | 0.012
2 | 2 | 0 | 0.04 | 0.0184 | 0.053 | 0.027
3 | 2 | 0 | 0.029 | 0.0014 | 0.03 | 0.028
7 | 1 | 0 | 0.063 | 0 | 0.063 | 0.063
8 | 1 | 0 | 0.038 | 0 | 0.038 | 0.038
9 | 3 | 0 | 0.0553 | 0.0177 | 0.067 | 0.035
10 | 3 | 0 | 0.027 | 0.0082 | 0.034 | 0.018
11 | 2 | 0 | 0.027 | 0.0099 | 0.034 | 0.02
12 | 2 | 0 | 0.0385 | 0.0007 | 0.039 | 0.038
Yearly totals/averages | 19 | 0 | 0.0388 | 0.0162 | 0.067 | 0.012
plant Valmont | test period | 11/2/1999 | 11/3/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Valmont | 1 | BITUMINOUS | 0.01 | 1.5333 | 1.2467 | 0.878
Valmont | 2 | BITUMINOUS | 0.0055 | 2.5584 | 1.1493 | 0.8065
Valmont | 3 | BITUMINOUS | 0.0083 | 2.3994 | 1.7158 | 1.0838
Averages |  |  | 0.0079 | 2.1637 | 1.3706 | 0.9228
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Valmont | 1 | PM/BAGHOUSE | no bypass | 0.8342 | 0.866 | 0.1348 | 0.1176 | 134
Valmont | 2 | PM/BAGHOUSE | no bypass | 0.7814 | 0.8911 | 0.0982 | 0.0878 | 138
Valmont | 3 | PM/BAGHOUSE | no bypass | 0.7043 | 0.8385 | 0.2114 | 0.1751 | 148
Averages |  | PM/BAGHOUSE | no bypass | 0.7733 | 0.8652 | 0.1481 | 0.1268 | 140
Mecklenburg Cogeneration Facility |  | GEN 1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
2 | 4 | 0 | 0.125 | 0.0759 | 0.2 | 0.05
3 | 5 | 0 | 0.082 | 0.0217 | 0.1 | 0.05
4 | 4 | 0 | 0.0725 | 0.0126 | 0.09 | 0.06
7 | 4 | 0 | 0.095 | 0.0058 | 0.1 | 0.09
8 | 5 | 0 | 0.092 | 0.0295 | 0.14 | 0.06
9 | 6 | 0 | 0.0883 | 0.0117 | 0.1 | 0.07
10 | 3 | 0 | 0.0867 | 0.0058 | 0.09 | 0.08
11 | 4 | 0 | 0.1 | 0.0606 | 0.19 | 0.06
12 | 6 | 1 | 0.0983 | 0.0591 | 0.2 | 0.05
Yearly totals/averages | 41 | 1 | 0.0932 | 0.0386 | 0.2 | 0.05
plant Mecklenburg | test period | 10/11/1999 | 10/13/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Mecklenburg | 1 | BITUMINOUS | 0.09 | 1.9741 | 12.6529 | 15.4373
Mecklenburg | 2 | BITUMINOUS | 0.11 | 0.7958 | 6.308 | 7.1527
Mecklenburg | 3 | BITUMINOUS | 0.09 | 0.9396 | 6.098 | 7.1998
Averages |  |  | 0.0967 | 1.2365 | 8.353 | 9.9299
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Mecklenburg | 1 | SO2/SDA | no bypass | 0.9822 | 0.9923 | 0.114 | 0.1182 | 75.5
Mecklenburg | 2 | SO2/SDA | no bypass | 0.9861 | 0.9842 | 0.1102 | 0.1128 | 74.4
Mecklenburg | 3 | SO2/SDA | no bypass | 0.987 | 0.9878 | 0.0847 | 0.0877 | 73.9
Averages |  | SO2/SDA | no bypass | 0.9851 | 0.9881 | 0.1029 | 0.1062 | 74.6
Logan Generating Plant |  | GEN 1
Boiler/NOx type: | CONV/PC/NOX/SCR/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.1033 | 0.0153 | 0.12 | 0.09
2 | 3 | 0 | 0.17 | 0.01 | 0.18 | 0.16
3 | 4 | 0 | 0.1625 | 0.0479 | 0.22 | 0.11
4 | 2 | 0 | 0.165 | 0.0071 | 0.17 | 0.16
6 | 3 | 0 | 0.2 | 0.0346 | 0.22 | 0.16
7 | 3 | 0 | 0.17 | 0.01 | 0.18 | 0.16
8 | 3 | 0 | 0.2633 | 0.0586 | 0.33 | 0.22
9 | 3 | 0 | 0.2167 | 0.0709 | 0.28 | 0.14
10 | 3 | 0 | 0.1433 | 0.0503 | 0.19 | 0.09
11 | 3 | 0 | 0.19 | 0.0721 | 0.27 | 0.13
12 | 3 | 0 | 0.1167 | 0.0115 | 0.13 | 0.11
Yearly totals/averages | 33 | 0 | 0.1727 | 0.0569 | 0.33 | 0.09
plant Logan | test period | 8/10/1999 | 8/12/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Logan | 1 | BITUMINOUS | 0.19 | 0.9687 | 13.3776 | 13.4654
Logan | 2 | BITUMINOUS | 0.18 | 0.9102 | 11.9 | 12.0194
Logan | 3 | BITUMINOUS | 0.17 | 0.8562 | 10.5802 | 10.7888
Averages |  |  | 0.18 | 0.9117 | 11.9526 | 12.0912
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Logan | 1 | SO2/SDA | no bypass | 0.9914 | 0.9909 | 0.1183 | 0.1225 | 86.7
Logan | 2 | SO2/SDA | no bypass | 0.9909 | 0.9899 | 0.119 | 0.1212 | 87
Logan | 3 | SO2/SDA | no bypass | 0.953 | 0.9447 | 0.5811 | 0.5968 | 87.2
Averages |  | SO2/SDA | no bypass | 0.9784 | 0.9752 | 0.2728 | 0.2801 | 87
SEI - Birchwood Power Facility |  | 1
Boiler/NOx type: | CONV/PC/NOX/SCR/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.07 | 0.0383 | 0.12 | 0.04
2 | 3 | 0 | 0.16 | 0.0819 | 0.23 | 0.07
3 | 3 | 0 | 0.13 | 0.0529 | 0.17 | 0.07
4 | 3 | 0 | 0.1533 | 0.0814 | 0.21 | 0.06
5 | 4 | 0 | 0.1075 | 0.0556 | 0.19 | 0.07
6 | 5 | 0 | 0.212 | 0.063 | 0.29 | 0.12
7 | 4 | 0 | 0.1825 | 0.0911 | 0.28 | 0.1
8 | 5 | 0 | 0.088 | 0.0657 | 0.17 | 0.01
9 | 4 | 0 | 0.1525 | 0.0727 | 0.25 | 0.08
10 | 4 | 0 | 0.1325 | 0.0492 | 0.17 | 0.06
11 | 3 | 0 | 0.13 | 0.0173 | 0.14 | 0.11
12 | 4 | 0 | 0.24 | 0.1074 | 0.35 | 0.1
Yearly totals/averages | 46 | 0 | 0.147 | 0.078 | 0.35 | 0.01
plant SEI | test period | 9/13/1999 | 9/15/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
SEI | 1 | BITUMINOUS | 0.11 | 1.0801 | 9.3923 | 10.0568
SEI | 2 | BITUMINOUS | 0.11 | 0.7669 | 6.7109 | 7.1079
SEI | 3 | BITUMINOUS | 0.11 | 0.9431 | 8.3397 | 8.9151
Averages |  |  | 0.11 | 0.93 | 8.1477 | 8.6933
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
SEI | 1 | SO2/SDA | no bypass | 0.9518 | 0.959 | 0.4187 | 0.4127 | 90
SEI | 2 | SO2/SDA | no bypass | 0.9817 | 0.9779 | 0.1604 | 0.1572 | 90
SEI | 3 | SO2/SDA | no bypass | 0.9826 | 0.9839 | 0.154 | 0.1438 | 90
Averages |  | SO2/SDA | no bypass | 0.972 | 0.9736 | 0.2444 | 0.2379 | 90
Big Bend |  | BB03
Boiler/NOx type: | CONV/TURBO/NOX/WET
Particulate control: | ESP- CS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 1 | 0.02 | 0.01 | 0.03 | 0.01
4 | 3 | 0 | 0.02 | 0 | 0.02 | 0.02
5 | 3 | 0 | 0.0367 | 0.0115 | 0.05 | 0.03
6 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
7 | 3 | 0 | 0.0367 | 0.0058 | 0.04 | 0.03
8 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
9 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
Yearly totals/averages | 21 | 1 | 0.0348 | 0.0117 | 0.05 | 0.01
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 16 | 0 | 0.0894 | 0.0291 | 0.13 | 0.05
2 | 17 | 0 | 0.0888 | 0.0212 | 0.12 | 0.05
3 | 17 | 0 | 0.0894 | 0.0277 | 0.13 | 0.04
4 | 18 | 0 | 0.0989 | 0.0285 | 0.15 | 0.05
5 | 18 | 0 | 0.0989 | 0.0256 | 0.13 | 0.05
6 | 19 | 0 | 0.0995 | 0.023 | 0.14 | 0.06
7 | 18 | 0 | 0.1144 | 0.0299 | 0.17 | 0.06
8 | 15 | 0 | 0.1127 | 0.0246 | 0.15 | 0.06
9 | 17 | 0 | 0.0941 | 0.0235 | 0.12 | 0.05
10 | 15 | 0 | 0.12 | 0.0334 | 0.19 | 0.06
11 | 18 | 0 | 0.1322 | 0.0349 | 0.18 | 0.05
12 | 16 | 0 | 0.105 | 0.0294 | 0.18 | 0.06
Yearly totals/averages | 204 | 0 | 0.1035 | 0.0301 | 0.19 | 0.04
Fuel number3 | PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
11 | 3 | 1 | 0.0333 | 0.0321 | 0.07 | 0.01
12 | 3 | 3 | 0.01 | 0 | 0.01 | 0.01
Yearly totals/averages | 6 | 4 | 0.0217 | 0.024 | 0.07 | 0.01
plant Big Bend | test period | 11/30/1999 | 12/2/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Big Bend | 1 | BITUMINOUS | 0.177
Big Bend | 2 | BITUMINOUS | 0.113
Big Bend | 3 | BITUMINOUS | 0.125
Averages |  |  | 0.1383
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Big Bend | 1 | SO2/WETSCRUB | no bypass | 0.8538 | 0.6703 | 2.0328 | 1.7181 | 52
Big Bend | 2 | SO2/WETSCRUB | no bypass | 0.8174 | 0.7421 | 1.6129 | 1.3401 | 52
Big Bend | 3 | SO2/WETSCRUB | no bypass | 0.7994 | 0.6432 | 1.9322 | 1.6374 | 52
Averages |  | SO2/WETSCRUB | no bypass | 0.8235 | 0.6852 | 1.8593 | 1.5652 | 52
AES Cayuga (formerly NYSEG Milliken) |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.41 | 0.2702 | 0.65 | 0.12
2 | 4 | 0 | 0.1925 | 0.1788 | 0.46 | 0.09
3 | 5 | 0 | 0.144 | 0.0195 | 0.17 | 0.12
4 | 2 | 0 | 0.135 | 0.0212 | 0.15 | 0.12
5 | 9 | 0 | 0.1589 | 0.0672 | 0.25 | 0.06
6 | 13 | 0 | 0.2215 | 0.117 | 0.47 | 0.07
7 | 11 | 0 | 0.2136 | 0.1595 | 0.51 | 0.01
8 | 15 | 0 | 0.322 | 0.2334 | 0.78 | 0.07
9 | 20 | 0 | 0.4135 | 0.2486 | 0.87 | 0.09
10 | 21 | 0 | 0.4262 | 0.2695 | 0.94 | 0.09
11 | 17 | 0 | 0.3424 | 0.1959 | 0.78 | 0.09
12 | 19 | 0 | 0.3516 | 0.1783 | 0.7 | 0.06
Yearly totals/averages | 140 | 0 | 0.3186 | 0.2178 | 0.94 | 0.01
plant Milliken 2 | test period | 8/7/1996 | 8/9/1996
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Milliken 2 | 1 | BITUMINOUS | 0.1051
Milliken 2 | 2 | BITUMINOUS | 0.1125
Milliken 2 | 3 | BITUMINOUS | 0.1021
Averages |  |  | 0.1065
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Milliken 2 | 1 | SO2/WETSCRUB | no bypass | 0.7125 | 0.6377 | 2.1994 | 2.0824 | 49.9
Milliken 2 | 2 | SO2/WETSCRUB | no bypass | 0.7554 | 0.7209 | 1.9948 | 1.9295 | 50.4
Milliken 2 | 3 | SO2/WETSCRUB | no bypass | 0.6935 | 0.6999 | 2.2893 | 2.1837 | 49.9
Averages |  | SO2/WETSCRUB | no bypass | 0.7205 | 0.6861 | 2.1612 | 2.0652 | 50.1
Charles R. Lowman |  | 2
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- HS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.12 | 0.07 | 0.19 | 0.05
2 | 5 | 0 | 0.118 | 0.037 | 0.17 | 0.08
3 | 4 | 0 | 0.0825 | 0.0206 | 0.11 | 0.06
4 | 6 | 0 | 0.0917 | 0.0133 | 0.11 | 0.07
5 | 2 | 0 | 0.1 | 0 | 0.1 | 0.1
6 | 3 | 0 | 0.0833 | 0.0115 | 0.09 | 0.07
7 | 3 | 0 | 0.0667 | 0.0058 | 0.07 | 0.06
8 | 3 | 0 | 0.0833 | 0.0058 | 0.09 | 0.08
9 | 3 | 0 | 0.0833 | 0.0058 | 0.09 | 0.08
10 | 2 | 0 | 0.075 | 0.0071 | 0.08 | 0.07
11 | 3 | 0 | 0.09 | 0.0173 | 0.1 | 0.07
12 | 4 | 0 | 0.0725 | 0.0171 | 0.09 | 0.05
Yearly totals/averages | 41 | 0 | 0.09 | 0.0275 | 0.19 | 0.05
plant Charles R. Lowman | test period | 1/25/2000 | 1/26/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Charles R. Lowman | 1 | BITUMINOUS | 0.084 | 0 | 0 | 0
Charles R. Lowman | 2 | BITUMINOUS | 0.077 | 0 | 0 | 0
Charles R. Lowman | 3 | BITUMINOUS | 0.08 | 0 | 0 | 0
Averages |  |  | 0.0803
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Charles R. Lowman | 1 | SO2/WETSCRUB | after bypass | 0.4709 | 0.1708 | 3.3284 | 3.2315 | 122
Charles R. Lowman | 2 | SO2/WETSCRUB | after bypass | 0.8397 | 0.8419 | 0.924 | 0.873 | 121
Charles R. Lowman | 3 | SO2/WETSCRUB | after bypass | 1.2085 | 1.1844 | -1.2493 | -1.1928 | 123
Averages |  | SO2/WETSCRUB | after bypass | 0.8397 | 0.7324 | 1.001 | 0.9706 | 122
R. D. Morrow Sr. Generating plant |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- HS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.1055 | 0.043 | 0.161 | 0.056
2 | 5 | 0 | 0.2786 | 0.1053 | 0.387 | 0.156
3 | 4 | 0 | 0.2408 | 0.0855 | 0.355 | 0.169
4 | 4 | 0 | 0.1438 | 0.0085 | 0.156 | 0.138
5 | 4 | 0 | 0.2773 | 0.1233 | 0.419 | 0.119
6 | 4 | 0 | 0.118 | 0.0232 | 0.14 | 0.089
7 | 4 | 0 | 0.174 | 0.0599 | 0.259 | 0.132
8 | 4 | 0 | 0.2313 | 0.0314 | 0.261 | 0.187
9 | 4 | 0 | 0.1495 | 0.0368 | 0.202 | 0.116
10 | 4 | 0 | 0.155 | 0.0191 | 0.18 | 0.14
11 | 4 | 0 | 0.275 | 0.0387 | 0.33 | 0.24
12 | 4 | 0 | 0.18 | 0.0141 | 0.2 | 0.17
Yearly totals/averages | 49 | 0 | 0.1958 | 0.0827 | 0.419 | 0.056
plant Morrow | test period | 10/27/1999 | 10/28/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Morrow | 1 | BITUMINOUS | 0.05 | 0 | 0 | 0
Morrow | 2 | BITUMINOUS | 0.05 | 0 | 0 | 0
Morrow | 3 | BITUMINOUS | 0.05 | 0 | 0 | 0
Averages |  |  | 0.05
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Morrow | 1 | SO2/WETSCRUB | after bypass | 0.5133 | 0.8253 | 1.8512 | 1.9177 | 83
Morrow | 2 | SO2/WETSCRUB | after bypass | 0.4445 | 0.7576 | 2.1396 | 2.163 | 88
Morrow | 3 | SO2/WETSCRUB | after bypass | 0.4124 | 0.6897 | 2.2818 | 2.2999 | 88
Averages |  | SO2/WETSCRUB | after bypass | 0.4567 | 0.7575 | 2.0909 | 2.1269 | 86.3
Navajo |  | 3
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- HS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.06 | 0.0141 | 0.07 | 0.04
2 | 5 | 0 | 0.052 | 0.0084 | 0.06 | 0.04
3 | 5 | 0 | 0.064 | 0.023 | 0.1 | 0.04
4 | 5 | 0 | 0.042 | 0.0045 | 0.05 | 0.04
5 | 5 | 0 | 0.038 | 0.0179 | 0.06 | 0.02
6 | 5 | 0 | 0.026 | 0.0055 | 0.03 | 0.02
7 | 5 | 0 | 0.028 | 0.0045 | 0.03 | 0.02
8 | 6 | 0 | 0.0283 | 0.0041 | 0.03 | 0.02
9 | 6 | 0 | 0.0283 | 0.0075 | 0.04 | 0.02
10 | 5 | 0 | 0.026 | 0.0055 | 0.03 | 0.02
11 | 5 | 0 | 0.026 | 0.0089 | 0.04 | 0.02
12 | 5 | 0 | 0.034 | 0.0055 | 0.04 | 0.03
Yearly totals/averages | 62 | 0 | 0.0374 | 0.0164 | 0.1 | 0.02
plant Navajo | test period | 10/25/1999 | 10/26/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Navajo | 1 | BITUMINOUS | 0.04 | 0 | 0 | 0
Navajo | 2 | BITUMINOUS | 0.024 | 0 | 0 | 0
Navajo | 3 | BITUMINOUS | 0.027 | 0 | 0 | 0
Averages |  |  | 0.0303
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Navajo | 1 | SO2/WETSCRUB | no bypass | 0.1484 | 0.42 | 2.6673 | 2.7026 | 49
Navajo | 2 | SO2/WETSCRUB | no bypass | -0.4611 | 0.1265 | 2.7611 | 2.7661 | 49
Navajo | 3 | SO2/WETSCRUB | no bypass | -0.3012 | 0.0818 | 2.7341 | 2.7392 | 49
Averages |  | SO2/WETSCRUB | no bypass | -0.2046 | 0.2095 | 2.7208 | 2.7359 | 49
Clover Power Station |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 35 | 0 | 0.1114 | 0.0685 | 0.26 | 0.01
2 | 29 | 0 | 0.0817 | 0.0252 | 0.13 | 0.02
3 | 29 | 0 | 0.0983 | 0.0594 | 0.28 | 0.01
4 | 27 | 0 | 0.1181 | 0.0369 | 0.17 | 0.04
5 | 36 | 0 | 0.1189 | 0.0393 | 0.22 | 0.05
6 | 15 | 0 | 0.1027 | 0.0337 | 0.16 | 0.05
7 | 20 | 0 | 0.0895 | 0.0206 | 0.14 | 0.06
8 | 15 | 0 | 0.0987 | 0.0236 | 0.16 | 0.07
9 | 19 | 0 | 0.0995 | 0.0241 | 0.15 | 0.05
10 | 22 | 0 | 0.0805 | 0.025 | 0.15 | 0.05
11 | 19 | 0 | 0.0758 | 0.0252 | 0.15 | 0.04
12 | 17 | 0 | 0.0694 | 0.0143 | 0.09 | 0.04
Yearly totals/averages | 283 | 0 | 0.0978 | 0.0425 | 0.28 | 0.01
plant Clover | test period | 11/30/1999 | 12/1/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Clover | 1 | BITUMINOUS | 0.115 | 0 | 0 | 0
Clover | 2 | BITUMINOUS | 0.1657 | 0 | 0 | 0
Clover | 3 | BITUMINOUS | 0.1975 | 0 | 0 | 0
Averages |  |  | 0.1594
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Clover | 1 | SO2/WETSCRUB | no bypass | 0.9385 | 0.6174 | 0.5403 | 0.5606 | 50.6
Clover | 2 | SO2/WETSCRUB | no bypass | 0.9722 | 0.7817 | 0.3382 | 0.3566 | 50
Clover | 3 | SO2/WETSCRUB | no bypass | 0.9905 | 0.8907 | 0.1377 | 0.1417 | 50
Averages |  | SO2/WETSCRUB | no bypass | 0.9671 | 0.7633 | 0.3387 | 0.3529 | 50.2
Intermountain |  | 2SGA
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 8 | 0 | 0.0493 | 0.0193 | 0.074 | 0.024
2 | 9 | 0 | 0.041 | 0.011 | 0.055 | 0.024
3 | 6 | 0 | 0.053 | 0.0078 | 0.067 | 0.045
4 | 7 | 0 | 0.0519 | 0.0227 | 0.081 | 0.018
5 | 8 | 0 | 0.0366 | 0.0196 | 0.073 | 0.009
6 | 8 | 0 | 0.0383 | 0.0163 | 0.072 | 0.023
7 | 3 | 0 | 0.0257 | 0.01 | 0.036 | 0.016
8 | 4 | 0 | 0.029 | 0.0078 | 0.038 | 0.019
9 | 4 | 0 | 0.0265 | 0.0111 | 0.037 | 0.015
10 | 3 | 0 | 0.0293 | 0.0192 | 0.05 | 0.012
11 | 4 | 0 | 0.0218 | 0.0066 | 0.03 | 0.016
12 | 3 | 0 | 0.0343 | 0.0117 | 0.047 | 0.024
Yearly totals/averages | 67 | 0 | 0.0391 | 0.0173 | 0.081 | 0.009
Fuel number2 | PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
11 | 3 | 0 | 0.0117 | 0.004 | 0.016 | 0.008
Yearly totals/averages | 3 | 0 | 0.0117 | 0.004 | 0.016 | 0.008
plant Intermountain | test period | 10/13/1999 | 10/14/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Intermountain | 1 | BITUMINOUS | 0.02 | 0 | 0 | 0
Intermountain | 2 | BITUMINOUS | 0.02 | 0 | 0 | 0
Intermountain | 3 | BITUMINOUS | 0.03 | 0 | 0 | 0
Averages |  |  | 0.0233
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Intermountain | 1 | SO2/WETSCRUB | no bypass | 0.899 | 0.8403 | 0.1556 | 0.1343 | 49
Intermountain | 2 | SO2/WETSCRUB | no bypass | 0.7562 | 0.6553 | 0.3745 | 0.3178 | 49
Intermountain | 3 | SO2/WETSCRUB | no bypass | 0.8599 | 0.7402 | 0.3245 | 0.2878 | 48
Averages |  | SO2/WETSCRUB | no bypass | 0.8384 | 0.7453 | 0.2849 | 0.2466 | 48.7
Montrose |  | 1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0533 | 0.0252 | 0.08 | 0.03
2 | 3 | 0 | 0.0367 | 0.0058 | 0.04 | 0.03
3 | 3 | 0 | 0.0333 | 0.0058 | 0.04 | 0.03
4 | 3 | 0 | 0.0367 | 0.0153 | 0.05 | 0.02
5 | 3 | 0 | 0.04 | 0 | 0.04 | 0.04
6 | 3 | 0 | 0.0433 | 0.0208 | 0.06 | 0.02
7 | 3 | 0 | 0.04 | 0.01 | 0.05 | 0.03
8 | 3 | 0 | 0.0633 | 0.0058 | 0.07 | 0.06
9 | 3 | 0 | 0.0533 | 0.0252 | 0.08 | 0.03
10 | 3 | 0 | 0.0467 | 0.0153 | 0.06 | 0.03
11 | 3 | 0 | 0.03 | 0 | 0.03 | 0.03
12 | 3 | 0 | 0.03 | 0 | 0.03 | 0.03
Yearly totals/averages | 36 | 0 | 0.0422 | 0.0153 | 0.08 | 0.02
plant Montrose | test period | 1/18/2000 | 1/19/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Montrose | 1 | SUBBITUMINOUS | 0.089 | 0.2168 | 1.8479 | 6.9835
Montrose | 2 | SUBBITUMINOUS | 0.107 | 0.1597 | 1.6593 | 5.9624
Montrose | 3 | SUBBITUMINOUS | 0.103 | 0.1906 | 1.8695 | 6.5345
Averages |  |  | 0.0997 | 0.189 | 1.7922 | 6.4935
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Montrose | 1 | PM/ESP- CS | no bypass | 0.3238 | 0.1759 | 5.7649 | 5.7593 | 166.1
Montrose | 2 | PM/ESP- CS | no bypass | 0.3766 | -0.0234 | 6.4762 | 6.1072 | 167.8
Montrose | 3 | PM/ESP- CS | no bypass | 0.3712 | 0.1275 | 6.1687 | 5.7054 | 167.8
Averages |  | PM/ESP- CS | no bypass | 0.3572 | 0.0933 | 6.1366 | 5.8573 | 167.2
George Neal South |  | 4
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0867 | 0.0153 | 0.1 | 0.07
2 | 2 | 0 | 0.045 | 0.0354 | 0.07 | 0.02
3 | 4 | 0 | 0.09 | 0.0141 | 0.11 | 0.08
4 | 3 | 0 | 0.0767 | 0.0289 | 0.11 | 0.06
5 | 3 | 0 | 0.0867 | 0.0208 | 0.11 | 0.07
6 | 3 | 0 | 0.0733 | 0.0115 | 0.08 | 0.06
7 | 3 | 0 | 0.0867 | 0.0115 | 0.1 | 0.08
8 | 4 | 0 | 0.075 | 0.037 | 0.12 | 0.03
9 | 4 | 0 | 0.0825 | 0.005 | 0.09 | 0.08
10 | 3 | 0 | 0.0867 | 0.0153 | 0.1 | 0.07
11 | 3 | 0 | 0.0733 | 0.0115 | 0.08 | 0.06
12 | 3 | 0 | 0.0833 | 0.0058 | 0.09 | 0.08
Yearly totals/averages | 38 | 0 | 0.08 | 0.0196 | 0.12 | 0.02
plant Neal | test period | 9/14/1999 | 9/14/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Neal | 1 | SUBBITUMINOUS | 0.09 | 0.9044 | 6.7814 | 8.0507
Neal | 2 | SUBBITUMINOUS | 0.08 | 1.1544 | 7.6867 | 9.09
Neal | 3 | SUBBITUMINOUS | 0.1 | 0.4972 | 4.1775 | 5.2592
Averages |  |  | 0.09 | 0.852 | 6.2152 | 7.4666
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Neal | 1 | PM/ESP- CS | no bypass | 0.2934 | 0.1462 | 5.2981 | 6.8781 | 138
Neal | 2 | PM/ESP- CS | no bypass | 0.0193 | 0.0891 | 6.5304 | 8.2831 | 142
Neal | 3 | PM/ESP- CS | no bypass | 0.3456 | -0.5232 | 5.4987 | 8.0193 | 144
Averages |  | PM/ESP- CS | no bypass | 0.2194 | -0.096 | 5.7757 | 7.7269 | 141.3
Newton |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0717 | 0.0276 | 0.103 | 0.051
2 | 3 | 0 | 0.0423 | 0.0084 | 0.052 | 0.037
Yearly totals/averages | 6 | 0 | 0.057 | 0.0243 | 0.103 | 0.037
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0697 | 0.0006 | 0.07 | 0.069
2 | 3 | 0 | 0.071 | 0.0106 | 0.083 | 0.063
3 | 5 | 4 | 0.0204 | 0.0177 | 0.052 | 0.0125
4 | 3 | 0 | 0.0737 | 0.0072 | 0.082 | 0.069
5 | 10 | 1 | 0.0569 | 0.019 | 0.079 | 0.0125
6 | 7 | 2 | 0.0589 | 0.041 | 0.129 | 0.0125
7 | 9 | 1 | 0.0667 | 0.0277 | 0.105 | 0.0125
8 | 6 | 1 | 0.0334 | 0.0147 | 0.055 | 0.0125
9 | 6 | 3 | 0.0371 | 0.0386 | 0.109 | 0.0125
10 | 6 | 0 | 0.0685 | 0.0098 | 0.084 | 0.057
11 | 6 | 0 | 0.0572 | 0.0115 | 0.067 | 0.035
12 | 4 | 0 | 0.0523 | 0.0093 | 0.062 | 0.04
Yearly totals/averages | 68 | 12 | 0.0546 | 0.0264 | 0.129 | 0.0125
plant Newton | test period | 7/31/1999 | 8/2/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Newton | 1 | SUBBITUMINOUS | 0.074 | 1.2004 | 8.057 | 7.4068
Newton | 2 | SUBBITUMINOUS | 0.068 | 1.306 | 7.9974 | 7.5469
Newton | 3 | SUBBITUMINOUS | 0.07 | 1.3966 | 8.8722 | 7.8895
Averages |  |  | 0.0707 | 1.301 | 8.3088 | 7.6144
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Newton | 1 | PM/ESP- CS | no bypass | -0.2025 | -0.001 | 8.0709 | 7.4196 | 169
Newton | 2 | PM/ESP- CS | no bypass | -0.0935 | 0.1633 | 6.6961 | 6.3189 | 163
Newton | 3 | PM/ESP- CS | no bypass | -0.2789 | 0.0846 | 8.1245 | 7.2247 | 170
Averages |  | PM/ESP- CS | no bypass | -0.1916 | 0.0823 | 7.6305 | 6.9877 | 167.3
Cholla |  | 3
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- HS
SO2 control: | NONE
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 6 | 0 | 0.0433 | 0.0103 | 0.06 | 0.03
2 | 5 | 0 | 0.08 | 0.0339 | 0.13 | 0.04
3 | 6 | 0 | 0.0517 | 0.0117 | 0.07 | 0.04
4 | 5 | 0 | 0.084 | 0.0577 | 0.16 | 0.03
5 | 9 | 0 | 0.07 | 0.0456 | 0.17 | 0.03
6 | 4 | 0 | 0.04 | 0.0082 | 0.05 | 0.03
7 | 6 | 0 | 0.06 | 0.04 | 0.14 | 0.04
8 | 9 | 0 | 0.0756 | 0.0384 | 0.14 | 0.04
9 | 8 | 0 | 0.0488 | 0.0136 | 0.08 | 0.04
10 | 6 | 0 | 0.0567 | 0.0163 | 0.08 | 0.04
11 | 7 | 0 | 0.0486 | 0.0146 | 0.08 | 0.04
12 | 8 | 0 | 0.0388 | 0.0064 | 0.05 | 0.03
Yearly totals/averages | 79 | 0 | 0.0582 | 0.0314 | 0.17 | 0.03
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
3 | 2 | 0 | 0.07 | 0.0424 | 0.1 | 0.04
4 | 1 | 0 | 0.04 | 0 | 0.04 | 0.04
5 | 1 | 0 | 0.03 | 0 | 0.03 | 0.03
6 | 1 | 0 | 0.02 | 0 | 0.02 | 0.02
7 | 2 | 0 | 0.035 | 0.0071 | 0.04 | 0.03
Yearly totals/averages | 7 | 0 | 0.0429 | 0.0263 | 0.1 | 0.02
plant Cholla 3 | test period | 11/2/1999 | 11/5/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Cholla 3 | 1 | SUBBITUMINOUS | 0.04 | 0.3785 | 1.2763 | 1.4115
Cholla 3 | 2 | SUBBITUMINOUS | 0.04 | 0.1431 | 0.4703 | 0.5589
Cholla 3 | 3 | SUBBITUMINOUS | 0.03 | 0.257 | 0.6354 | 0.7464
Averages |  |  | 0.0367 | 0.2595 | 0.794 | 0.9056
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Cholla 3 | 1 | PM/ESP- HS | no bypass | 0.5369 | -0.2116 | 1.5616 | 1.7118 | 159
Cholla 3 | 2 | PM/ESP- HS | no bypass | 0.8069 | -0.2821 | 0.6345 | 0.717 | 155
Cholla 3 | 3 | PM/ESP- HS | no bypass | 0.5823 | -0.5943 | 1.0328 | 1.1909 | 159
Averages |  | PM/ESP- HS | no bypass | 0.642 | -0.3627 | 1.0763 | 1.2066 | 157.7
Columbia |  | 1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- HS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 7 | 0 | 0.06 | 0.0191 | 0.09 | 0.03
2 | 4 | 0 | 0.0675 | 0.0096 | 0.08 | 0.06
3 | 4 | 0 | 0.0625 | 0.005 | 0.07 | 0.06
4 | 3 | 0 | 0.0533 | 0.0115 | 0.06 | 0.04
5 | 5 | 0 | 0.062 | 0.013 | 0.08 | 0.05
6 | 5 | 0 | 0.054 | 0.0089 | 0.06 | 0.04
7 | 4 | 0 | 0.075 | 0.0129 | 0.09 | 0.06
8 | 5 | 0 | 0.03 | 0.01 | 0.04 | 0.02
9 | 4 | 0 | 0.065 | 0.0129 | 0.08 | 0.05
10 | 7 | 0 | 0.0529 | 0.0138 | 0.07 | 0.03
11 | 9 | 0 | 0.0589 | 0.0127 | 0.07 | 0.03
12 | 6 | 0 | 0.055 | 0.0055 | 0.06 | 0.05
Yearly totals/averages | 63 | 0 | 0.0575 | 0.015 | 0.09 | 0.02
plant Columbia | test period | 10/19/1999 | 10/19/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Columbia | 1 | SUBBITUMINOUS | 0.1 | 1.5464 | 12.6119 | 10.9239
Columbia | 2 | SUBBITUMINOUS | 0.1 | 1.8699 | 15.4283 | 13.8184
Columbia | 3 | SUBBITUMINOUS | 0.1 | 1.4634 | 12.0127 | 10.8704
Averages |  |  | 0.1 | 1.6265 | 13.351 | 11.8709
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Columbia | 1 | PM/ESP- HS | no bypass | -0.28 | 0.0508 | 10.4397 | 10.3776 | 149
Columbia | 2 | PM/ESP- HS | no bypass | -0.2134 | 0.2742 | 10.0118 | 10.0361 | 156
Columbia | 3 | PM/ESP- HS | no bypass | -0.263 | 0.0333 | 10.3679 | 10.5155 | 157
Averages |  | PM/ESP- HS | no bypass | -0.2522 | 0.1195 | 10.2732 | 10.3097 | 154
Platte |  | 1
Boiler/NOx type: | CONV/PC/NOX/WET
Particulate control: | ESP- HS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.045 | 0.0036 | 0.049 | 0.042
2 | 2 | 0 | 0.077 | 0.0014 | 0.078 | 0.076
3 | 3 | 0 | 0.0733 | 0.0132 | 0.085 | 0.059
4 | 2 | 0 | 0.0375 | 0.0106 | 0.045 | 0.03
5 | 1 | 0 | 0.041 | 0 | 0.041 | 0.041
6 | 3 | 0 | 0.0477 | 0.0194 | 0.07 | 0.035
7 | 3 | 0 | 0.0817 | 0.0181 | 0.095 | 0.061
8 | 3 | 0 | 0.0653 | 0.0165 | 0.079 | 0.047
9 | 3 | 0 | 0.0323 | 0.0159 | 0.042 | 0.014
10 | 2 | 0 | 0.0765 | 0.0092 | 0.083 | 0.07
11 | 2 | 0 | 0.0795 | 0.0078 | 0.085 | 0.074
12 | 2 | 0 | 0.073 | 0 | 0.073 | 0.073
Yearly totals/averages | 29 | 0 | 0.0608 | 0.0208 | 0.095 | 0.014
plant Platte | test period | 8/18/1999 | 8/19/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Platte | 1 | SUBBITUMINOUS | 0.11 | 1.2606 | 11.3382 | 10.0437
Platte | 2 | SUBBITUMINOUS | 0.09 | 1.3744 | 10.1298 | 9.5174
Platte | 3 | SUBBITUMINOUS | 0.07 | 2.6519 | 15.1119 | 11.5047
Averages |  |  | 0.09 | 1.7623 | 12.1933 | 10.3553
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Platte | 1 | PM/ESP- HS | no bypass | 0.1091 | 0.2682 | 8.0134 | 7.3539 | 153.4
Platte | 2 | PM/ESP- HS | no bypass | -0.7317 | -0.3316 | 12.7635 | 12.6805 | 158
Platte | 3 | PM/ESP- HS | no bypass | -1.4032 | -0.0247 | 13.6947 | 11.802 | 152.9
Averages |  | PM/ESP- HS | no bypass | -0.6753 | -0.0293 | 11.4905 | 10.6121 | 154.8
Presque Isle |  | 9
Boiler/NOx type: | CONV/PC/NOX/WET
Particulate control: | ESP- HS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.043 | 0.0087 | 0.048 | 0.033
2 | 4 | 0 | 0.0523 | 0.016 | 0.071 | 0.032
3 | 5 | 0 | 0.0408 | 0.0097 | 0.051 | 0.029
4 | 3 | 0 | 0.0273 | 0.0021 | 0.029 | 0.025
5 | 5 | 0 | 0.0282 | 0.0246 | 0.072 | 0.014
6 | 4 | 0 | 0.0127 | 0.0041 | 0.016 | 0.0076
7 | 4 | 0 | 0.0284 | 0.0298 | 0.072 | 0.0091
8 | 4 | 0 | 0.0225 | 0.0066 | 0.029 | 0.015
9 | 5 | 0 | 0.0442 | 0.0427 | 0.12 | 0.019
10 | 4 | 0 | 0.017 | 0.0062 | 0.022 | 0.008
11 | 5 | 0 | 0.0208 | 0.0055 | 0.027 | 0.015
12 | 4 | 0 | 0.0215 | 0.0048 | 0.026 | 0.015
Yearly totals/averages | 50 | 0 | 0.03 | 0.0208 | 0.12 | 0.0076
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.056 | 0.0074 | 0.067 | 0.051
2 | 4 | 0 | 0.0455 | 0.0055 | 0.051 | 0.039
3 | 5 | 0 | 0.0536 | 0.0084 | 0.063 | 0.044
4 | 4 | 0 | 0.0588 | 0.005 | 0.063 | 0.052
5 | 5 | 0 | 0.036 | 0.007 | 0.043 | 0.027
6 | 4 | 0 | 0.0423 | 0.0083 | 0.049 | 0.031
7 | 4 | 0 | 0.031 | 0.0088 | 0.039 | 0.022
8 | 4 | 0 | 0.0608 | 0.0266 | 0.1 | 0.041
9 | 5 | 0 | 0.0576 | 0.0108 | 0.07 | 0.046
10 | 4 | 0 | 0.0418 | 0.0069 | 0.049 | 0.033
11 | 5 | 0 | 0.0698 | 0.0159 | 0.088 | 0.048
12 | 4 | 0 | 0.0538 | 0.0096 | 0.063 | 0.042
Yearly totals/averages | 52 | 0 | 0.0508 | 0.015 | 0.1 | 0.022
plant Presque Isle 9 | test period | 7/12/1999 | 7/20/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Presque Isle 9 | 1 | SUBBITUMINOUS | 0.0687 | 0.8886 | 5.0754 | 4.938
Presque Isle 9 | 2 | SUBBITUMINOUS | 0.0654 | 0.9942 | 5.3927 | 5.0516
Presque Isle 9 | 3 | SUBBITUMINOUS | 0.0704 | 0.8313 | 4.8592 | 4.6937
Averages |  |  | 0.0682 | 0.9047 | 5.1091 | 4.8944
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Presque Isle 9 | 1 | PM/ESP- HS | no bypass | 0.1378 | 0.001 | 4.925 | 4.936 | 195
Presque Isle 9 | 2 | PM/ESP- HS | no bypass | 0.0228 | -0.0523 | 5.3005 | 5.3188 | 195.6
Presque Isle 9 | 3 | PM/ESP- HS | no bypass | 0.1372 | -0.0576 | 5.0432 | 4.9665 | 196.7
Averages |  | PM/ESP- HS | no bypass | 0.0993 | -0.0363 | 5.0896 | 5.0738 | 195.7
Clay Boswell |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 6 | 0 | 0.0783 | 0.0438 | 0.154 | 0.035
2 | 7 | 0 | 0.0614 | 0.0246 | 0.094 | 0.013
3 | 6 | 0 | 0.0787 | 0.0126 | 0.101 | 0.068
4 | 3 | 0 | 0.0693 | 0.0199 | 0.085 | 0.047
5 | 3 | 0 | 0.0707 | 0.0153 | 0.088 | 0.059
6 | 3 | 0 | 0.0457 | 0.0361 | 0.085 | 0.014
7 | 3 | 0 | 0.0803 | 0.0366 | 0.12 | 0.048
8 | 4 | 0 | 0.0585 | 0.0312 | 0.089 | 0.023
9 | 4 | 0 | 0.072 | 0.0329 | 0.109 | 0.037
10 | 4 | 0 | 0.0898 | 0.0145 | 0.108 | 0.075
11 | 3 | 0 | 0.0823 | 0.0634 | 0.141 | 0.015
12 | 3 | 0 | 0.045 | 0.0161 | 0.062 | 0.03
Yearly totals/averages | 49 | 0 | 0.0701 | 0.0302 | 0.154 | 0.013
plant Boswell 2 | test period | 3/20/2000 | 3/28/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Boswell 2 | 1 | SUBBITUMINOUS | 0.078 | 0.7367 | 4.7262 | 4.4202
Boswell 2 | 2 | SUBBITUMINOUS | 0.043 | 1.0813 | 3.8467 | 3.3814
Boswell 2 | 3 | SUBBITUMINOUS | 0.049 | 0.8582 | 3.4752 | 3.2052
Averages |  |  | 0.0567 | 0.892 | 4.016 | 3.6689
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Boswell 2 | 1 | PM/BAGHOUSE | no bypass | 0.8223 | 0.7606 | 1.14 | 1.0585 | 169
Boswell 2 | 2 | PM/BAGHOUSE | no bypass | 0.8814 | 0.8745 | 0.4219 | 0.4245 | 166
Boswell 2 | 3 | PM/BAGHOUSE | no bypass | 0.8773 | 0.8419 | 0.4969 | 0.507 | 168
Averages |  | PM/BAGHOUSE | no bypass | 0.8603 | 0.8257 | 0.6863 | 0.6633 | 167.7
Comanche |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.0548 | 0.015 | 0.078 | 0.039
2 | 3 | 0 | 0.065 | 0.0104 | 0.072 | 0.053
3 | 4 | 0 | 0.0615 | 0.0093 | 0.075 | 0.055
4 | 4 | 0 | 0.0758 | 0.008 | 0.087 | 0.068
5 | 5 | 0 | 0.0812 | 0.0083 | 0.089 | 0.068
6 | 3 | 0 | 0.0627 | 0.0175 | 0.08 | 0.045
7 | 3 | 0 | 0.0993 | 0.0315 | 0.119 | 0.063
8 | 2 | 0 | 0.064 | 0.0014 | 0.065 | 0.063
9 | 3 | 0 | 0.0927 | 0.0065 | 0.099 | 0.086
10 | 3 | 0 | 0.08 | 0.0036 | 0.083 | 0.076
11 | 3 | 0 | 0.1023 | 0.0521 | 0.156 | 0.052
12 | 3 | 0 | 0.0943 | 0.0015 | 0.096 | 0.093
Yearly totals/averages | 41 | 0 | 0.0767 | 0.0223 | 0.156 | 0.039
plant Comanche | test period | 10/12/1998 | 10/16/1998
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Comanche | 1 | SUBBITUMINOUS | 0.094 | 0.9213 | 7.2864 | 7.6699
Comanche | 2 | SUBBITUMINOUS | 0.0963 | 0.7266 | 5.8868 | 6.4995
Comanche | 3 | SUBBITUMINOUS | 0.0862 | 0.9148 | 6.633 | 6.8608
Averages |  |  | 0.0922 | 0.8542 | 6.6021 | 7.0101
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Comanche | 1 | PM/BAGHOUSE | no bypass | 0.69 | 0.686 | 2.4513 | 2.4072 | 149.4
Comanche | 2 | PM/BAGHOUSE | no bypass | 0.6079 | 0.5263 | 3.1766 | 3.0761 | 157.8
Comanche | 3 | PM/BAGHOUSE | no bypass | 0.6752 | 0.6652 | 2.3554 | 2.296 | 147.2
Averages |  | PM/BAGHOUSE | no bypass | 0.6577 | 0.6259 | 2.6611 | 2.5931 | 151.5
Clay Boswell |  | 3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | PARTSCRUB
SO2 control: | WETSCRUB/COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 6 | 0 | 0.0783 | 0.0438 | 0.154 | 0.035
2 | 7 | 0 | 0.0614 | 0.0246 | 0.094 | 0.013
3 | 6 | 0 | 0.0787 | 0.0126 | 0.101 | 0.068
4 | 3 | 0 | 0.0693 | 0.0199 | 0.085 | 0.047
5 | 3 | 0 | 0.0707 | 0.0153 | 0.088 | 0.059
6 | 3 | 0 | 0.0457 | 0.0361 | 0.085 | 0.014
7 | 3 | 0 | 0.0803 | 0.0366 | 0.12 | 0.048
8 | 4 | 0 | 0.0585 | 0.0312 | 0.089 | 0.023
9 | 4 | 0 | 0.072 | 0.0329 | 0.109 | 0.037
10 | 4 | 0 | 0.0898 | 0.0145 | 0.108 | 0.075
11 | 3 | 0 | 0.0823 | 0.0634 | 0.141 | 0.015
12 | 3 | 0 | 0.045 | 0.0161 | 0.062 | 0.03
Yearly totals/averages | 49 | 0 | 0.0701 | 0.0302 | 0.154 | 0.013
plant Boswell 3 | test period | 3/20/2000 | 3/28/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Boswell 3 | 1 | SUBBITUMINOUS | 0.054 | 1.2657 | 5.6615 | 4.539
Boswell 3 | 2 | SUBBITUMINOUS | 0.072 | 0.9915 | 5.9235 | 4.539
Boswell 3 | 3 | SUBBITUMINOUS | 0.063 | 1.0174 | 5.354 | 4.2267
Averages |  |  | 0.063 | 1.0915 | 5.6463 | 4.4349
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Boswell 3 | 1 | PM/PARTSCRUB | no bypass | -0.1754 | 0.0716 | 5.2576 | 4.2151 | 51
Boswell 3 | 2 | PM/PARTSCRUB | no bypass | 0.145 | 0.1381 | 5.1078 | 3.914 | 51
Boswell 3 | 3 | PM/PARTSCRUB | no bypass | 0.0354 | 0.0525 | 5.0757 | 4.007 | 51
Averages |  | PM/PARTSCRUB | no bypass | 0.0017 | 0.0874 | 5.147 | 4.0454 | 51
Clay Boswell |  | 4
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | PARTSCRUB
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 6 | 0 | 0.0783 | 0.0438 | 0.154 | 0.035
2 | 7 | 0 | 0.0614 | 0.0246 | 0.094 | 0.013
3 | 6 | 0 | 0.0787 | 0.0126 | 0.101 | 0.068
4 | 3 | 0 | 0.0693 | 0.0199 | 0.085 | 0.047
5 | 3 | 0 | 0.0707 | 0.0153 | 0.088 | 0.059
6 | 3 | 0 | 0.0457 | 0.0361 | 0.085 | 0.014
7 | 3 | 0 | 0.0803 | 0.0366 | 0.12 | 0.048
8 | 4 | 0 | 0.0585 | 0.0312 | 0.089 | 0.023
9 | 4 | 0 | 0.072 | 0.0329 | 0.109 | 0.037
10 | 4 | 0 | 0.0898 | 0.0145 | 0.108 | 0.075
11 | 3 | 0 | 0.0823 | 0.0634 | 0.141 | 0.015
12 | 3 | 0 | 0.045 | 0.0161 | 0.062 | 0.03
Yearly totals/averages | 49 | 0 | 0.0701 | 0.0302 | 0.154 | 0.013
plant Boswell 4 | test period | 3/20/2000 | 3/28/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Boswell 4 | 1 | SUBBITUMINOUS | 0.065 | 0.7858 | 4.2301 | 3.9354
Boswell 4 | 2 | SUBBITUMINOUS | 0.063 | 0.8224 | 4.2478 | 3.966
Boswell 4 | 3 | SUBBITUMINOUS | 0.07 | 0.5616 | 3.3066 | 3.1973
Averages |  |  | 0.066 | 0.7233 | 3.9282 | 3.6996
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Boswell 4 | 1 | PM/PARTSCRUB | no bypass | 0.1465 | -0.0308 | 4.5944 | 4.056 | 67
Boswell 4 | 2 | PM/PARTSCRUB | no bypass | 0.0171 | -0.1825 | 5.0771 | 4.6907 | 68
Boswell 4 | 3 | PM/PARTSCRUB | no bypass | 0.1784 | -0.444 | 4.8377 | 4.6184 | 69
Averages |  | PM/PARTSCRUB | no bypass | 0.114 | -0.2191 | 4.8364 | 4.455 | 68
Cholla |  | 2
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | MECH/PARTSCRUB
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 6 | 0 | 0.0433 | 0.0103 | 0.06 | 0.03
2 | 5 | 0 | 0.08 | 0.0339 | 0.13 | 0.04
3 | 6 | 0 | 0.0517 | 0.0117 | 0.07 | 0.04
4 | 5 | 0 | 0.084 | 0.0577 | 0.16 | 0.03
5 | 9 | 0 | 0.07 | 0.0456 | 0.17 | 0.03
6 | 4 | 0 | 0.04 | 0.0082 | 0.05 | 0.03
7 | 6 | 0 | 0.06 | 0.04 | 0.14 | 0.04
8 | 9 | 0 | 0.0756 | 0.0384 | 0.14 | 0.04
9 | 8 | 0 | 0.0488 | 0.0136 | 0.08 | 0.04
10 | 6 | 0 | 0.0567 | 0.0163 | 0.08 | 0.04
11 | 7 | 0 | 0.0486 | 0.0146 | 0.08 | 0.04
12 | 8 | 0 | 0.0388 | 0.0064 | 0.05 | 0.03
Yearly totals/averages | 79 | 0 | 0.0582 | 0.0314 | 0.17 | 0.03
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
3 | 2 | 0 | 0.07 | 0.0424 | 0.1 | 0.04
4 | 1 | 0 | 0.04 | 0 | 0.04 | 0.04
5 | 1 | 0 | 0.03 | 0 | 0.03 | 0.03
6 | 1 | 0 | 0.02 | 0 | 0.02 | 0.02
7 | 2 | 0 | 0.035 | 0.0071 | 0.04 | 0.03
Yearly totals/averages | 7 | 0 | 0.0429 | 0.0263 | 0.1 | 0.02
plant Cholla 2 | test period | 11/2/1999 | 11/5/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Cholla 2 | 1 | SUBBITUMINOUS | 0.045 | 0.811 | 3.252 | 3.8436
Cholla 2 | 2 | SUBBITUMINOUS | 0.04 | 0.5669 | 2.0701 | 2.5902
Cholla 2 | 3 | SUBBITUMINOUS | 0.035 | 0.8371 | 2.6316 | 3.0557
Averages |  |  | 0.04 | 0.7384 | 2.6512 | 3.1632
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Cholla 2 | 1 | PM/MECH/ PARTSCRUB | no bypass | 0.3849 | 0.2268 | 2.4667 | 2.9731 | 86.7
Cholla 2 | 2 | PM/MECH/ PARTSCRUB | no bypass | 0.2022 | -0.3339 | 2.9129 | 3.4578 | 86.7
Cholla 2 | 3 | PM/MECH/ PARTSCRUB | no bypass | 0.1436 | -0.0233 | 2.6922 | 3.1284 | 86.6
Averages |  | PM/MECH/ PARTSCRUB | no bypass | 0.2436 | -0.0435 | 2.6906 | 3.1864 | 86.7
Colstrip |  | 3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | PARTSCRUB
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 6 | 0 | 0.0477 | 0.0294 | 0.101 | 0.015
2 | 6 | 0 | 0.0468 | 0.0238 | 0.094 | 0.029
3 | 6 | 0 | 0.0535 | 0.0315 | 0.108 | 0.026
4 | 3 | 0 | 0.051 | 0.0205 | 0.071 | 0.03
5 | 4 | 0 | 0.0473 | 0.0076 | 0.055 | 0.037
6 | 4 | 0 | 0.0665 | 0.0196 | 0.09 | 0.044
7 | 3 | 0 | 0.0603 | 0.0223 | 0.077 | 0.035
8 | 4 | 0 | 0.051 | 0.0042 | 0.056 | 0.046
9 | 2 | 0 | 0.067 | 0 | 0.067 | 0.067
10 | 3 | 0 | 0.0637 | 0.0099 | 0.075 | 0.057
11 | 4 | 0 | 0.0693 | 0.025 | 0.1 | 0.039
12 | 3 | 0 | 0.0607 | 0.0067 | 0.068 | 0.055
Yearly totals/averages | 48 | 0 | 0.0555 | 0.0209 | 0.108 | 0.015
plant Colstrip | test period | 9/28/1999 | 9/30/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Colstrip | 1 | SUBBITUMINOUS | 0.063 | 0.6749 | 3.9446 | 3.694
Colstrip | 2 | SUBBITUMINOUS | 0.066 | 1.3383 | 8.3582 | 7.6637
Colstrip | 3 | SUBBITUMINOUS | 0.067 | 1.2458 | 7.8097 | 7.0891
Averages |  |  | 0.0653 | 1.0864 | 6.7042 | 6.1489
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Colstrip | 1 | PM/PARTSCRUB | no bypass | -0.0718 | -0.8828 | 6.2645 | 6.9598 | 89
Colstrip | 2 | PM/PARTSCRUB | no bypass | -0.2111 | -0.0884 | 7.5635 | 8.3467 | 89
Colstrip | 3 | PM/PARTSCRUB | no bypass | 0.7243 | 0.736 | 1.728 | 1.8725 | 89
Averages |  | PM/PARTSCRUB | no bypass | 0.1472 | -0.0784 | 5.1853 | 5.7264 | 89
Lawrence |  | 4
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | PARTSCRUB
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.06 | 0.0082 | 0.07 | 0.05
2 | 5 | 0 | 0.072 | 0.0148 | 0.09 | 0.05
3 | 4 | 0 | 0.0775 | 0.005 | 0.08 | 0.07
4 | 5 | 0 | 0.076 | 0.027 | 0.12 | 0.05
5 | 2 | 0 | 0.045 | 0.0212 | 0.06 | 0.03
6 | 1 | 0 | 0.1 | 0 | 0.1 | 0.1
7 | 3 | 0 | 0.0667 | 0.0058 | 0.07 | 0.06
8 | 5 | 0 | 0.068 | 0.013 | 0.08 | 0.05
9 | 3 | 0 | 0.05 | 0 | 0.05 | 0.05
10 | 3 | 0 | 0.0633 | 0.0115 | 0.07 | 0.05
11 | 3 | 0 | 0.0667 | 0.0115 | 0.08 | 0.06
12 | 3 | 0 | 0.08 | 0.0173 | 0.1 | 0.07
Yearly totals/averages | 41 | 0 | 0.0683 | 0.0166 | 0.12 | 0.03
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
5 | 3 | 0 | 0.11 | 0.0557 | 0.17 | 0.06
6 | 4 | 0 | 0.0775 | 0.0275 | 0.11 | 0.05
7 | 4 | 0 | 0.08 | 0.0082 | 0.09 | 0.07
8 | 3 | 0 | 0.0733 | 0.0153 | 0.09 | 0.06
11 | 3 | 0 | 0.0733 | 0.0321 | 0.11 | 0.05
12 | 3 | 0 | 0.0633 | 0.0153 | 0.08 | 0.05
Yearly totals/averages | 20 | 0 | 0.0795 | 0.0286 | 0.17 | 0.05
plant Lawrence | test period | 10/25/1999 | 10/26/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Lawrence | 1 | SUBBITUMINOUS | 0.052 | 1.0993 | 4.6551 | 4.9289
Lawrence | 2 | SUBBITUMINOUS | 0.044 | 1.0199 | 3.6604 | 4.0065
Lawrence | 3 | SUBBITUMINOUS | 0.047 | 0.9842 | 3.7485 | 4.2607
Averages |  |  | 0.0477 | 1.0345 | 4.0213 | 4.3987
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Lawrence | 1 | PM/PARTSCRUB | no bypass | -0.1405 | -0.0159 | 4.8295 | 5.0089 | 68
Lawrence | 2 | PM/PARTSCRUB | no bypass | -0.3364 | -0.3383 | 4.7963 | 5.3657 | 66
Lawrence | 3 | PM/PARTSCRUB | no bypass | -0.218 | -0.1683 | 4.6392 | 4.9798 | 68
Averages |  | PM/PARTSCRUB | no bypass | -0.2317 | -0.1742 | 4.755 | 5.1181 | 67.3
GRDA |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | SDA
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.0625 | 0.0435 | 0.12 | 0.02
2 | 5 | 0 | 0.064 | 0.0207 | 0.09 | 0.04
3 | 5 | 0 | 0.068 | 0.0084 | 0.08 | 0.06
4 | 4 | 0 | 0.0775 | 0.0299 | 0.12 | 0.05
5 | 5 | 0 | 0.06 | 0.0255 | 0.09 | 0.03
6 | 4 | 0 | 0.0625 | 0.0126 | 0.08 | 0.05
7 | 4 | 1 | 0.02 | 0.0082 | 0.03 | 0.01
8 | 5 | 0 | 0.054 | 0.0114 | 0.07 | 0.04
9 | 4 | 0 | 0.06 | 0.0245 | 0.09 | 0.04
10 | 5 | 0 | 0.056 | 0.0251 | 0.08 | 0.02
11 | 3 | 1 | 0.03 | 0.0173 | 0.04 | 0.01
12 | 3 | 0 | 0.0367 | 0.0115 | 0.05 | 0.03
Yearly totals/averages | 51 | 2 | 0.0557 | 0.0249 | 0.12 | 0.01
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0367 | 0.0035 | 0.04 | 0.033
2 | 3 | 0 | 0.0347 | 0.0055 | 0.041 | 0.031
3 | 3 | 0 | 0.051 | 0.0217 | 0.074 | 0.031
4 | 4 | 0 | 0.0423 | 0.0213 | 0.067 | 0.018
5 | 3 | 0 | 0.0963 | 0.0393 | 0.121 | 0.051
6 | 3 | 0 | 0.097 | 0.0272 | 0.128 | 0.077
7 | 4 | 0 | 0.1053 | 0.0131 | 0.12 | 0.089
8 | 3 | 0 | 0.079 | 0.0191 | 0.091 | 0.057
9 | 4 | 0 | 0.1043 | 0.0078 | 0.11 | 0.093
10 | 3 | 0 | 0.075 | 0.0204 | 0.098 | 0.059
11 | 3 | 0 | 0.1063 | 0.0084 | 0.116 | 0.101
12 | 4 | 0 | 0.0867 | 0.0143 | 0.105 | 0.073
Yearly totals/averages | 40 | 0 | 0.0771 | 0.0314 | 0.128 | 0.018
plant GRDA | test period | 9/22/1999 | 9/22/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
GRDA | 1 | SUBBITUMINOUS/ BITUMINOUS | 0.1 | 1.0078 | 8.3348 | 8.9289
GRDA | 2 | SUBBITUMINOUS/ BITUMINOUS | 0.1 | 0.8418 | 6.908 | 7.1744
GRDA | 3 | SUBBITUMINOUS/ BITUMINOUS | 0.1 | 1.0223 | 8.4519 | 9.7883
Averages |  |  | 0.1 | 0.9573 | 7.8983 | 8.6306
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
GRDA | 1 | SO2/SDA | no bypass | -0.083 | -0.0228 | 8.9568 | 9.1353 | 84
GRDA | 2 | SO2/SDA | no bypass | -0.098 | -0.2435 | 9.0102 | 8.9249 | 84.2
GRDA | 3 | SO2/SDA | no bypass | 0.1518 | 0.1815 | 7.0123 | 8.0152 | 84.2
Averages |  | SO2/SDA | no bypass | -0.0097 | -0.0283 | 8.3264 | 8.6918 | 84.1
Laramie River Station |  | 3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | SDA
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 9 | 0 | 0.06 | 0.01 | 0.08 | 0.05
2 | 7 | 0 | 0.0414 | 0.0121 | 0.06 | 0.03
3 | 7 | 0 | 0.0457 | 0.0151 | 0.06 | 0.02
4 | 7 | 0 | 0.0557 | 0.0098 | 0.07 | 0.04
5 | 6 | 0 | 0.0517 | 0.016 | 0.06 | 0.02
6 | 6 | 0 | 0.06 | 0.0219 | 0.09 | 0.03
7 | 10 | 0 | 0.059 | 0.011 | 0.08 | 0.05
8 | 10 | 0 | 0.06 | 0.0194 | 0.09 | 0.03
9 | 9 | 0 | 0.0344 | 0.0073 | 0.05 | 0.03
10 | 10 | 0 | 0.047 | 0.0125 | 0.07 | 0.03
11 | 9 | 0 | 0.0511 | 0.0078 | 0.06 | 0.04
12 | 7 | 0 | 0.0586 | 0.0069 | 0.07 | 0.05
Yearly totals/averages | 97 | 0 | 0.0521 | 0.0148 | 0.09 | 0.02
plant Laramie 3 | test period | 9/22/1999 | 9/23/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Laramie 3 | 1 | SUBBITUMINOUS | 0.118 | 0.0584 | 0.5833 | 0.6319
Laramie 3 | 2 | SUBBITUMINOUS | 0.142 | 0.6085 | 7.206 | 7.736
Laramie 3 | 3 | SUBBITUMINOUS | 0.114 | 0.9548 | 9.0183 | 10.2704
Averages |  |  | 0.1247 | 0.5406 | 5.6025 | 6.2128
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Laramie 3 | 1 | SO2/SDA | no bypass | 0.7364 | -3.5534 | 2.632 | 2.8775 | 77.7
Laramie 3 | 2 | SO2/SDA | no bypass | 0.7429 | 0.5735 | 3.0454 | 3.2994 | 78.9
Laramie 3 | 3 | SO2/SDA | no bypass | 0.6322 | 0.6254 | 3.4737 | 3.8466 | 78.9
Averages |  | SO2/SDA | no bypass | 0.7038 | -0.7848 | 3.0504 | 3.3411 | 78.5
Wyodak |  | BW 91
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | SDA
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.0525 | 0.0377 | 0.09 | 0.02
2 | 4 | 0 | 0.0625 | 0.0126 | 0.08 | 0.05
3 | 4 | 0 | 0.095 | 0.0332 | 0.14 | 0.07
4 | 4 | 0 | 0.0625 | 0.0096 | 0.07 | 0.05
5 | 2 | 0 | 0.065 | 0.0071 | 0.07 | 0.06
6 | 5 | 0 | 0.072 | 0.0466 | 0.14 | 0.03
7 | 4 | 0 | 0.0625 | 0.005 | 0.07 | 0.06
8 | 4 | 0 | 0.0675 | 0.0222 | 0.09 | 0.04
9 | 4 | 0 | 0.065 | 0.0238 | 0.09 | 0.04
10 | 4 | 0 | 0.0425 | 0.005 | 0.05 | 0.04
11 | 4 | 0 | 0.0575 | 0.005 | 0.06 | 0.05
12 | 5 | 0 | 0.056 | 0.0195 | 0.09 | 0.04
Yearly totals/averages | 48 | 0 | 0.0633 | 0.0249 | 0.14 | 0.02
plant Wyodak | test period | 9/29/1999 | 9/30/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Wyodak | 1 | SUBBITUMINOUS | 0.03 | 5.6559 | 14.6905 | 12.7389
Wyodak | 2 | SUBBITUMINOUS | 0.04 | 3.8179 | 13.0783 | 12.3408
Wyodak | 3 | SUBBITUMINOUS | 0.05 | 3.0451 | 13.0803 | 12.4581
Averages |  |  | 0.04 | 4.1729 | 13.6164 | 12.5126
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Wyodak | 1 | SO2/SDA | no bypass | -2.0922 | 0.4469 | 8.0318 | 7.0455 | 82
Wyodak | 2 | SO2/SDA | no bypass | -1.3381 | 0.4273 | 8.0092 | 7.0676 | 82
Wyodak | 3 | SO2/SDA | no bypass | -0.8896 | 0.4305 | 8.1167 | 7.0974 | 81
Averages |  | SO2/SDA | no bypass | -1.44 | 0.4349 | 8.0526 | 7.0701 | 81.7
Craig |  | C3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 7 | 0 | 0.0314 | 0.0038 | 0.04 | 0.03
2 | 6 | 0 | 0.0217 | 0.0041 | 0.03 | 0.02
3 | 6 | 0 | 0.03 | 0.0155 | 0.06 | 0.02
4 | 6 | 0 | 0.0233 | 0.0052 | 0.03 | 0.02
5 | 8 | 0 | 0.0238 | 0.0106 | 0.05 | 0.02
6 | 7 | 0 | 0.0343 | 0.0215 | 0.08 | 0.02
7 | 8 | 0 | 0.0288 | 0.0099 | 0.04 | 0.02
8 | 10 | 0 | 0.023 | 0.0095 | 0.05 | 0.02
9 | 7 | 0 | 0.02 | 0 | 0.02 | 0.02
10 | 9 | 0 | 0.0222 | 0.0044 | 0.03 | 0.02
11 | 4 | 0 | 0.02 | 0 | 0.02 | 0.02
12 | 4 | 0 | 0.025 | 0.01 | 0.04 | 0.02
Yearly totals/averages | 82 | 0 | 0.0254 | 0.0103 | 0.08 | 0.02
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
2 | 1 | 0 | 0.03 | 0 | 0.03 | 0.03
6 | 1 | 0 | 0.05 | 0 | 0.05 | 0.05
8 | 1 | 0 | 0.03 | 0 | 0.03 | 0.03
Yearly totals/averages | 3 | 0 | 0.0367 | 0.0115 | 0.05 | 0.03
plant Craig 3 | test period | 10/2/1999 | 10/5/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Craig 3 | 1 | SUBBITUMINOUS | 0.011 | 1.1647 | 1.0209 | 1.093
Craig 3 | 2 | SUBBITUMINOUS | 0.01 | 1.4716 | 1.1657 | 1.2273
Craig 3 | 3 | SUBBITUMINOUS | 0.009 | 1.3182 | 0.9444 | 0.9713
Averages |  |  | 0.01 | 1.3182 | 1.0437 | 1.0972
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Craig 3 | 1 | SO2/SDA | no bypass | 0.2019 | 0.3155 | 0.6996 | 0.749 | 80.6
Craig 3 | 2 | SO2/SDA | no bypass | 0.1132 | 0.3981 | 0.7025 | 0.7395 | 85.6
Craig 3 | 3 | SO2/SDA | no bypass | 0.0691 | 0.2945 | 0.6669 | 0.6858 | 79.4
Averages |  | SO2/SDA | no bypass | 0.1281 | 0.336 | 0.6897 | 0.7248 | 81.9
Rawhide |  | 101
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.061 | 0.0095 | 0.071 | 0.052
2 | 3 | 0 | 0.0393 | 0.0075 | 0.048 | 0.035
3 | 3 | 0 | 0.0247 | 0.0061 | 0.03 | 0.018
4 | 4 | 0 | 0.0265 | 0.0196 | 0.054 | 0.012
5 | 3 | 0 | 0.024 | 0.01 | 0.034 | 0.014
6 | 2 | 0 | 0.0355 | 0.0233 | 0.052 | 0.019
7 | 4 | 0 | 0.0418 | 0.0136 | 0.06 | 0.028
8 | 6 | 0 | 0.054 | 0.0169 | 0.085 | 0.038
9 | 5 | 0 | 0.0418 | 0.0088 | 0.055 | 0.032
10 | 7 | 0 | 0.0493 | 0.0268 | 0.105 | 0.025
11 | 6 | 0 | 0.0682 | 0.026 | 0.112 | 0.044
12 | 7 | 0 | 0.0581 | 0.0327 | 0.125 | 0.028
Yearly totals/averages | 53 | 0 | 0.0469 | 0.0234 | 0.125 | 0.012
plant Rawhide | test period | 8/25/1999 | 8/26/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Rawhide | 1 | SUBBITUMINOUS | 0.07 | 1.7426 | 10.2792 | 10.1164
Rawhide | 2 | SUBBITUMINOUS | 0.07 | 2.1274 | 12.4065 | 11.1856
Rawhide | 3 | SUBBITUMINOUS | 0.08 | 2.0574 | 13.794 | 13.644
Averages |  |  | 0.0733 | 1.9758 | 12.1599 | 11.6487
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Rawhide | 1 | SO2/SDA | no bypass | -0.3759 | 0.1631 | 8.116 | 8.4699 | 103.8
Rawhide | 2 | SO2/SDA | no bypass | -0.3342 | 0.3203 | 7.7807 | 7.6072 | 104.9
Rawhide | 3 | SO2/SDA | no bypass | -0.0591 | 0.4715 | 7.1006 | 7.2119 | 103.3
Averages |  | SO2/SDA | no bypass | -0.2564 | 0.3183 | 7.6658 | 7.763 | 104
Sherburne County Generating Plant |  | #3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 7 | 0 | 0.04 | 0.02 | 0.06 | 0.01
2 | 4 | 0 | 0.0425 | 0.0096 | 0.05 | 0.03
3 | 7 | 0 | 0.0443 | 0.0098 | 0.06 | 0.03
4 | 7 | 0 | 0.0257 | 0.0172 | 0.05 | 0.01
5 | 9 | 0 | 0.0211 | 0.0169 | 0.05 | 0.01
6 | 9 | 0 | 0.0567 | 0.0229 | 0.1 | 0.01
7 | 8 | 0 | 0.09 | 0.0207 | 0.12 | 0.07
8 | 10 | 0 | 0.055 | 0.0299 | 0.11 | 0.03
9 | 9 | 0 | 0.0678 | 0.0156 | 0.1 | 0.05
10 | 8 | 0 | 0.0575 | 0.0231 | 0.09 | 0.03
11 | 9 | 0 | 0.0678 | 0.0148 | 0.09 | 0.05
12 | 7 | 0 | 0.0529 | 0.0221 | 0.08 | 0.02
Yearly totals/averages | 94 | 0 | 0.0528 | 0.0264 | 0.12 | 0.01
plant Sherburne | test period | 1/25/2000 | 1/26/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Sherburne | 1 | SUBBITUMINOUS | 0.08 | 1.3812 | 9.3878 | 8.2174
Sherburne | 2 | SUBBITUMINOUS | 0.08 | 1.3488 | 9.2466 | 8.0036
Sherburne | 3 | SUBBITUMINOUS | 0.07 | 1.3514 | 8.1969 | 7.4917
Averages |  |  | 0.0767 | 1.3605 | 8.9438 | 7.9042
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Sherburne | 1 | SO2/SDA | no bypass | 0.0699 | 0.2367 | 6.3215 | 6.2785 | 80
Sherburne | 2 | SO2/SDA | no bypass | -0.1891 | -0.1114 | 8.1514 | 8.9061 | 80
Sherburne | 3 | SO2/SDA | no bypass | -0.1719 | 0.0084 | 7.1077 | 7.4356 | 81
Averages |  | SO2/SDA | no bypass | -0.097 | 0.0446 | 7.1935 | 7.5401 | 80.3
Jim Bridger |  | BW 74
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 11 | 0 | 0.0545 | 0.0202 | 0.11 | 0.04
2 | 8 | 0 | 0.08 | 0.0307 | 0.13 | 0.04
3 | 13 | 0 | 0.0546 | 0.0139 | 0.08 | 0.04
4 | 11 | 0 | 0.0509 | 0.0104 | 0.07 | 0.04
5 | 11 | 0 | 0.0464 | 0.0163 | 0.09 | 0.03
6 | 10 | 0 | 0.052 | 0.0132 | 0.08 | 0.04
7 | 10 | 0 | 0.044 | 0.0084 | 0.06 | 0.03
8 | 9 | 0 | 0.0556 | 0.0201 | 0.09 | 0.04
9 | 12 | 0 | 0.0442 | 0.0144 | 0.07 | 0.03
10 | 11 | 0 | 0.04 | 0.0118 | 0.07 | 0.03
11 | 11 | 0 | 0.0427 | 0.0101 | 0.06 | 0.03
12 | 11 | 0 | 0.0445 | 0.0151 | 0.08 | 0.03
Yearly totals/averages | 128 | 0 | 0.0501 | 0.0178 | 0.13 | 0.03
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0867 | 0.0153 | 0.1 | 0.07
2 | 4 | 0 | 0.0425 | 0.005 | 0.05 | 0.04
3 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
4 | 3 | 0 | 0.04 | 0.01 | 0.05 | 0.03
5 | 3 | 0 | 0.0667 | 0.0289 | 0.1 | 0.05
6 | 3 | 0 | 0.04 | 0 | 0.04 | 0.04
7 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
8 | 3 | 0 | 0.0533 | 0.0058 | 0.06 | 0.05
9 | 3 | 0 | 0.0367 | 0.0058 | 0.04 | 0.03
10 | 3 | 0 | 0.04 | 0.01 | 0.05 | 0.03
11 | 1 | 0 | 0.04 | 0 | 0.04 | 0.04
12 | 3 | 0 | 0.04 | 0 | 0.04 | 0.04
Yearly totals/averages | 35 | 0 | 0.048 | 0.0171 | 0.1 | 0.03
plant Bridger | test period | 3/28/2000 | 3/29/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Bridger | 1 | SUBBITUMINOUS | 0.08 | 0 | 0 | 0
Bridger | 2 | SUBBITUMINOUS | 0.08 | 0 | 0 | 0
Bridger | 3 | SUBBITUMINOUS | 0.06 | 0 | 0 | 0
Averages |  |  | 0.0733
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Bridger | 1 | SO2/WETSCRUB | no bypass | 0.2319 | 0.1032 | 5.1983 | 4.9866 | 54
Bridger | 2 | SO2/WETSCRUB | no bypass | 0.2489 | 0.1552 | 5.0229 | 4.8182 | 53
Bridger | 3 | SO2/WETSCRUB | no bypass | 0.104 | 0.0295 | 4.4902 | 4.3073 | 54
Averages |  | SO2/WETSCRUB | no bypass | 0.1949 | 0.096 | 4.9038 | 4.704 | 53.7
Laramie River Station |  | 1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 9 | 0 | 0.06 | 0.01 | 0.08 | 0.05
2 | 7 | 0 | 0.0414 | 0.0121 | 0.06 | 0.03
3 | 7 | 0 | 0.0457 | 0.0151 | 0.06 | 0.02
4 | 7 | 0 | 0.0557 | 0.0098 | 0.07 | 0.04
5 | 6 | 0 | 0.0517 | 0.016 | 0.06 | 0.02
6 | 6 | 0 | 0.06 | 0.0219 | 0.09 | 0.03
7 | 10 | 0 | 0.059 | 0.011 | 0.08 | 0.05
8 | 10 | 0 | 0.06 | 0.0194 | 0.09 | 0.03
9 | 9 | 0 | 0.0344 | 0.0073 | 0.05 | 0.03
10 | 10 | 0 | 0.047 | 0.0125 | 0.07 | 0.03
11 | 9 | 0 | 0.0511 | 0.0078 | 0.06 | 0.04
12 | 7 | 0 | 0.0586 | 0.0069 | 0.07 | 0.05
Yearly totals/averages | 97 | 0 | 0.0521 | 0.0148 | 0.09 | 0.02
plant Laramie 1 | test period | 9/20/1999 | 9/21/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Laramie 1 | 1 | SUBBITUMINOUS | 0.103
Laramie 1 | 2 | SUBBITUMINOUS | 0.111
Laramie 1 | 3 | SUBBITUMINOUS | 0.144
Averages |  |  | 0.1193
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Laramie 1 | 1 | SO2/WETSCRUB | after bypass | 0.7311 | 0.6209 | 2.3351 | 2.9793 | 64.4
Laramie 1 | 2 | SO2/WETSCRUB | after bypass | 0.6785 | 0.524 | 2.9891 | 3.612 | 63.3
Laramie 1 | 3 | SO2/WETSCRUB | after bypass | 0.7917 | 0.6775 | 2.5221 | 2.4638 | 63.3
Averages |  | SO2/WETSCRUB | after bypass | 0.7338 | 0.6074 | 2.6154 | 3.0184 | 63.7
Sam Seymour |  | 3
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- CS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 11 | 0 | 0.0909 | 0.053 | 0.18 | 0.01
2 | 9 | 0 | 0.08 | 0.0374 | 0.16 | 0.04
3 | 13 | 0 | 0.08 | 0.0216 | 0.12 | 0.04
4 | 10 | 0 | 0.0816 | 0.0204 | 0.12 | 0.056
5 | 9 | 0 | 0.0911 | 0.0247 | 0.14 | 0.06
6 | 7 | 0 | 0.0729 | 0.0049 | 0.08 | 0.07
7 | 9 | 0 | 0.0733 | 0.026 | 0.13 | 0.04
8 | 6 | 0 | 0.07 | 0.0374 | 0.13 | 0.03
9 | 10 | 0 | 0.112 | 0.0421 | 0.18 | 0.04
10 | 7 | 0 | 0.0943 | 0.0346 | 0.15 | 0.05
11 | 8 | 0 | 0.0875 | 0.0661 | 0.24 | 0.03
12 | 5 | 0 | 0.078 | 0.037 | 0.14 | 0.05
Yearly totals/averages | 104 | 0 | 0.0852 | 0.0367 | 0.24 | 0.01
plant Sam Seymour | test period | 12/2/1998 | 12/3/1998
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Sam Seymour | 1 | SUBBITUMINOUS | 0.139
Sam Seymour | 2 | SUBBITUMINOUS | 0.115
Sam Seymour | 3 | SUBBITUMINOUS | 0.114
Averages |  |  | 0.1227
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Sam Seymour | 1 | SO2/WETSCRUB | after control | 0.6213 | -0.3143 | 4.4713 | 8.4097 | 57.1
Sam Seymour | 2 | SO2/WETSCRUB | after control | 0.4851 | -0.4656 | 4.9774 | 9.1959 | 53.9
Sam Seymour | 3 | SO2/WETSCRUB | after control | 0.5809 | 0.1703 | 3.9929 | 8.3002 | 56.1
Averages |  | SO2/WETSCRUB | after control | 0.5624 | -0.2032 | 4.4806 | 8.6353 | 55.7
Coronado |  | U1B
Boiler/NOx type: | CONV/PC/NOX/WET
Particulate control: | ESP- HS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.0725 | 0.0499 | 0.14 | 0.03
2 | 4 | 0 | 0.1 | 0.0942 | 0.24 | 0.04
3 | 5 | 0 | 0.064 | 0.0472 | 0.14 | 0.02
4 | 5 | 0 | 0.046 | 0.0089 | 0.06 | 0.04
5 | 9 | 0 | 0.0767 | 0.0412 | 0.16 | 0.04
6 | 7 | 0 | 0.04 | 0.0082 | 0.05 | 0.03
7 | 6 | 0 | 0.04 | 0.0063 | 0.05 | 0.03
8 | 3 | 0 | 0.04 | 0.0173 | 0.05 | 0.02
9 | 5 | 0 | 0.056 | 0.0351 | 0.11 | 0.02
10 | 4 | 0 | 0.0475 | 0.0126 | 0.06 | 0.03
11 | 4 | 0 | 0.0475 | 0.0275 | 0.08 | 0.02
12 | 3 | 0 | 0.0433 | 0.0058 | 0.05 | 0.04
Yearly totals/averages | 59 | 0 | 0.0569 | 0.0382 | 0.24 | 0.02
plant Coronado | test period | 10/18/1999 | 10/19/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Coronado | 1 | SUBBITUMINOUS | 0.035 | 0 | 0 | 0
Coronado | 2 | SUBBITUMINOUS | 0.039 | 0 | 0 | 0
Coronado | 3 | SUBBITUMINOUS | 0.031 | 0 | 0 | 0
Averages |  |  | 0.035
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Coronado | 1 | SO2/WETSCRUB | after control | 0.2363 | -0.1302 | 2.3894 | 2.5964 | 48
Coronado | 2 | SO2/WETSCRUB | after control | 0.407 | -0.2141 | 2.0217 | 2.3583 | 47
Coronado | 3 | SO2/WETSCRUB | after control | 0.2749 | -0.113 | 1.9959 | 2.3856 | 49
Averages |  | SO2/WETSCRUB | after control | 0.3061 | -0.1524 | 2.1357 | 2.4468 | 48
Craig |  | C1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- HS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 7 | 0 | 0.0314 | 0.0038 | 0.04 | 0.03
2 | 6 | 0 | 0.0217 | 0.0041 | 0.03 | 0.02
3 | 6 | 0 | 0.03 | 0.0155 | 0.06 | 0.02
4 | 6 | 0 | 0.0233 | 0.0052 | 0.03 | 0.02
5 | 8 | 0 | 0.0238 | 0.0106 | 0.05 | 0.02
6 | 7 | 0 | 0.0343 | 0.0215 | 0.08 | 0.02
7 | 8 | 0 | 0.0288 | 0.0099 | 0.04 | 0.02
8 | 10 | 0 | 0.023 | 0.0095 | 0.05 | 0.02
9 | 7 | 0 | 0.02 | 0 | 0.02 | 0.02
10 | 9 | 0 | 0.0222 | 0.0044 | 0.03 | 0.02
11 | 4 | 0 | 0.02 | 0 | 0.02 | 0.02
12 | 4 | 0 | 0.025 | 0.01 | 0.04 | 0.02
Yearly totals/averages | 82 | 0 | 0.0254 | 0.0103 | 0.08 | 0.02
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
2 | 1 | 0 | 0.03 | 0 | 0.03 | 0.03
6 | 1 | 0 | 0.05 | 0 | 0.05 | 0.05
8 | 1 | 0 | 0.03 | 0 | 0.03 | 0.03
Yearly totals/averages | 3 | 0 | 0.0367 | 0.0115 | 0.05 | 0.03
plant Craig 1 | test period | 9/27/1999 | 9/29/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Craig 1 | 1 | SUBBITUMINOUS | 0.022
Craig 1 | 2 | SUBBITUMINOUS | 0.025
Craig 1 | 3 | SUBBITUMINOUS | 0.021
Averages |  |  | 0.0227
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Craig 1 | 1 | SO2/WETSCRUB | after bypass | 0.2612 | 0.5242 | 1.3191 | 1.3582 | 64
Craig 1 | 2 | SO2/WETSCRUB | after bypass | 0.332 | 0.2905 | 1.3418 | 1.4535 | 64
Craig 1 | 3 | SO2/WETSCRUB | after bypass | 0.1169 | 0.0309 | 1.4894 | 1.5252 | 58
Averages |  | SO2/WETSCRUB | after bypass | 0.2367 | 0.2819 | 1.3834 | 1.4456 | 62
San Juan |  | 2
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- HS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.1148 | 0.0086 | 0.121 | 0.102
2 | 4 | 0 | 0.0845 | 0.0087 | 0.097 | 0.078
3 | 5 | 0 | 0.097 | 0.0236 | 0.118 | 0.059
4 | 4 | 0 | 0.0873 | 0.0155 | 0.105 | 0.071
5 | 4 | 0 | 0.1003 | 0.0275 | 0.124 | 0.07
6 | 5 | 0 | 0.0846 | 0.0175 | 0.102 | 0.055
7 | 4 | 0 | 0.0978 | 0.0171 | 0.118 | 0.077
8 | 4 | 0 | 0.0903 | 0.0255 | 0.115 | 0.064
9 | 5 | 0 | 0.083 | 0.0262 | 0.124 | 0.053
10 | 4 | 0 | 0.0745 | 0.0094 | 0.084 | 0.065
11 | 4 | 0 | 0.1083 | 0.0366 | 0.141 | 0.057
12 | 5 | 0 | 0.0836 | 0.0263 | 0.109 | 0.055
Yearly totals/averages | 52 | 0 | 0.0918 | 0.0225 | 0.141 | 0.053
plant San Juan | test period | 10/20/1999 | 10/22/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
San Juan | 1 | SUBBITUMINOUS | 0.045
San Juan | 2 | SUBBITUMINOUS | 0.051
San Juan | 3 | SUBBITUMINOUS | 0.065
Averages |  |  | 0.0537
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
San Juan | 1 | SO2/WETSCRUB | after control | -0.1872 | 0.3674 | 5.3553 | 5.4848 | 47.7
San Juan | 2 | SO2/WETSCRUB | after control | 0.2634 | 0.3135 | 3.4321 | 3.7679 | 47.7
San Juan | 3 | SO2/WETSCRUB | after control | 0.4478 | 0.4239 | 3.4665 | 3.6036 | 48.3
Averages |  | SO2/WETSCRUB | after control | 0.1747 | 0.3683 | 4.0847 | 4.2854 | 47.9
Stanton Station |  | 1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | NONE
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.0728 | 0.0079 | 0.082 | 0.064
2 | 4 | 0 | 0.0763 | 0.0036 | 0.081 | 0.073
3 | 3 | 0 | 0.0763 | 0.0103 | 0.085 | 0.065
4 | 3 | 0 | 0.0743 | 0.0087 | 0.084 | 0.067
5 | 4 | 0 | 0.0568 | 0.007 | 0.067 | 0.051
6 | 3 | 0 | 0.051 | 0.001 | 0.052 | 0.05
7 | 3 | 0 | 0.104 | 0 | 0.104 | 0.104
8 | 3 | 0 | 0.116 | 0 | 0.116 | 0.116
9 | 3 | 0 | 0.115 | 0 | 0.115 | 0.115
10 | 3 | 0 | 0.115 | 0 | 0.115 | 0.115
11 | 3 | 0 | 0.091 | 0 | 0.091 | 0.091
12 | 4 | 0 | 0.1198 | 0.0005 | 0.12 | 0.119
Yearly totals/averages | 40 | 0 | 0.0883 | 0.0242 | 0.12 | 0.05
plant Stanton 1 | test period | 8/23/1999 | 8/28/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Stanton 1 | 1 | LIGNITE | 0.086 | 0.4799 | 3.3483 | 6.9181
Stanton 1 | 2 | LIGNITE | 0.105 | 0.3535 | 2.977 | 6.285
Stanton 1 | 3 | LIGNITE | 0.056 | 0.7912 | 3.5602 | 6.8231
Averages |  |  | 0.0823 | 0.5415 | 3.2952 | 6.6754
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Stanton 1 | 1 | PM/ESP- CS | no bypass | 0.513 | 0.0199 | 3.9237 | 6.7787 | 191.1
Stanton 1 | 2 | PM/ESP- CS | no bypass | 0.6209 | -0.0875 | 3.7032 | 6.8356 | 150
Stanton 1 | 3 | PM/ESP- CS | no bypass | 0.1889 | -0.0395 | 4.2438 | 7.0931 | 158.3
Averages |  | PM/ESP- CS | no bypass | 0.4409 | -0.0357 | 3.9569 | 6.9024 | 166.5
La Cygne |  | 1
Boiler/NOx type: | CYCLONE/NOX/WET
Particulate control: | PARTSCRUB
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.076 | 0.0207 | 0.11 | 0.06
2 | 4 | 0 | 0.06 | 0.0082 | 0.07 | 0.05
3 | 3 | 0 | 0.0567 | 0.0058 | 0.06 | 0.05
4 | 6 | 0 | 0.0567 | 0.0207 | 0.09 | 0.03
5 | 6 | 0 | 0.05 | 0.0167 | 0.07 | 0.02
6 | 4 | 0 | 0.0475 | 0.0287 | 0.09 | 0.03
7 | 6 | 0 | 0.0317 | 0.0133 | 0.05 | 0.02
8 | 3 | 0 | 0.0467 | 0.0153 | 0.06 | 0.03
9 | 3 | 0 | 0.0667 | 0.0208 | 0.09 | 0.05
10 | 2 | 0 | 0.055 | 0.0354 | 0.08 | 0.03
11 | 3 | 0 | 0.0467 | 0.0153 | 0.06 | 0.03
12 | 3 | 0 | 0.0367 | 0.0153 | 0.05 | 0.02
Yearly totals/averages | 48 | 0 | 0.0523 | 0.0205 | 0.11 | 0.02
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.1013 | 0.0385 | 0.139 | 0.062
2 | 3 | 0 | 0.1327 | 0.0246 | 0.156 | 0.107
3 | 4 | 0 | 0.1113 | 0.0232 | 0.136 | 0.081
4 | 4 | 0 | 0.0968 | 0.0285 | 0.137 | 0.075
5 | 3 | 0 | 0.1167 | 0.0245 | 0.141 | 0.092
6 | 4 | 0 | 0.1098 | 0.0109 | 0.119 | 0.096
7 | 3 | 0 | 0.2357 | 0.03 | 0.253 | 0.201
8 | 3 | 0 | 0.1587 | 0.0282 | 0.181 | 0.127
9 | 2 | 0 | 0.0785 | 0.0007 | 0.079 | 0.078
10 | 3 | 0 | 0.122 | 0.0061 | 0.129 | 0.118
11 | 3 | 0 | 0.1087 | 0.0059 | 0.113 | 0.102
12 | 3 | 0 | 0.1307 | 0.0273 | 0.162 | 0.112
Yearly totals/averages | 38 | 0 | 0.1249 | 0.0426 | 0.253 | 0.062
plant Lacygne | test period | 10/16/1999 | 10/18/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Lacygne | 1 | SUBBITUMINOUS | 0.11 |  |  | 8.6142
Lacygne | 2 | SUBBITUMINOUS | 0.102 |  |  | 7.5056
Lacygne | 3 | SUBBITUMINOUS | 0.098 |  |  | 5.1564
Averages |  |  | 0.1033 |  |  | 7.092
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Lacygne | 1 | PM/PARTSCRUB | no bypass | 0.3651 | 0.2208 | 5.9185 | 6.7188 | 72
Lacygne | 2 | PM/PARTSCRUB | no bypass | 0.3834 | 0.2378 | 5.357 | 5.7258 | 72
Lacygne | 3 | PM/PARTSCRUB | no bypass | 0.5325 | 0.2058 | 3.8827 | 4.0974 | 74
Averages |  | PM/PARTSCRUB | no bypass | 0.427 | 0.2215 | 5.0527 | 5.514 | 72.7
Nelson Dewey |  | 1
Boiler/NOx type: | CYCLONE/NONOX/WET
Particulate control: | ESP- HS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0733 | 0.0231 | 0.1 | 0.06
2 | 3 | 0 | 0.1033 | 0.0321 | 0.14 | 0.08
3 | 3 | 0 | 0.11 | 0.01 | 0.12 | 0.1
4 | 3 | 0 | 0.0733 | 0.0115 | 0.08 | 0.06
5 | 3 | 0 | 0.0733 | 0.0115 | 0.08 | 0.06
6 | 5 | 0 | 0.09 | 0.0071 | 0.1 | 0.08
7 | 3 | 0 | 0.0933 | 0.0058 | 0.1 | 0.09
8 | 7 | 0 | 0.0557 | 0.0282 | 0.09 | 0.02
9 | 3 | 0 | 0.0833 | 0.0058 | 0.09 | 0.08
10 | 3 | 0 | 0.0767 | 0.0058 | 0.08 | 0.07
11 | 3 | 0 | 0.0767 | 0.0058 | 0.08 | 0.07
12 | 4 | 0 | 0.0825 | 0.005 | 0.09 | 0.08
Yearly totals/averages | 43 | 0 | 0.0805 | 0.0214 | 0.14 | 0.02
plant Nelson | test period | 2/8/2000 | 2/9/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Nelson | 1 | SUBBITUMINOUS/ PETCOKE | 0.06 | 0.5608 | 2.587 | 2.6629
Nelson | 2 | SUBBITUMINOUS/ PETCOKE | 0.06 | 0.3776 | 1.7358 | 1.7531
Nelson | 3 | SUBBITUMINOUS/ PETCOKE | 0.06 | 0.3607 | 1.6669 | 1.576
Averages |  |  | 0.06 | 0.433 | 1.9965 | 1.9973
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Nelson | 1 | PM/ESP- HS | no bypass | 0.4752 | 0.0195 | 2.4211 | 2.6107 | 258
Nelson | 2 | PM/ESP- HS | no bypass | 0.6146 | -0.056 | 1.7717 | 1.8512 | 258
Nelson | 3 | PM/ESP- HS | no bypass | 0.5772 | -0.2327 | 1.9536 | 1.9427 | 264
Averages |  | PM/ESP- HS | no bypass | 0.5557 | -0.0897 | 2.0488 | 2.1349 | 260
Leland Olds Station |  | 2
Boiler/NOx type: | CYCLONE/NONOX/WET
Particulate control: | ESP- CS
SO2 control: | NONE
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 10 | 0 | 0.0738 | 0.0126 | 0.097 | 0.05
2 | 10 | 0 | 0.0925 | 0.0218 | 0.129 | 0.058
3 | 11 | 0 | 0.0815 | 0.0119 | 0.097 | 0.054
4 | 9 | 0 | 0.0674 | 0.0064 | 0.076 | 0.055
5 | 11 | 1 | 0.0566 | 0.0149 | 0.089 | 0.025
6 | 9 | 2 | 0.0558 | 0.02 | 0.082 | 0.025
7 | 8 | 2 | 0.0539 | 0.0181 | 0.068 | 0.025
8 | 9 | 0 | 0.0701 | 0.017 | 0.097 | 0.05
9 | 8 | 0 | 0.0746 | 0.0195 | 0.103 | 0.05
11 | 8 | 0 | 0.0743 | 0.0123 | 0.092 | 0.057
12 | 10 | 0 | 0.0838 | 0.0102 | 0.099 | 0.062
Yearly totals/averages | 103 | 5 | 0.0717 | 0.019 | 0.129 | 0.025
plant Leland | test period | 7/15/1999 | 7/16/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Leland | 1 | LIGNITE | 0.025 | 1.0926 | 2.6015 | 2.8228
Leland | 2 | LIGNITE | 0.056 | 1.466 | 7.6726 | 6.8304
Averages |  |  | 0.0405 | 1.2793 | 5.137 | 4.8266
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Leland | 1 | PM/ESP- CS | no bypass | -0.2982 | -0.2353 | 3.0909 | 3.4876 | 182
Leland | 2 | PM/ESP- CS | no bypass | 0.0424 | 0.3326 | 5.0115 | 4.5589 | 182
Averages |  | PM/ESP- CS | no bypass | -0.1279 | 0.0487 | 4.0512 | 4.0233 | 182
Stockton Cogen Company |  | GEN1
Boiler/NOx type: | FBC/SNCR
Particulate control: | BAGHOUSE
SO2 control: | FBC
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0373 | 0.0204 | 0.052 | 0.014
2 | 5 | 0 | 0.015 | 0.0141 | 0.04 | 0.007
3 | 3 | 0 | 0.0273 | 0.0126 | 0.039 | 0.014
4 | 3 | 0 | 0.0643 | 0.0267 | 0.095 | 0.046
5 | 4 | 0 | 0.0343 | 0.0207 | 0.065 | 0.02
6 | 4 | 0 | 0.0585 | 0.0142 | 0.076 | 0.043
7 | 3 | 0 | 0.0787 | 0.0338 | 0.117 | 0.053
8 | 3 | 0 | 0.035 | 0.019 | 0.056 | 0.019
9 | 3 | 0 | 0.0347 | 0.0102 | 0.042 | 0.023
10 | 3 | 0 | 0.018 | 0.0075 | 0.026 | 0.011
11 | 3 | 0 | 0.027 | 0.0052 | 0.03 | 0.021
12 | 3 | 0 | 0.0673 | 0.028 | 0.09 | 0.036
Yearly totals/averages | 40 | 0 | 0.0404 | 0.0258 | 0.117 | 0.007
Fuel number2 | PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 1 | 0 | 0.045 | 0 | 0.045 | 0.045
4 | 1 | 0 | 0.012 | 0 | 0.012 | 0.012
7 | 1 | 0 | 0.031 | 0 | 0.031 | 0.031
Yearly totals/averages | 3 | 0 | 0.0293 | 0.0166 | 0.045 | 0.012
Fuel number3 | TIRES
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
3 | 1 | 1 | 0.1 | 0 | 0.1 | 0.1
4 | 1 | 1 | 0.1 | 0 | 0.1 | 0.1
7 | 1 | 1 | 0.1 | 0 | 0.1 | 0.1
Yearly totals/averages | 3 | 3 | 0.1 | 0 | 0.1 | 0.1
plant Stockton | test period | 10/20/1999 | 10/22/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Stockton | 1 | BITUMINOUS/ PETCOKE | 0.026 | 1.7824 | 3.7573 | 2.1437
Stockton | 2 | BITUMINOUS/ PETCOKE | 0.026 | 1.2375 | 2.4873 | 1.2776
Stockton | 3 | BITUMINOUS/ PETCOKE | 0.029 | 1.4186 | 3.3572 | 1.6883
Averages |  |  | 0.027 | 1.4795 | 3.2006 | 1.7032
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Stockton | 1 | PM/BAGHOUSE | no bypass | 0.9098 | 0.9435 | 0.1901 | 0.1212 | 147
Stockton | 2 | PM/BAGHOUSE | no bypass | 0.8714 | 0.8895 | 0.2585 | 0.1412 | 146
Stockton | 3 | PM/BAGHOUSE | no bypass | 0.897 | 0.9216 | 0.2439 | 0.1325 | 145
Averages |  | PM/BAGHOUSE | no bypass | 0.8927 | 0.9182 | 0.2308 | 0.1316 | 146
Scrubgrass Generating Company L. P. |  | GEN1
Boiler/NOx type: | FBC/NONOX
Particulate control: | BAGHOUSE
SO2 control: | FBC
Test on last control unit
Fuel number1 | WASTE BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.6575 | 0.1253 | 0.83 | 0.56
2 | 4 | 0 | 0.79 | 0.1523 | 1.01 | 0.67
3 | 5 | 0 | 0.722 | 0.2449 | 1.08 | 0.5
4 | 3 | 0 | 0.8167 | 0.2363 | 1 | 0.55
5 | 3 | 0 | 0.7 | 0.0656 | 0.76 | 0.63
6 | 5 | 0 | 0.834 | 0.1981 | 1.08 | 0.57
7 | 4 | 0 | 0.5875 | 0.1417 | 0.8 | 0.51
8 | 6 | 0 | 0.655 | 0.1115 | 0.84 | 0.56
9 | 4 | 0 | 0.5 | 0.0668 | 0.57 | 0.41
10 | 4 | 0 | 0.56 | 0.2412 | 0.89 | 0.32
11 | 5 | 0 | 0.822 | 0.1706 | 0.97 | 0.53
12 | 4 | 0 | 0.775 | 0.1287 | 0.95 | 0.64
Yearly totals/averages | 51 | 0 | 0.7029 | 0.1833 | 1.08 | 0.32
plant Scrubgrass | test period | 9/14/1999 | 9/17/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Scrubgrass | 1 | WASTE BITUMINOUS | 0.55 | 0.9438 | 61.0042 | 132.7702
Scrubgrass | 2 | WASTE BITUMINOUS | 0.52 | 0.711 | 43.3954 | 89.4894
Scrubgrass | 3 | WASTE BITUMINOUS | 0.51 | 0.4262 | 27.1852 | 55.2757
Averages |  |  | 0.5267 | 0.6937 | 43.8616 | 92.5118
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Scrubgrass | 1 | PM/BAGHOUSE | no bypass | 0.9992 | 0.9992 | 0.0516 | 0.1056 | 156
Scrubgrass | 2 | PM/BAGHOUSE | no bypass | 0.9992 | 0.999 | 0.0483 | 0.0917 | 157
Scrubgrass | 3 | PM/BAGHOUSE | no bypass | 0.9993 | 0.9985 | 0.0455 | 0.0835 | 158
Averages |  | PM/BAGHOUSE | no bypass | 0.9992 | 0.9989 | 0.0485 | 0.0936 | 157
R.M. Heskett Station |  | B2
Boiler/NOx type: | FBC/NONOX
Particulate control: | ESP- CS
SO2 control: | FBC
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.1157 | 0.0429 | 0.165 | 0.087
2 | 3 | 0 | 0.099 | 0.0339 | 0.137 | 0.072
3 | 3 | 0 | 0.0843 | 0.0509 | 0.143 | 0.052
4 | 3 | 0 | 0.104 | 0.0226 | 0.125 | 0.08
5 | 3 | 0 | 0.1043 | 0.0223 | 0.13 | 0.09
6 | 3 | 0 | 0.1007 | 0.0117 | 0.111 | 0.088
7 | 3 | 0 | 0.091 | 0.0092 | 0.101 | 0.083
8 | 3 | 0 | 0.0597 | 0.0218 | 0.084 | 0.042
9 | 3 | 0 | 0.0667 | 0.0347 | 0.099 | 0.03
10 | 3 | 0 | 0.0757 | 0.0215 | 0.1 | 0.059
11 | 3 | 0 | 0.0757 | 0.0225 | 0.098 | 0.053
12 | 3 | 0 | 0.0807 | 0.0306 | 0.116 | 0.062
Yearly totals/averages | 36 | 0 | 0.0881 | 0.0295 | 0.165 | 0.03
plant Heskett | test period | 7/19/1999 | 7/20/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Heskett | 1 | LIGNITE | 0.098 | 0.9875 | 8.9374 | 9.6445
Heskett | 2 | LIGNITE | 0.088 | 0.5129 | 4.1458 | 4.6761
Heskett | 3 | LIGNITE | 0.073 | 0.958 | 6.5565 | 7.6525
Averages |  |  | 0.0863 | 0.8195 | 6.5466 | 7.3244
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Heskett | 1 | PM/ESP- CS | no bypass | 0.5641 | 0.5538 | 3.9456 | 4.3019 | 159
Heskett | 2 | PM/ESP- CS | no bypass | 0.5477 | 0.1109 | 3.6556 | 4.1561 | 153
Heskett | 3 | PM/ESP- CS | no bypass | 0.5723 | 0.5462 | 2.9273 | 3.4724 | 161
Averages |  | PM/ESP- CS | no bypass | 0.5614 | 0.4036 | 3.5095 | 3.9768 | 157.7
TNP-One |  | U2
Boiler/NOx type: | FBC/NONOX
Particulate control: | BAGHOUSE
SO2 control: | FBC
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 4 | 0.01 | 0 | 0.01 | 0.01
2 | 4 | 4 | 0.01 | 0 | 0.01 | 0.01
3 | 4 | 4 | 0.01 | 0 | 0.01 | 0.01
4 | 4 | 2 | 0.02 | 0.0129 | 0.037 | 0.01
5 | 4 | 2 | 0.0325 | 0.0278 | 0.067 | 0.01
6 | 4 | 0 | 0.0283 | 0.0062 | 0.035 | 0.02
7 | 6 | 0 | 0.0618 | 0.0297 | 0.113 | 0.035
8 | 6 | 3 | 0.019 | 0.0105 | 0.033 | 0.01
9 | 6 | 6 | 0.01 | 0 | 0.01 | 0.01
10 | 19 | 0 | 0.0544 | 0.0117 | 0.068 | 0.026
11 | 18 | 0 | 0.0427 | 0.0082 | 0.059 | 0.028
12 | 20 | 14 | 0.0141 | 0.0065 | 0.027 | 0.01
Yearly totals/averages | 99 | 39 | 0.031 | 0.0217 | 0.113 | 0.01
plant TNP | test period | 10/6/1999 | 10/8/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
TNP | 1 | LIGNITE | 0.222 | 1.0984 | 25.6131 | 27.0916
TNP | 2 | LIGNITE | 0.18 | 0.8283 | 15.1977 | 15.2571
TNP | 3 | LIGNITE | 0.362 | 0.9163 | 36.8569 | 35.1151
Averages |  |  | 0.2547 | 0.9477 | 25.8893 | 25.8212
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
TNP | 1 | PM/BAGHOUSE | no bypass | 0.5067 | 0.5511 | 11.5024 | 12.1664 | 177
TNP | 2 | PM/BAGHOUSE | no bypass | 0.6187 | 0.5396 | 6.9966 | 7.0239 | 178
TNP | 3 | PM/BAGHOUSE | no bypass | 0.6506 | 0.6188 | 14.0528 | 13.3887 | 171
Averages |  | PM/BAGHOUSE | no bypass | 0.592 | 0.5698 | 10.8506 | 10.8596 | 175.3
Kline Township Cogeneration Facility |  | GEN1
Boiler/NOx type: | FBC/NONOX
Particulate control: | BAGHOUSE
SO2 control: | FBC
Test on last control unit
Fuel number1 | WASTE ANTHRACITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.176 | 0.0207 | 0.21 | 0.16
2 | 4 | 0 | 0.165 | 0.0208 | 0.19 | 0.14
3 | 4 | 0 | 0.1175 | 0.0512 | 0.17 | 0.05
4 | 4 | 0 | 0.1625 | 0.0222 | 0.19 | 0.14
5 | 5 | 0 | 0.178 | 0.037 | 0.22 | 0.12
6 | 4 | 0 | 0.1725 | 0.0126 | 0.19 | 0.16
7 | 4 | 0 | 0.195 | 0.0311 | 0.24 | 0.17
8 | 6 | 0 | 0.1767 | 0.0489 | 0.23 | 0.11
9 | 5 | 0 | 0.162 | 0.0217 | 0.19 | 0.13
10 | 5 | 0 | 0.184 | 0.0152 | 0.2 | 0.16
11 | 5 | 0 | 0.178 | 0.0148 | 0.2 | 0.16
12 | 4 | 0 | 0.2075 | 0.0236 | 0.24 | 0.19
Yearly totals/averages | 55 | 0 | 0.1733 | 0.0333 | 0.24 | 0.05
plant Kline | test period | 10/28/1999 | 10/29/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Kline | 1 | WASTE ANTHRACITE | 0.3 | 0.303 | 17.788 | 32.3043
Kline | 2 | WASTE ANTHRACITE | 0.4 | 0.2045 | 16.1984 | 31.2287
Kline | 3 | WASTE ANTHRACITE | 0.3 | 0.2949 | 17.9438 | 32.5127
Averages |  |  | 0.3333 | 0.2675 | 17.3101 | 32.0152
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Kline | 1 | PM/BAGHOUSE | no bypass | 0.9994 | 0.9975 | 0.0332 | 0.0801 | 173
Kline | 2 | PM/BAGHOUSE | no bypass | 0.9996 | 0.9974 | 0.0315 | 0.0801 | 174
Kline | 3 | PM/BAGHOUSE | no bypass | 0.9995 | 0.9974 | 0.033 | 0.0846 | 174
Averages |  | PM/BAGHOUSE | no bypass | 0.9995 | 0.9975 | 0.0326 | 0.0816 | 173.7
Dwayne Collier Battle Cogeneration Facility |  | 2B
Boiler/NOx type: | STOKER/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.048 | 0.0164 | 0.07 | 0.03
2 | 5 | 0 | 0.114 | 0.0532 | 0.17 | 0.05
3 | 4 | 0 | 0.0825 | 0.0206 | 0.11 | 0.06
4 | 5 | 0 | 0.056 | 0.0089 | 0.07 | 0.05
5 | 4 | 0 | 0.095 | 0.0173 | 0.11 | 0.08
6 | 4 | 0 | 0.1 | 0.0424 | 0.13 | 0.04
7 | 5 | 0 | 0.102 | 0.0676 | 0.22 | 0.05
8 | 3 | 0 | 0.07 | 0.03 | 0.1 | 0.04
9 | 5 | 0 | 0.062 | 0.0239 | 0.1 | 0.04
10 | 3 | 0 | 0.0633 | 0.0115 | 0.07 | 0.05
11 | 4 | 0 | 0.0775 | 0.0222 | 0.11 | 0.06
12 | 7 | 0 | 0.0586 | 0.0248 | 0.09 | 0.02
Yearly totals/averages | 54 | 0 | 0.0767 | 0.0369 | 0.22 | 0.02
plant Collier | test period | 11/16/1999 | 11/18/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Collier | 1 | BITUMINOUS | 0.03 | 0.7164 | 1.5551 | 1.6535
Collier | 2 | BITUMINOUS | 0.03 | 0.8077 | 1.7432 | 1.9258
Collier | 3 | BITUMINOUS | 0.03 | 0.679 | 1.4624 | 1.5313
Averages |  |  | 0.03 | 0.7344 | 1.5869 | 1.7035
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Collier | 1 | SO2/SDA | no bypass | 0.9475 | 0.9292 | 0.114 | 0.1171 | 85
Collier | 2 | SO2/SDA | no bypass | 0.9521 | 0.9435 | 0.1033 | 0.1089 | 86
Collier | 3 | SO2/SDA | no bypass | 0.9565 | 0.9371 | 0.0937 | 0.0963 | 86
Averages |  | SO2/SDA | no bypass | 0.952 | 0.9366 | 0.1037 | 0.1074 | 85.7
Big Brown |  | 1
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- CS/BAGHOUSE
SO2 control: | NONE
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.236 | 0.1222 | 0.42 | 0.11
2 | 4 | 1 | 0.1113 | 0.0614 | 0.16 | 0.025
3 | 5 | 0 | 0.156 | 0.0635 | 0.23 | 0.07
4 | 6 | 1 | 0.1142 | 0.0767 | 0.21 | 0.025
5 | 6 | 0 | 0.1283 | 0.0591 | 0.22 | 0.05
6 | 6 | 3 | 0.0458 | 0.0248 | 0.08 | 0.025
7 | 5 | 4 | 0.03 | 0.0112 | 0.05 | 0.025
8 | 5 | 1 | 0.071 | 0.0288 | 0.09 | 0.025
9 | 5 | 1 | 0.113 | 0.0595 | 0.18 | 0.025
10 | 5 | 0 | 0.214 | 0.0619 | 0.32 | 0.17
11 | 5 | 0 | 0.18 | 0.0628 | 0.29 | 0.14
12 | 5 | 0 | 0.2 | 0.0707 | 0.29 | 0.11
Yearly totals/averages | 62 | 11 | 0.1319 | 0.0861 | 0.42 | 0.025
plant Bigbrown | test period | 11/8/1999 | 11/10/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Bigbrown | 1 | LIGNITE | 0.287 | 0.8295 | 27.3938 | 30.2836
Bigbrown | 2 | LIGNITE | 0.29 | 0.765 | 25.4414 | 27.4269
Bigbrown | 3 | LIGNITE | 0.287 | 0.784 | 24.8639 | 26.0531
Averages |  |  | 0.288 | 0.7928 | 25.8997 | 27.9212
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Bigbrown | 1 | PM/ESP- CS/BAGHOUSE | no bypass | 0.0794 | 0.0072 | 30.4049 | 30.0713 | 167
Bigbrown | 2 | PM/ESP- CS/BAGHOUSE | no bypass | 0.1189 | -0.1296 | 29.3042 | 31.0035 | 171
Bigbrown | 3 | PM/ESP- CS/BAGHOUSE | no bypass | 0.1024 | -0.1199 | 28.4644 | 29.192 | 164
Averages |  | PM/ESP- CS/BAGHOUSE | no bypass | 0.1002 | -0.0808 | 29.3912 | 30.0889 | 167.3
Monticello |  | 1
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- CS/BAGHOUSE
SO2 control: | NONE
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.312 | 0.0687 | 0.39 | 0.25
2 | 4 | 0 | 0.375 | 0.0351 | 0.41 | 0.34
3 | 5 | 0 | 0.354 | 0.0428 | 0.4 | 0.31
4 | 5 | 1 | 0.093 | 0.0948 | 0.26 | 0.025
5 | 6 | 4 | 0.0483 | 0.0374 | 0.11 | 0.025
6 | 5 | 2 | 0.056 | 0.0286 | 0.08 | 0.025
7 | 5 | 1 | 0.077 | 0.0387 | 0.12 | 0.025
8 | 5 | 1 | 0.093 | 0.0587 | 0.17 | 0.025
9 | 12 | 2 | 0.1133 | 0.0685 | 0.22 | 0.025
10 | 9 | 0 | 0.1478 | 0.0507 | 0.22 | 0.05
11 | 13 | 0 | 0.22 | 0.0774 | 0.43 | 0.16
12 | 14 | 0 | 0.2264 | 0.0389 | 0.28 | 0.16
Yearly totals/averages | 88 | 11 | 0.1754 | 0.111 | 0.43 | 0.025
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
2 | 1 | 0 | 0.022 | 0 | 0.022 | 0.022
4 | 3 | 0 | 0.0633 | 0.0321 | 0.1 | 0.04
5 | 3 | 0 | 0.0267 | 0.0058 | 0.03 | 0.02
6 | 3 | 0 | 0.0533 | 0.0404 | 0.1 | 0.03
7 | 4 | 0 | 0.0843 | 0.0227 | 0.118 | 0.069
8 | 5 | 0 | 0.0674 | 0.0093 | 0.081 | 0.056
9 | 3 | 0 | 0.0573 | 0.017 | 0.075 | 0.041
10 | 7 | 0 | 0.0941 | 0.014 | 0.108 | 0.069
11 | 4 | 0 | 0.0683 | 0.0083 | 0.079 | 0.06
12 | 3 | 0 | 0.1347 | 0.047 | 0.175 | 0.083
Yearly totals/averages | 36 | 0 | 0.0732 | 0.0339 | 0.175 | 0.02
plant Monticello 1-2 | test period | 2/21/2000 | 2/23/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Monticello 1-2 | 1 | LIGNITE | 0.318 | 0.8801 | 34.0488 | 33.9588
Monticello 1-2 | 2 | LIGNITE | 0.325 | 1.1365 | 44.287 | 44.1311
Monticello 1-2 | 3 | LIGNITE | 0.472 | 0.8848 | 53.9559 | 53.8169
Averages |  |  | 0.3717 | 0.9671 | 44.0972 | 43.9689
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Monticello 1-2 | 1 | PM/ESP-CS/ BAGHOUSE | no bypass | 0.37 | 0.2869 | 24.3713 | 24.3075 | 166
Monticello 1-2 | 2 | PM/ESP-CS/ BAGHOUSE | no bypass | -0.729 | -0.5152 | 67.376 | 67.1383 | 166
Monticello 1-2 | 3 | PM/ESP-CS/ BAGHOUSE | no bypass | -0.2521 | -0.4095 | 76.3583 | 76.1601 | 164
Averages |  | PM/ESP-CS/ BAGHOUSE | no bypass | -0.2037 | -0.2126 | 56.0352 | 55.8686 | 165.3
Antelope Valley Station |  | B1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 8 | 1 | 0.0599 | 0.0174 | 0.088 | 0.025
2 | 6 | 2 | 0.0447 | 0.0157 | 0.06 | 0.025
3 | 10 | 2 | 0.0655 | 0.0252 | 0.103 | 0.025
4 | 7 | 0 | 0.0603 | 0.0029 | 0.065 | 0.057
5 | 7 | 1 | 0.0637 | 0.0213 | 0.092 | 0.025
6 | 7 | 0 | 0.0623 | 0.011 | 0.083 | 0.05
7 | 7 | 1 | 0.0567 | 0.0231 | 0.102 | 0.025
8 | 7 | 0 | 0.0826 | 0.0178 | 0.107 | 0.058
9 | 7 | 0 | 0.0669 | 0.026 | 0.123 | 0.05
10 | 7 | 1 | 0.0649 | 0.0273 | 0.109 | 0.025
11 | 7 | 2 | 0.0609 | 0.0274 | 0.1 | 0.025
12 | 7 | 0 | 0.0991 | 0.068 | 0.25 | 0.059
Yearly totals/averages | 87 | 10 | 0.0658 | 0.029 | 0.25 | 0.025
plant Antelope | test period | 7/13/1999 | 7/14/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Antelope | 1 | LIGNITE | 0.06 | 0.5962 | 3.514 | 5.9264
Antelope | 2 | LIGNITE | 0.071 | 0.5318 | 3.6732 | 6.121
Antelope | 3 | LIGNITE | 0.055 | 0.6546 | 3.4617 | 5.8726
Averages |  |  | 0.062 | 0.5942 | 3.5496 | 5.9733
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Antelope | 1 | SO2/SDA | no bypass | 0.9724 | 0.9455 | 0.1629 | 0.3231 | 86
Antelope | 2 | SO2/SDA | no bypass | 0.5146 | -0.0527 | 3.3525 | 6.4451 | 82
Antelope | 3 | SO2/SDA | no bypass | 0.4853 | 0.107 | 2.722 | 5.2445 | 84
Averages |  | SO2/SDA | no bypass | 0.6574 | 0.3333 | 2.0791 | 4.0042 | 84
Stanton Station |  | 10
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.0728 | 0.0079 | 0.082 | 0.064
2 | 4 | 0 | 0.0763 | 0.0036 | 0.081 | 0.073
3 | 3 | 0 | 0.0763 | 0.0103 | 0.085 | 0.065
4 | 3 | 0 | 0.0743 | 0.0087 | 0.084 | 0.067
5 | 4 | 0 | 0.0568 | 0.007 | 0.067 | 0.051
6 | 3 | 0 | 0.051 | 0.001 | 0.052 | 0.05
7 | 3 | 0 | 0.104 | 0 | 0.104 | 0.104
8 | 3 | 0 | 0.116 | 0 | 0.116 | 0.116
9 | 3 | 0 | 0.115 | 0 | 0.115 | 0.115
10 | 3 | 0 | 0.115 | 0 | 0.115 | 0.115
11 | 3 | 0 | 0.091 | 0 | 0.091 | 0.091
12 | 4 | 0 | 0.1198 | 0.0005 | 0.12 | 0.119
Yearly totals/averages | 40 | 0 | 0.0883 | 0.0242 | 0.12 | 0.05
plant Stanton 10 | test period | 8/23/1999 | 8/28/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Stanton 10 | 1 | LIGNITE | 0.0865 | 1.1158 | 9.0876 | 6.4818
Stanton 10 | 2 | LIGNITE | 0.101 | 0.8805 | 8.5121 | 6.2435
Stanton 10 | 3 | LIGNITE | 0.063 | 1.4629 | 8.7534 | 6.3132
Averages |  |  | 0.0835 | 1.1531 | 8.7844 | 6.3462
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Stanton 10 | 1 | SO2/SDA | no bypass | 0.0191 | 0.0603 | 7.9889 | 6.0938 | 91.1
Stanton 10 | 2 | SO2/SDA | no bypass | 0.1572 | -0.003 | 8.1471 | 6.2643 | 95
Stanton 10 | 3 | SO2/SDA | no bypass | -0.3867 | -0.0131 | 8.2975 | 6.3971 | 93.9
Averages |  | SO2/SDA | no bypass | -0.0701 | 0.0147 | 8.1445 | 6.2517 | 93.3
Lewis & Clark |  | B1
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | PARTSCRUB
SO2 control: | NONE
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.123 | 0.0365 | 0.164 | 0.094
2 | 4 | 0 | 0.1043 | 0.0082 | 0.114 | 0.097
3 | 3 | 0 | 0.101 | 0.0242 | 0.123 | 0.075
4 | 3 | 0 | 0.0797 | 0.0158 | 0.097 | 0.066
7 | 1 | 0 | 0.09 | 0 | 0.09 | 0.09
8 | 7 | 0 | 0.0783 | 0.0112 | 0.095 | 0.065
9 | 7 | 0 | 0.0831 | 0.0163 | 0.112 | 0.06
10 | 5 | 0 | 0.106 | 0.0263 | 0.148 | 0.081
11 | 4 | 0 | 0.1098 | 0.0334 | 0.15 | 0.078
12 | 4 | 0 | 0.1118 | 0.0352 | 0.137 | 0.061
Yearly totals/averages | 41 | 0 | 0.0967 | 0.0253 | 0.164 | 0.06
plant Lewis | test period | 4/11/2000 | 4/11/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Lewis | 1 | LIGNITE | 0.107 | 1.8107 | 18.5815 | 21.0034
Lewis | 2 | LIGNITE | 0.121 | 1.4259 | 16.5339 | 17.0401
Lewis | 3 | LIGNITE | 0.13 | 1.0659 | 13.3349 | 12.8385
Averages |  |  | 0.1193 | 1.4342 | 16.1501 | 16.9607
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Lewis | 1 | PM/PARTSCRUB | no bypass | 0.1681 | 0.5075 | 8.5364 | 10.3457 | 60
Lewis | 2 | PM/PARTSCRUB | no bypass | 0.2541 | 0.3874 | 8.6487 | 10.4404 | 60
Lewis | 3 | PM/PARTSCRUB | no bypass | 0.1761 | 0.0881 | 10.3071 | 11.7084 | 60
Averages |  | PM/PARTSCRUB | no bypass | 0.1995 | 0.3277 | 9.1641 | 10.8315 | 60
Monticello |  | 3
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- CS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.312 | 0.0687 | 0.39 | 0.25
2 | 4 | 0 | 0.375 | 0.0351 | 0.41 | 0.34
3 | 5 | 0 | 0.354 | 0.0428 | 0.4 | 0.31
4 | 5 | 1 | 0.093 | 0.0948 | 0.26 | 0.025
5 | 6 | 4 | 0.0483 | 0.0374 | 0.11 | 0.025
6 | 5 | 2 | 0.056 | 0.0286 | 0.08 | 0.025
7 | 5 | 1 | 0.077 | 0.0387 | 0.12 | 0.025
8 | 5 | 1 | 0.093 | 0.0587 | 0.17 | 0.025
9 | 12 | 2 | 0.1133 | 0.0685 | 0.22 | 0.025
10 | 9 | 0 | 0.1478 | 0.0507 | 0.22 | 0.05
11 | 13 | 0 | 0.22 | 0.0774 | 0.43 | 0.16
12 | 14 | 0 | 0.2264 | 0.0389 | 0.28 | 0.16
Yearly totals/averages | 88 | 11 | 0.1754 | 0.111 | 0.43 | 0.025
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
2 | 1 | 0 | 0.022 | 0 | 0.022 | 0.022
4 | 3 | 0 | 0.0633 | 0.0321 | 0.1 | 0.04
5 | 3 | 0 | 0.0267 | 0.0058 | 0.03 | 0.02
6 | 3 | 0 | 0.0533 | 0.0404 | 0.1 | 0.03
7 | 4 | 0 | 0.0843 | 0.0227 | 0.118 | 0.069
8 | 5 | 0 | 0.0674 | 0.0093 | 0.081 | 0.056
9 | 3 | 0 | 0.0573 | 0.017 | 0.075 | 0.041
10 | 7 | 0 | 0.0941 | 0.014 | 0.108 | 0.069
11 | 4 | 0 | 0.0683 | 0.0083 | 0.079 | 0.06
12 | 3 | 0 | 0.1347 | 0.047 | 0.175 | 0.083
Yearly totals/averages | 36 | 0 | 0.0732 | 0.0339 | 0.175 | 0.02
plant Monticello 3 | test period | 2/23/2000 | 2/24/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Monticello 3 | 1 | LIGNITE | 0.388
Monticello 3 | 2 | LIGNITE | 0.375
Monticello 3 | 3 | LIGNITE | 0.482
Averages |  |  | 0.415
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Monticello 3 | 1 | SO2/WETSCRUB | after bypass | 0.57 | 0.2782 | 19.2221 | 23.9517 | 90
Monticello 3 | 2 | SO2/WETSCRUB | after bypass | 0.6868 | 0.5949 | 14.2345 | 13.9807 | 89
Monticello 3 | 3 | SO2/WETSCRUB | after bypass | 0.697 | 0.5541 | 16.71 | 17.0373 | 89
Averages |  | SO2/WETSCRUB | after bypass | 0.6513 | 0.4757 | 16.7222 | 18.3232 | 89.3
Limestone |  | LIM1
Boiler/NOx type: | CONV/PC/NOX/WET
Particulate control: | ESP- CS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.1733 | 0.0208 | 0.19 | 0.15
2 | 3 | 0 | 0.1167 | 0.0208 | 0.14 | 0.1
3 | 3 | 0 | 0.13 | 0.0361 | 0.17 | 0.1
4 | 3 | 2 | 0.05 | 0.0433 | 0.1 | 0.025
5 | 3 | 0 | 0.14 | 0.02 | 0.16 | 0.12
6 | 3 | 0 | 0.1433 | 0.0231 | 0.17 | 0.13
7 | 3 | 1 | 0.0783 | 0.0525 | 0.13 | 0.025
8 | 3 | 1 | 0.0717 | 0.0475 | 0.12 | 0.025
9 | 3 | 0 | 0.2333 | 0.0929 | 0.34 | 0.17
10 | 6 | 0 | 0.155 | 0.0464 | 0.2 | 0.08
11 | 6 | 0 | 0.1817 | 0.0496 | 0.26 | 0.13
12 | 6 | 0 | 0.19 | 0.0335 | 0.22 | 0.14
Yearly totals/averages | 45 | 4 | 0.146 | 0.0626 | 0.34 | 0.025
plant Limestone | test period | 11/16/1999 | 11/16/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Limestone | 1 | LIGNITE | 0.121
Limestone | 2 | LIGNITE | 0.171
Limestone | 3 | LIGNITE | 0.125
Averages |  |  | 0.139
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Limestone | 1 | SO2/WETSCRUB | after control | -0.2211 | 0.494 | 14.177 | 13.4356 | 59
Limestone | 2 | SO2/WETSCRUB | after control | 0.0897 | 0.4759 | 14.5472 | 14.192 | 61
Limestone | 3 | SO2/WETSCRUB | after control | -0.0937 | 0.5607 | 12.9286 | 13.356 | 59
Averages |  | SO2/WETSCRUB | after control | -0.075 | 0.5102 | 13.8843 | 13.6612 | 59.7
Bay Front Plant Generating |  | 5
Boiler/NOx type: | CYCLONE/NONOX/WET
Particulate control: | MECH
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 2 | 0.01 | 0.0087 | 0.02 | 0.005
2 | 3 | 0 | 0.0233 | 0.0058 | 0.03 | 0.02
3 | 3 | 0 | 0.0267 | 0.0153 | 0.04 | 0.01
4 | 8 | 0 | 0.0438 | 0.0338 | 0.1 | 0.01
5 | 9 | 0 | 0.0156 | 0.0133 | 0.05 | 0.01
6 | 3 | 0 | 0.0433 | 0.0577 | 0.11 | 0.01
7 | 6 | 0 | 0.0383 | 0.0264 | 0.09 | 0.02
8 | 6 | 0 | 0.0233 | 0.0082 | 0.04 | 0.02
9 | 4 | 0 | 0.0425 | 0.0189 | 0.07 | 0.03
10 | 2 | 0 | 0.015 | 0.0071 | 0.02 | 0.01
11 | 2 | 0 | 0.025 | 0.0071 | 0.03 | 0.02
12 | 4 | 0 | 0.0275 | 0.005 | 0.03 | 0.02
Yearly totals/averages | 53 | 2 | 0.0289 | 0.0236 | 0.11 | 0.005
Fuel number2 | PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
8 | 4 | 1 | 0.0087 | 0.0025 | 0.01 | 0.005
Yearly totals/averages | 4 | 1 | 0.0087 | 0.0025 | 0.01 | 0.005
plant Bayfront | test period | 10/26/1999 | 10/27/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Bayfront | 1 | BITUMINOUS | 0.06 | 2.5045 | 11.7488 | 2.6624
Bayfront | 2 | BITUMINOUS | 0.06 | 2.1611 | 10.2623 | 2.6492
Bayfront | 3 | BITUMINOUS | 0.06 | 1.4005 | 6.6706 | 1.8664
Averages |  |  | 0.06 | 2.022 | 9.5606 | 2.3927
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Bayfront | 1 | PM/MECH | no bypass | -0.0044 | 0.0034 | 4.7119 | 2.654 | 135
Bayfront | 2 | PM/MECH | no bypass | -0.6934 | -0.4654 | 8.0413 | 3.8839 | 132
Bayfront | 3 | PM/MECH | no bypass | -0.7234 | -1.25 | 8.2088 | 4.1997 | 134
Averages |  | PM/MECH | no bypass | -0.4737 | -0.5707 | 6.9873 | 3.5792 | 133.7
Bailly |  | 7
Boiler/NOx type: | CYCLONE/NONOX/ WET
Particulate control: | ESP- CS
SO2 control: | WETSCRUB
Test on last control unit
Fuel number1 | BITUMINOUS - LOW SULFUR
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 1 | 0 | 0.022 | 0 | 0.022 | 0.022
2 | 1 | 0 | 0.018 | 0 | 0.018 | 0.018
3 | 2 | 0 | 0.022 | 0.0014 | 0.023 | 0.021
4 | 1 | 0 | 0.017 | 0 | 0.017 | 0.017
5 | 1 | 0 | 0.018 | 0 | 0.018 | 0.018
6 | 3 | 0 | 0.0187 | 0.0055 | 0.025 | 0.015
7 | 1 | 0 | 0.021 | 0 | 0.021 | 0.021
8 | 3 | 0 | 0.0223 | 0.0032 | 0.026 | 0.02
9 | 1 | 0 | 0.044 | 0 | 0.044 | 0.044
10 | 2 | 0 | 0.045 | 0 | 0.045 | 0.045
11 | 2 | 0 | 0.0315 | 0.0021 | 0.033 | 0.03
12 | 2 | 0 | 0.0235 | 0.0078 | 0.029 | 0.018
Yearly totals/averages | 20 | 0 | 0.0254 | 0.0096 | 0.045 | 0.015
Fuel number2 | BITUMINOUS - HIGH SULFUR
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 5 | 0 | 0.0554 | 0.0121 | 0.077 | 0.05
2 | 8 | 0 | 0.0638 | 0.0233 | 0.12 | 0.05
3 | 10 | 0 | 0.066 | 0.0272 | 0.12 | 0.04
4 | 1 | 0 | 0.07 | 0 | 0.07 | 0.07
5 | 8 | 0 | 0.0525 | 0.0046 | 0.06 | 0.05
6 | 8 | 0 | 0.06 | 0.0076 | 0.07 | 0.05
7 | 5 | 0 | 0.064 | 0.0152 | 0.09 | 0.05
8 | 7 | 0 | 0.0543 | 0.0053 | 0.06 | 0.05
9 | 7 | 0 | 0.0643 | 0.0127 | 0.09 | 0.05
10 | 10 | 0 | 0.058 | 0.0092 | 0.08 | 0.05
11 | 10 | 0 | 0.059 | 0.0088 | 0.08 | 0.05
12 | 8 | 0 | 0.06 | 0.0131 | 0.09 | 0.05
Yearly totals/averages | 87 | 0 | 0.06 | 0.0144 | 0.12 | 0.04
Fuel number3 | PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
3 | 8 | 0 | 0.0688 | 0.0259 | 0.1 | 0.05
4 | 12 | 0 | 0.075 | 0.0151 | 0.1 | 0.06
6 | 3 | 0 | 0.09 | 0 | 0.09 | 0.09
7 | 2 | 0 | 0.08 | 0 | 0.08 | 0.08
8 | 10 | 0 | 0.07 | 0.0105 | 0.08 | 0.06
Yearly totals/averages | 35 | 0 | 0.0737 | 0.0166 | 0.1 | 0.05
Fuel number4 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0967 | 0.0321 | 0.12 | 0.06
2 | 3 | 0 | 0.1233 | 0.0513 | 0.18 | 0.08
4 | 3 | 0 | 0.1233 | 0.0115 | 0.13 | 0.11
Yearly totals/averages | 9 | 0 | 0.1144 | 0.0336 | 0.18 | 0.06
plant Bailly | test period | 12/9/1999 | 12/10/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Bailly | 1 | BITUMINOUS | 0.07 | 0 | 0 | 0
Bailly | 2 | BITUMINOUS | 0.08 | 0 | 0 | 0
Bailly | 3 | BITUMINOUS | 0.06 | 0 | 0 | 0
Averages |  |  | 0.07
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Bailly | 1 | SO2/WETSCRUB | no bypass | 0.581 | 0.4883 | 2.305 | 2.31 | 54.5
Bailly | 2 | SO2/WETSCRUB | no bypass | 0.6658 | 0.4639 | 2.0991 | 2.1068 | 53.9
Bailly | 3 | SO2/WETSCRUB | no bypass | 0.5115 | 0.4862 | 2.2874 | 2.2749 | 54.2
Averages |  | SO2/WETSCRUB | no bypass | 0.5861 | 0.4795 | 2.2305 | 2.2306 | 54.2
Coyote |  | 1
Boiler/NOx type: | CYCLONE/NONOX/WET
Particulate control: | BAGHOUSE
SO2 control: | SDA
Test on last control unit
Fuel number1 | LIGNITE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.213 | 0.0603 | 0.263 | 0.146
2 | 3 | 0 | 0.141 | 0.0278 | 0.166 | 0.111
3 | 3 | 0 | 0.1337 | 0.0122 | 0.147 | 0.123
4 | 3 | 0 | 0.1277 | 0.0278 | 0.153 | 0.098
5 | 3 | 0 | 0.1397 | 0.0332 | 0.175 | 0.109
6 | 3 | 0 | 0.129 | 0.0229 | 0.154 | 0.109
7 | 3 | 0 | 0.1223 | 0.025 | 0.148 | 0.098
8 | 3 | 0 | 0.1177 | 0.0368 | 0.157 | 0.084
9 | 3 | 0 | 0.0983 | 0.0264 | 0.127 | 0.075
10 | 3 | 0 | 0.1017 | 0.005 | 0.107 | 0.097
11 | 3 | 0 | 0.1613 | 0.0477 | 0.2 | 0.108
12 | 3 | 0 | 0.1323 | 0.0329 | 0.162 | 0.097
Yearly totals/averages | 36 | 0 | 0.1348 | 0.0399 | 0.263 | 0.075
plant Coyote | test period | 9/28/1999 | 9/29/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Coyote | 1 | LIGNITE | 0.088 | 1.522 | 12.088 | 11.494
Coyote | 2 | LIGNITE | 0.15 | 0.9732 | 13.677 | 12.9811
Coyote | 3 | LIGNITE | 0.094 | 1.7267 | 14.8855 | 14.1324
Averages |  |  | 0.1107 | 1.4073 | 13.5502 | 12.8692
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Coyote | 1 | SO2/SDA | no bypass | -0.172 | 0.1199 | 9.3084 | 10.1268 | 109
Coyote | 2 | SO2/SDA | no bypass | 0.9762 | 0.9725 | 0.3349 | 0.3576 | 96
Coyote | 3 | SO2/SDA | no bypass | -0.4409 | 0.0548 | 12.4216 | 13.3726 | 102
Averages |  | SO2/SDA | no bypass | 0.1211 | 0.3824 | 7.355 | 7.9523 | 102.3
AES Hawaii, Inc. |  | A
Boiler/NOx type: | FBC/SNCR
Particulate control: | BAGHOUSE
SO2 control: | FBC
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 1 | 1 | 0.05 | 0 | 0.05 | 0.05
2 | 1 | 1 | 0.05 | 0 | 0.05 | 0.05
3 | 1 | 1 | 0.05 | 0 | 0.05 | 0.05
4 | 4 | 0 | 0.025 | 0.0058 | 0.03 | 0.02
5 | 5 | 0 | 0.024 | 0.0055 | 0.03 | 0.02
6 | 5 | 0 | 0.028 | 0.0045 | 0.03 | 0.02
7 | 3 | 0 | 0.0267 | 0.0058 | 0.03 | 0.02
8 | 4 | 0 | 0.025 | 0.0058 | 0.03 | 0.02
9 | 5 | 0 | 0.03 | 0.0071 | 0.04 | 0.02
10 | 4 | 0 | 0.0275 | 0.005 | 0.03 | 0.02
11 | 4 | 0 | 0.0225 | 0.005 | 0.03 | 0.02
12 | 5 | 0 | 0.026 | 0.0055 | 0.03 | 0.02
Yearly totals/averages | 42 | 3 | 0.0279 | 0.0081 | 0.05 | 0.02
Fuel number2 | TIRES
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
9 | 3 | 0 | 0.02 | 0 | 0.02 | 0.02
10 | 3 | 0 | 0.02 | 0 | 0.02 | 0.02
11 | 3 | 0 | 0.0233 | 0.0058 | 0.03 | 0.02
Yearly totals/averages | 9 | 0 | 0.0211 | 0.0033 | 0.03 | 0.02
plant AES Hawaii | test period | 1/11/2000 | 1/12/2000
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
AES Hawaii | 1 | SUBBITUMINOUS | 0.03 | 0.4244 | 0.9991 | 1.0032
AES Hawaii | 2 | SUBBITUMINOUS | 0.03 | 0.5597 | 1.3177 | 1.3037
AES Hawaii | 3 | SUBBITUMINOUS | 0.02 | 0.669 | 1.0599 | 0.6493
Averages |  |  | 0.0267 | 0.551 | 1.1256 | 0.9854
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
AES Hawaii | 1 | PM/BAGHOUSE | no bypass | 0.8231 | 0.567 | 0.4165 | 0.4344 | 133.7
AES Hawaii | 2 | PM/BAGHOUSE | no bypass | 0.7509 | 0.5374 | 0.5864 | 0.6031 | 133.2
AES Hawaii | 3 | PM/BAGHOUSE | no bypass | 0.79 | 0.4712 | 0.3328 | 0.3443 | 133.7
Averages |  | PM/BAGHOUSE | no bypass | 0.788 | 0.5252 | 0.4452 | 0.4606 | 133.5
Meramec |  | 4
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | ESP- CS
SO2 control: | NONE
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 1 | 0.0538 | 0.0358 | 0.076 | 0.0125
2 | 3 | 2 | 0.0267 | 0.0245 | 0.055 | 0.0125
3 | 2 | 2 | 0.0125 | 0 | 0.0125 | 0.0125
4 | 4 | 0 | 0.0573 | 0.0074 | 0.065 | 0.048
5 | 3 | 0 | 0.0667 | 0.0047 | 0.072 | 0.063
6 | 3 | 0 | 0.076 | 0.0122 | 0.09 | 0.068
7 | 3 | 2 | 0.032 | 0.0338 | 0.071 | 0.0125
8 | 3 | 0 | 0.059 | 0.0135 | 0.072 | 0.045
9 | 3 | 1 | 0.0472 | 0.0302 | 0.068 | 0.0125
10 | 3 | 0 | 0.0617 | 0.0032 | 0.064 | 0.058
11 | 4 | 0 | 0.0695 | 0.0137 | 0.084 | 0.051
12 | 3 | 0 | 0.0647 | 0.004 | 0.069 | 0.061
Yearly totals/averages | 37 | 8 | 0.0539 | 0.0237 | 0.09 | 0.0125
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0437 | 0.0057 | 0.05 | 0.039
2 | 3 | 0 | 0.043 | 0.0101 | 0.052 | 0.032
3 | 3 | 0 | 0.0787 | 0.011 | 0.086 | 0.066
4 | 6 | 0 | 0.079 | 0.0091 | 0.091 | 0.067
5 | 5 | 0 | 0.0914 | 0.0086 | 0.105 | 0.084
6 | 6 | 0 | 0.1005 | 0.0141 | 0.123 | 0.084
7 | 6 | 0 | 0.0947 | 0.0267 | 0.121 | 0.049
8 | 6 | 0 | 0.0842 | 0.0137 | 0.098 | 0.066
9 | 6 | 0 | 0.108 | 0.015 | 0.135 | 0.094
10 | 3 | 0 | 0.0927 | 0.0006 | 0.093 | 0.092
11 | 6 | 0 | 0.1197 | 0.0593 | 0.181 | 0.064
Yearly totals/averages | 53 | 0 | 0.0896 | 0.0303 | 0.181 | 0.032
plant Meramec | test period | 7/27/1999 | 7/29/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Meramec | 1 | SUBBITUMINOUS/ BITUMINOUS | 0.085 | 0.9967 | 6.3922 | 5.9925
Meramec | 2 | SUBBITUMINOUS/ BITUMINOUS | 0.12 | 0.9133 | 8.1185 | 8.0058
Meramec | 3 | SUBBITUMINOUS/ BITUMINOUS | 0.068 | 1.1773 | 5.9678 | 5.8824
Averages |  |  | 0.091 | 1.0291 | 6.8262 | 6.6269
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Meramec | 1 | PM/ESP- CS | no bypass | 0.8153 | 0.8127 | 1.1845 | 1.1228 | 162
Meramec | 2 | PM/ESP- CS | no bypass | 0.7 | 0.6997 | 2.6666 | 2.4046 | 163
Meramec | 3 | PM/ESP- CS | no bypass | 0.6195 | 0.7196 | 1.9289 | 1.649 | 150
Averages |  | PM/ESP- CS | no bypass | 0.7116 | 0.744 | 1.9267 | 1.7255 | 158.3
St Clair Power Plant |  | 4
Boiler/NOx type: | CONV/PC/NONOX/DRY
Particulate control: | ESP- CS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0467 | 0.0153 | 0.06 | 0.03
2 | 10 | 0 | 0.035 | 0.0118 | 0.05 | 0.02
3 | 13 | 0 | 0.03 | 0.01 | 0.05 | 0.02
4 | 10 | 0 | 0.034 | 0.0107 | 0.05 | 0.02
5 | 10 | 0 | 0.029 | 0.0099 | 0.05 | 0.02
6 | 9 | 0 | 0.0289 | 0.0093 | 0.04 | 0.02
7 | 8 | 0 | 0.0363 | 0.0141 | 0.06 | 0.02
8 | 4 | 2 | 0.02 | 0.0141 | 0.04 | 0.01
9 | 4 | 0 | 0.025 | 0.0058 | 0.03 | 0.02
10 | 6 | 0 | 0.0433 | 0.0121 | 0.05 | 0.02
11 | 6 | 0 | 0.0567 | 0.0163 | 0.08 | 0.04
12 | 4 | 0 | 0.0375 | 0.005 | 0.04 | 0.03
Yearly totals/averages | 87 | 2 | 0.0344 | 0.0135 | 0.08 | 0.01
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 3 | 0 | 0.0933 | 0.0058 | 0.1 | 0.09
2 | 3 | 0 | 0.0967 | 0.0058 | 0.1 | 0.09
3 | 3 | 0 | 0.0567 | 0.0058 | 0.06 | 0.05
4 | 3 | 0 | 0.0367 | 0.0208 | 0.06 | 0.02
5 | 3 | 0 | 0.0733 | 0.0306 | 0.1 | 0.04
6 | 3 | 0 | 0.0937 | 0.0085 | 0.1 | 0.084
7 | 2 | 0 | 0.074 | 0.0014 | 0.075 | 0.073
8 | 3 | 0 | 0.0813 | 0.0046 | 0.084 | 0.076
9 | 3 | 0 | 0.091 | 0 | 0.091 | 0.091
10 | 3 | 0 | 0.097 | 0.0161 | 0.114 | 0.082
11 | 3 | 0 | 0.059 | 0.032 | 0.096 | 0.04
12 | 3 | 0 | 0.1933 | 0.0306 | 0.22 | 0.16
Yearly totals/averages | 35 | 0 | 0.0875 | 0.0406 | 0.22 | 0.02
plant St Clair | test period | 11/2/1999 | 11/4/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
St Clair | 1 | SUBBITUMINOUS/ BITUMINOUS | 0.06 | 0.9204 | 4.4426 | 4.8786
St Clair | 2 | SUBBITUMINOUS/ BITUMINOUS | 0.055 | 0.9812 | 4.2594 | 4.5919
St Clair | 3 | SUBBITUMINOUS/ BITUMINOUS | 0.069 | 0.9102 | 4.9923 | 5.1752
Averages |  |  | 0.0613 | 0.9373 | 4.5648 | 4.8819
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
St Clair | 1 | PM/ESP- CS | no bypass | 0.4676 | 0.3395 | 2.57 | 3.2228 | 137
St Clair | 2 | PM/ESP- CS | no bypass | 0.3066 | 0.1908 | 3.01 | 3.7185 | 142
St Clair | 3 | PM/ESP- CS | no bypass | 0.3204 | 0.0765 | 3.7274 | 4.7815 | 141
Averages |  | PM/ESP- CS | no bypass | 0.3649 | 0.2023 | 3.1025 | 3.9076 | 140
Clifty Creek |  | 6
Boiler/NOx type: | CONV/PC/NOX/WET
Particulate control: | ESP- HS
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 6 | 0 | 0.0703 | 0.0121 | 0.084 | 0.054
2 | 6 | 0 | 0.0707 | 0.0135 | 0.094 | 0.059
3 | 7 | 0 | 0.0706 | 0.0135 | 0.09 | 0.051
4 | 6 | 0 | 0.068 | 0.0063 | 0.08 | 0.062
5 | 10 | 0 | 0.0713 | 0.0172 | 0.108 | 0.045
6 | 11 | 0 | 0.0764 | 0.0223 | 0.131 | 0.045
7 | 12 | 0 | 0.0763 | 0.0128 | 0.102 | 0.056
8 | 9 | 0 | 0.0779 | 0.0239 | 0.134 | 0.052
9 | 9 | 0 | 0.0637 | 0.0145 | 0.091 | 0.045
10 | 9 | 0 | 0.0692 | 0.0111 | 0.089 | 0.053
11 | 8 | 0 | 0.064 | 0.0184 | 0.09 | 0.037
12 | 7 | 0 | 0.0684 | 0.0099 | 0.085 | 0.057
Yearly totals/averages | 100 | 0 | 0.0711 | 0.0158 | 0.134 | 0.037
Fuel number2 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 10 | 0 | 0.1167 | 0.0699 | 0.235 | 0.068
2 | 9 | 0 | 0.1467 | 0.0933 | 0.332 | 0.079
3 | 9 | 0 | 0.1544 | 0.1242 | 0.431 | 0.067
4 | 11 | 0 | 0.1425 | 0.1185 | 0.413 | 0.069
5 | 9 | 0 | 0.2124 | 0.2074 | 0.562 | 0.077
6 | 9 | 0 | 0.1516 | 0.1208 | 0.414 | 0.07
7 | 9 | 0 | 0.1467 | 0.1078 | 0.339 | 0.073
8 | 9 | 0 | 0.1369 | 0.0923 | 0.281 | 0.064
9 | 7 | 0 | 0.1083 | 0.0704 | 0.266 | 0.071
10 | 9 | 0 | 0.1444 | 0.0985 | 0.315 | 0.075
11 | 9 | 0 | 0.1683 | 0.1507 | 0.453 | 0.067
12 | 9 | 0 | 0.1224 | 0.0657 | 0.242 | 0.073
Yearly totals/averages | 109 | 0 | 0.1463 | 0.1136 | 0.562 | 0.064
plant Clifty | test period | 11/2/1999 | 11/3/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Clifty | 1 | SUBBITUMINOUS/ BITUMINOUS | 0.08 | 1.7353 | 11.1114 | 9.9838
Clifty | 2 | SUBBITUMINOUS/ BITUMINOUS | 0.08 | 1.9233 | 12.2328 | 10.5711
Clifty | 3 | SUBBITUMINOUS/ BITUMINOUS | 0.08 | 1.8315 | 11.599 | 10.6701
Averages |  |  | 0.08 | 1.83 | 11.6477 | 10.4083
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Clifty | 1 | PM/ESP- HS | no bypass | -0.3002 | 0.3558 | 8.3255 | 6.4365 | 170
Clifty | 2 | PM/ESP- HS | no bypass | -0.368 | 0.2951 | 8.7012 | 7.4575 | 166
Clifty | 3 | PM/ESP- HS | no bypass | -0.2465 | 0.3699 | 7.8945 | 6.7294 | 166
Averages |  | PM/ESP- HS | no bypass | -0.3049 | 0.3403 | 8.3071 | 6.8745 | 167.3
Valley |  | 2
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | NONE
Test on last control unit
Fuel number1 | BITUMINOUS PETROLEUM COKE
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 4 | 0 | 0.0625 | 0.0066 | 0.07 | 0.056
2 | 4 | 0 | 0.0825 | 0.0128 | 0.097 | 0.069
3 | 5 | 0 | 0.092 | 0.0177 | 0.11 | 0.072
4 | 4 | 0 | 0.073 | 0.0249 | 0.088 | 0.036
5 | 4 | 0 | 0.044 | 0.0126 | 0.061 | 0.031
6 | 5 | 0 | 0.029 | 0.0113 | 0.04 | 0.016
7 | 4 | 0 | 0.041 | 0.0335 | 0.09 | 0.016
8 | 3 | 0 | 0.032 | 0.0259 | 0.061 | 0.011
9 | 4 | 0 | 0.0295 | 0.0079 | 0.037 | 0.02
10 | 3 | 0 | 0.029 | 0.0161 | 0.047 | 0.016
11 | 4 | 0 | 0.0198 | 0.0039 | 0.024 | 0.016
12 | 4 | 0 | 0.0203 | 0.0057 | 0.028 | 0.016
Yearly totals/averages | 48 | 0 | 0.0475 | 0.029 | 0.11 | 0.011
plant Valley | test period | 11/30/1999 | 11/30/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Valley | 1 | BITUMINOUS/ PETCOKE | 0.0092 | 2.8181 | 1.9467 | 1.9303
Valley | 2 | BITUMINOUS/ PETCOKE | 0.013 | 1.498 | 1.4676 | 1.4275
Valley | 3 | BITUMINOUS/ PETCOKE | 0.015 | 1.2685 | 1.4141 | 1.3819
Averages |  |  | 0.0124 | 1.8615 | 1.6095 | 1.5799
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Valley | 1 | PM/BAGHOUSE | no bypass | -1.8306 | 0.0567 | 1.9553 | 1.8211 | 157.8
Valley | 2 | PM/BAGHOUSE | no bypass | -0.6438 | -0.007 | 1.6105 | 1.4375 | 158.7
Valley | 3 | PM/BAGHOUSE | no bypass | -0.7836 | -0.2521 | 1.9883 | 1.7305 | 158.8
Averages |  | PM/BAGHOUSE | no bypass | -1.086 | -0.0675 | 1.8514 | 1.663 | 158.4
Shawnee Fossil Plant |  | 3
Boiler/NOx type: | CONV/PC/NOX/DRY
Particulate control: | BAGHOUSE
SO2 control: | COMP COAL
Test on last control unit
Fuel number1 | BITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 7 | 1 | 0.0509 | 0.0341 | 0.1 | 0.0064
2 | 9 | 0 | 0.0622 | 0.0377 | 0.12 | 0.02
3 | 7 | 0 | 0.0729 | 0.075 | 0.23 | 0.01
4 | 17 | 1 | 0.0516 | 0.0281 | 0.1031 | 0.0064
5 | 18 | 1 | 0.0585 | 0.031 | 0.1232 | 0.0064
6 | 10 | 3 | 0.0657 | 0.0633 | 0.2106 | 0.0064
7 | 9 | 0 | 0.0463 | 0.0474 | 0.1361 | 0.0131
8 | 10 | 0 | 0.0555 | 0.0438 | 0.111 | 0.0158
9 | 6 | 1 | 0.0157 | 0.0061 | 0.0241 | 0.0064
10 | 7 | 0 | 0.0188 | 0.0055 | 0.0295 | 0.0134
11 | 3 | 0 | 0.0148 | 0.0014 | 0.0162 | 0.0134
12 | 9 | 0 | 0.0154 | 0.0022 | 0.0188 | 0.0133
Yearly totals/averages | 112 | 7 | 0.0482 | 0.0414 | 0.23 | 0.0064
Fuel number2 | SUBBITUMINOUS
MONTH | number measured | number nondetects | average Hg in fuel (ppmw) | standard deviation (ppmw) | highest (ppmw) | lowest (ppmw)
1 | 1 | 0 | 0.1 | 0 | 0.1 | 0.1
2 | 2 | 0 | 0.095 | 0.0071 | 0.1 | 0.09
3 | 1 | 0 | 0.09 | 0 | 0.09 | 0.09
4 | 1 | 0 | 0.1288 | 0 | 0.1288 | 0.1288
6 | 1 | 0 | 0.162 | 0 | 0.162 | 0.162
7 | 4 | 0 | 0.1104 | 0.0473 | 0.1793 | 0.0732
8 | 2 | 0 | 0.1035 | 0.0177 | 0.116 | 0.0909
12 | 2 | 0 | 0.085 | 0.019 | 0.0984 | 0.0715
Yearly totals/averages | 14 | 0 | 0.1064 | 0.0311 | 0.1793 | 0.0715
plant Shawnee | test period | 10/27/1999 | 10/29/1999
plant name | run.no | test fuel | Hg in test coal (ppm) | Hg outlet/coal | lb/TBtu out furnace | F factor lb/TBtu out furnace
Shawnee | 1 | BITUMINOUS/ SUBBITUMINOUS | 0.022 | 1.868 | 3.1901 | 3.2096
Shawnee | 2 | BITUMINOUS/ SUBBITUMINOUS | 0.039 | 1.0841 | 3.3255 | 3.3461
Shawnee | 3 | BITUMINOUS/ SUBBITUMINOUS | 0.024 | 1.7597 | 3.3054 | 3.3662
Averages |  |  | 0.0283 | 1.5706 | 3.2737 | 3.3073
plant name | run.no | Control tested | location | fr.remove coal-stack | fremove control | lb/TBtu out control | F factor lb/TBtu out control | stack temp C
Shawnee | 1 | PM/BAGHOUSE | no bypass | 0.3516 | 0.653 | 1.1073 | 1.1141 | 152
Shawnee | 2 | PM/BAGHOUSE | no bypass | 0.6543 | 0.6813 | 1.0605 | 1.067 | 149
Shawnee | 3 | PM/BAGHOUSE | no bypass | 0.4862 | 0.7116 | 0.9651 | 0.971 | 153
Averages |  | PM/BAGHOUSE | no bypass | 0.4974 | 0.682 | 1.0443 | 1.0507 | 151.3
Note on E2016: the inlet flow rate was not reported.
Note on D29: A value of 0.1 with nondetect was reported for the test by the test contractor. A value of 0.1 detect is used here based upon a more sensitive analysis of the coal by the plant during the test month.