## list
source
cond
emiss
feed
df c1

## source
Source Description
Phase II ID No. | 911
EPA ID No. | OHD005108477
Facility Name | Sunoco Inc. (R&M) Haverhill Plant
Facility Location
City | Haverhill
State | OH
Unit ID Name/No. | Unit 2001-UA
Other Sister Facilities | Units UB, UC (2 other identical units)
Number of Sister Facilities | 2
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler. Riley/Union Iron Works, Model MH, 150,000 lb/hr steam, 183 MMBtu/hr
Capacity (MMBtu/hr) | 183
Soot Blowing | Yes, 2 min per 8 hrs
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics | NA
Hazardous Wastes | Liq
Haz Waste Description | Liq organic wastes (benzene, waste lubricating oil, AMS distillation bottoms, phenol waste water, aniline distillation) including codes D001, D018, D035, K022
Supplemental Fuel | Natural gas, oil
fuel oil
Stack Characteristics
Diameter (ft) | 4.9
Height (ft) | 50
Gas Velocity (ft/sec) | 59.7113
Gas Temperature (°F) | 509
Permitting Status | Ajusted tier I for metals and chlorine
HWC Burn Status (Date if Terminated)

## cond
Cond Description
911C1
Report Name/Date | Revised Certification of Compliance, November 1996
Report Prepare | Radian International LLC
Testing Firm | ENSR Consulting and Engineering
Testing Dates | 1995-05-16
Cond Dates | 1995-05-01
Condition Descr | CoC; HHC waste fuel
Content | PM, CO, HCl/Cl2, Cr/Cr+6
911C2
Report Name/Date | Revised Certification of Compliance, November 1996
Report Prepare | Radian International LLC
Testing Firm | ENSR Consulting and Engineering
Testing Dates | May 17-18, 1995
Cond Dates | 1995-05-01
Condition Descr | CoC; HHC waste fuel
Content | PM, CO, HCl/Cl2, Cr/Cr+6
911C3
Report Name/Date | Revised Certification of Compliance, November 1996
Report Prepare | Radian International LLC
Testing Firm | ENSR Consulting and Engineering
Testing Dates | May 18-19, 1995
Cond Dates | 1995-05-01
Condition Descr | CoC; HHC waste fuel
Content | PM, CO, HCl/Cl2, Cr/Cr+6
911C4
Report Name/Date | Revised Certification of Compliance, November 1996
Report Prepare | Radian International LLC
Testing Firm | ENSR Consulting and Engineering
Testing Dates | May 19-20, 1995
Cond Dates | 1995-05-01
Condition Descr | CoC; light HC waste
Content | PM, CO, HCl/Cl2, Cr/Cr+6
911C5
Report Name/Date | Revised Certification of Compliance, January 1999
Report Prepare | Radian International LLC
Testing Firm | ENSR Consulting and Engineering
Testing Dates | 1998-07-08
Cond Dates | 1998-07-01
Condition Descr | CoC; LHC waste fuel
Content | PM, CO
911C6
Report Name/Date | Revised Certification of Compliance, January 1999
Report Prepare | Radian International LLC
Testing Firm | ENSR Consulting and Engineering
Testing Dates | 1998-10-06
Cond Dates | 1998-10-01
Condition Descr | CoC; HHC waste fuel
Content | CO
911C7
Report Name/Date | Revised Certification of Compliance, January 1999
Report Prepare | Radian International LLC
Testing Firm | ENSR Consulting and Engineering
Testing Dates | 1998-10-07
Cond Dates | 1998-10-01
Condition Descr | CoC; HHC waste fuel
Content | PM, CO
911C8
Report Name/Date | Trial Burn Report, February 2002
Report Prepare | URS Corp.
Testing Firm | URS Corp.
Testing Dates | 11/6-7/2001
Cond Dates | 2001-11-01
Condition Descr | CoC; HHC waste fuel low range
Content | CO, DRE
911C9
Report Name/Date | Trial Burn Report, February 2002
Report Prepare | URS Corp.
Testing Firm | URS Corp.
Testing Dates | 11/10-11/2001
Cond Dates | 2001-11-01
Condition Descr | CoC; HHC waste fuel high range
Content | CO, DRE
911C10
Report Name/Date | Trial Burn Report, February 2002
Report Prepare | URS Corp.
Testing Firm | URS Corp.
Testing Dates | 11/5-6/2001
Cond Dates | 2001-11-01
Condition Descr | CoC; LHC waste fuel high range
Content | Metals, Cr+6, CO, DRE
911C11
Report Name/Date | Trial Burn Report, February 2002
Report Prepare | URS Corp.
Testing Firm | URS Corp.
Testing Dates | 11/9-12/2001
Cond Dates | 2001-11-01
Condition Descr | CoC; HHC waste fuel high range
Content | PM, HCl/Cl2, Metals, Cr+6, CO, DRE
911C12
Report Name/Date | Trial Burn Report, February 2002
Report Prepare | URS Corp.
Testing Firm | URS Corp.
Testing Dates | 11/13-14/2001
Cond Dates | 2001-11-01
Condition Descr | CoC; HHC waste fuel high range
Content | CO
911C13
Report Name/Date | Trial Burn Report, February 2002
Report Prepare | URS Corp.
Testing Firm | URS Corp.
Testing Dates | 11/14-16/2001
Cond Dates | 2001-11-01
Condition Descr | CoC; HHC waste fuel low range
Content | CO, D/F, PCB, PAH, VOC/SVOC, Aldehydes/ketones

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
Sootblow
1 | 911C1 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0062 |  | 0.0182 |  | 0.0065 |  | 0.0083
| CO (RA) | E1 | ppmv | y |  | 24.8 |  | 23.1 |  | 24.6 |  | 24.1667
| CO (MHRA) | E1 | ppmv | y |  | 29.7 |  | 29.5 |  | 29.8 |  | 29.6667
| HCl |  | g/hr | n | nd | 24.49 | nd | 22.65 | nd | 23.88
| Cl2 |  | g/hr | n | nd | 24.77 | nd | 19.15 | nd | 21.81
| Chromium (Hex) |  | g/hr | n |  | 1.91 |  | 5.09 |  | 1.21 |  | 2.15
| Chromium |  | g/hr | n |  | 4.08 |  | 8.36 |  | 3.98 |  | 4.75
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 32257 |  | 32410 |  | 32305 |  | 32324
| O2 |  | % |  |  | 3.8 |  | 4.17 |  | 3.3 |  | 3.7567
| Moisture |  | % |  |  | 16.3 |  | 16.6 |  | 16.6 |  | 16.5
| Temperature |  | °F |  |  | 506 |  | 504 |  | 504 |  | 504.6667
| Sampling Train | Cr (+6) | E2
| Stack Gas Flowrate |  | dscfm |  |  | 33655 |  | 33480 |  | 33801 |  | 33645.3333
| O2 |  | % |  |  | 3.8 |  | 4.17 |  | 3.3 |  | 3.7567
| Moisture |  | % |  |  | 13.7 |  | 14.4 |  | 13.1 |  | 13.7333
| Temperature |  | °F |  |  | 507 |  | 502 |  | 505 |  | 504.6667
| Sampling Train | Cr | E3
| Stack Gas Flowrate |  | dscfm |  |  | 33282 |  | 32861 |  | 33065 |  | 33069.3333
| O2 |  | % |  |  | 3.8 |  | 4.17 |  | 3.3 |  | 3.7567
| Moisture |  | % |  |  | 16.7 |  | 16.7 |  | 16.8 |  | 16.7333
| Temperature |  | °F |  |  | 505 |  | 500 |  | 501 |  | 502
| HCl | E1 | ppmv | y | nd | 0.12152 | nd | 0.11432 | nd | 0.11497 |  | 0.11694
| Cl2 | E1 | ppmv | y | nd | 0.063202 | nd | 0.049701 | nd | 0.053997 |  | 0.055634
| Total Chlorine | E1 | ppmv | y |  | 0.24792 |  | 0.21372 |  | 0.22297 |  | 0.2282
| Chromium (Hex) | E2 | µg/dscm | y |  | 27.2048 |  | 74.4798 |  | 16.6753 |  | 30.555
| Chromium | E3 | µg/dscm | y |  | 58.7642 |  | 124.6326 |  | 56.0701 |  | 68.6811
2 | 911C2 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0073 |  | 0.0368 |  | 0.0157 |  | 0.0176
| CO (RA) | E1 | ppmv | y |  | 17.2 |  | 19.7 |  | 9.6 |  | 15.5
| CO (MHRA) | E1 | ppmv | y |  | 19 |  | 37.1 |  | 17 |  | 24.3667
| HCl |  | g/hr | n |  | 599.4 |  | 709.1 |  | 733.9 |  | 677.2
| Cl2 |  | g/hr | n |  | 87.2 |  | 11.8 |  | 12.9 |  | 40.5
| Chromium (Hex) |  | g/hr | n |  | 0.36 |  | 3.07 |  | 1.69 |  | 1.54
| Chromium |  | g/hr | n |  | 5.8 |  | 11.05 |  | 4.34 |  | 6.57
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 30500 |  | 31292 |  | 31695 |  | 31162.3333
| O2 |  | % |  |  | 3.2 |  | 3.67 |  | 3.2 |  | 3.3567
| Moisture |  | % |  |  | 17.3 |  | 17.4 |  | 17.1 |  | 17.2667
| Temperature |  | °F |  |  | 523 |  | 516 |  | 520 |  | 519.6667
| Sampling Train | Cr (+6) | E2
| Stack Gas Flowrate |  | dscfm |  |  | 33288 |  | 31960 |  | 32329 |  | 32525.6667
| O2 |  | % |  |  | 3.2 |  | 3.67 |  | 3.2 |  | 3.3567
| Moisture |  | % |  |  | 12.8 |  | 15.5 |  | 15.4 |  | 14.5667
| Temperature |  | °F |  |  | 523 |  | 516 |  | 521 |  | 520
| Sampling Train | Cr | E3
| Stack Gas Flowrate |  | dscfm |  |  | 32197 |  | 31901 |  | 31121 |  | 31739.6667
| O2 |  | % |  |  | 3.2 |  | 3.67 |  | 3.2 |  | 3.3567
| Moisture |  | % |  |  | 17.4 |  | 17.3 |  | 17 |  | 17.2333
| Temperature |  | °F |  |  | 520 |  | 513 |  | 519 |  | 517.3333
| HCl | E1 | ppmv | y |  | 6.079 |  | 7.1997 |  | 7.1625 |  | 6.7818
| Cl2 | E1 | ppmv | y |  | 0.45477 |  | 0.061609 |  | 0.06474 |  | 0.20856
| Total Chlorine | E1 | ppmv | y |  | 6.9886 |  | 7.3229 |  | 7.292 |  | 7.1989
| Chromium (Hex) | E2 | µg/dscm | y |  | 5.0094 |  | 45.7008 |  | 24.2139 |  | 22.1261
| Chromium | E3 | µg/dscm | y |  | 83.4417 |  | 164.7972 |  | 64.5961 |  | 96.7326
3 | 911C3 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0146 |  | 0.0173 |  | 0.0196 |  | 0.0164
| CO (RA) | E1 | ppmv | y |  | 1 |  | 3.5 |  | 45 |  | 16.5
| CO (MHRA) | E1 | ppmv | y |  | 6.5 |  | 6 |  | 56.6 |  | 23.0333
| HCl |  | g/hr | n |  | 972.1 |  | 835.5 |  | 793.6 |  | 890
| Cl2 |  | g/hr | n |  | 27.2 |  | 19.4 |  | 24.9 |  | 23.5
| Chromium (Hex) |  | g/hr | n |  | 1.43 |  | 0.88 |  | 1.49 |  | 1.2
| Chromium |  | g/hr | n |  | 5.33 |  | 5.3 |  | 6.78 |  | 5.5
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 32250 |  | 32301 |  | 31451 |  | 32000.6667
| O2 |  | % |  |  | 3.2 |  | 3.53 |  | 3.8 |  | 3.51
| Moisture |  | % |  |  | 15.9 |  | 14.9 |  | 15.6 |  | 15.4667
| Temperature |  | °F |  |  | 529 |  | 531 |  | 534 |  | 531.3333
| Sampling Train | Cr (+6) | E2
| Stack Gas Flowrate |  | dscfm |  |  | 33339 |  | 33838 |  | 32520 |  | 33232.3333
| O2 |  | % |  |  | 3.2 |  | 3.53 |  | 3.8 |  | 3.51
| Moisture |  | % |  |  | 13.3 |  | 13.7 |  | 13.5 |  | 13.5
| Temperature |  | °F |  |  | 530 |  | 533 |  | 535 |  | 532.6667
| Sampling Train | Cr | E3
| Stack Gas Flowrate |  | dscfm |  |  | 32321 |  | 33062 |  | 32087 |  | 32490
| O2 |  | % |  |  | 3.2 |  | 3.53 |  | 3.8 |  | 3.51
| Moisture |  | % |  |  | 15.7 |  | 15.4 |  | 16 |  | 15.7
| Temperature |  | °F |  |  | 529 |  | 530 |  | 531 |  | 530
| HCl | E1 | ppmv | y |  | 9.3239 |  | 8.1522 |  | 8.0775 |  | 8.7554
| Cl2 | E1 | ppmv | y |  | 0.13416 |  | 0.097338 |  | 0.13032 |  | 0.11888
| Total Chlorine | E1 | ppmv | y |  | 9.5922 |  | 8.3469 |  | 8.3381 |  | 8.9932
| Chromium (Hex) | E2 | µg/dscm | y |  | 19.868 |  | 12.2737 |  | 21.9633 |  | 17.0224
| Chromium | E3 | µg/dscm | y |  | 76.3858 |  | 75.6561 |  | 101.289 |  | 79.802
4 | 911C4 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0254 |  | 0.0268 |  | 0.0237 |  | 0.0249
| CO (RA) | E1 | ppmv | y |  | 24.5 |  | 15.8 |  | 27.9 |  | 22.7333
| CO (MHRA) | E1 | ppmv | y |  | 33.8 |  | 19.7 |  | 23.6 |  | 25.7
| HCl |  | g/hr | n |  | 1059 |  | 1165 |  | 1036 |  | 1067
| Cl2 |  | g/hr | n |  | 20.9 |  | 22.7 |  | 16.5 |  | 19.4
| Chromium (Hex) |  | g/hr | n |  | 0.68 |  | 0.67 |  | 0.96 |  | 0.8
| Chromium |  | g/hr | n |  | 3.75 |  | 4.68 |  | 3.52 |  | 3.81
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 32000 |  | 33243 |  | 32819 |  | 32687.3333
| O2 |  | % |  |  | 4.4 |  | 4.6 |  | 4.37 |  | 4.4567
| Moisture |  | % |  |  | 12.5 |  | 11.9 |  | 12.8 |  | 12.4
| Temperature |  | °F |  |  | 542 |  | 551 |  | 549 |  | 547.3333
| Sampling Train | Cr (+6) | E2
| Stack Gas Flowrate |  | dscfm |  |  | 33693 |  | 33412 |  | 34121 |  | 33742
| O2 |  | % |  |  | 4.4 |  | 4.6 |  | 4.37 |  | 4.4567
| Moisture |  | % |  |  | 10.9 |  | 10.6 |  | 11.5 |  | 11
| Temperature |  | °F |  |  | 541 |  | 552 |  | 551 |  | 548
| Sampling Train | Cr | E3
| Stack Gas Flowrate |  | dscfm |  |  | 33665 |  | 33984 |  | 33294 |  | 33647.6667
| O2 |  | % |  |  | 4.4 |  | 4.6 |  | 4.37 |  | 4.4567
| Moisture |  | % |  |  | 11.9 |  | 12.4 |  | 12.7 |  | 12.3333
| Temperature |  | °F |  |  | 540 |  | 551 |  | 549 |  | 546.6667
| HCl | E1 | ppmv | y |  | 10.9768 |  | 11.7657 |  | 10.4515 |  | 10.8642
| Cl2 | E1 | ppmv | y |  | 0.1114 |  | 0.11789 |  | 0.085597 |  | 0.10158
| Total Chlorine | E1 | ppmv | y |  | 11.1996 |  | 12.0015 |  | 10.6227 |  | 11.0674
| Chromium (Hex) | E2 | µg/dscm | y |  | 10.0242 |  | 10.0814 |  | 13.9491 |  | 11.8164
| Chromium | E3 | µg/dscm | y |  | 55.3267 |  | 69.2338 |  | 52.4173 |  | 56.4335
| 911C5 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
sootblow
| PM | E1 | gr/dscf | y |  | 0.0019 |  | 0.0011 |  | 0.001 |  | 0.0013
| CO (RA) | E1 | ppmv | y |  | 0 |  | 0 |  | 0 |  | 0
| CO (MHRA) | E1 | ppmv | y |  | 0 |  | 0 |  | 0 |  | 0
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  |  | 33499 |  | 32993 |  | 32674 |  | 33055.3333
| O2 |  | % |  |  | 3.97 |  | 3.95 |  | 3.88 |  | 3.9333
| Moisture |  | % |  |  | 15.3 |  | 14.8 |  | 14.8 |  | 14.9667
| Temperature |  | °F |  |  | 427 |  | 431 |  | 430 |  | 429.3333
| 911C6 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
| CO (RA) | E1 | ppmv | y |  | 0 |  | 0 |  | 0.1 |  | 0.033333
| CO (MHRA) | E1 | ppmv | y |  | 0 |  | 0 |  | 0.2 |  | 0.066667
| 911C7 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
sootblow
| PM | E1 | gr/dscf | y |  | 0.0175 |  | 0.0183 |  | 0.0215 |  | 0.0246
| CO (RA) | E1 | ppmv | y |  | 1.2 |  | 0.3 |  | 0 |  | 0.5
| CO (MHRA) | E1 | ppmv | y |  | 1.4 |  | 0.6 |  | 0.1 |  | 0.7
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  |  | 32302 |  | 31918 |  | 33179 |  | 32466.3333
| O2 |  | % |  |  | 2.8 |  | 3.3 |  | 3.3 |  | 3.1333
| Moisture |  | % |  |  | 14.2 |  | 14.2 |  | 11.4 |  | 13.2667
| Temperature |  | °F |  |  | 442 |  | 446 |  | 451 |  | 446.3333
| 911C8 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
sootblow
| CO (RA) | E1 | ppmv | y |  | 0 |  | 3.4 |  | 0.3 |  | 1.2333
| Sampling Train |  | E1
| Stack Gas Flowrate |  | dscfm |  |  | 18136 |  | 19462 |  | 18248 |  | 18615.3333
| O2 |  | % |  |  | 5.2 |  | 4.6 |  | 6.1 |  | 5.3
| Moisture |  | % |  |  | 7.7 |  | 8.7 |  | 8.6 |  | 8.3333
| Temperature |  | °F |  |  | 367 |  | 375 |  | 367 |  | 369.6667
| 911C9 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
sootblow
| CO (RA) | E1 | ppmv | y |  | 8.5 |  | 17.1 |  | 15.5 | 2.7 | 13.7
| Sampling Train |  | E1
| Stack Gas Flowrate |  | dscfm |  |  | 30797 |  | 29148 |  | 30233 | 31533 | 30427.75
| O2 |  | % |  |  | 2.7 |  | 2.5 |  | 2.4 | 3.1 | 2.675
| Moisture |  | % |  |  | 12.7 |  | 12.5 |  | 12.7 | 12.5 | 12.6
| Temperature |  | °F |  |  | 476 |  | 460 |  | 472 | 468 | 469
| 911C10 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
| CO (RA) | E1 | ppmv | y |  | 13.9 |  | 21.4 |  | 28 |  | 21.1
| Sampling Train | Metals | E1
| Stack Gas Flowrate |  | dscfm |  |  | 28658 |  | 29951 |  | 29548 |  | 29385.6667
| O2 |  | % |  |  | 3.4 |  | 5.1 |  | 5.1 |  | 4.5333
| Moisture |  | % |  |  | 15.8 |  | 13.6 |  | 14.1 |  | 14.5
| Temperature |  | °F |  |  | 469 |  | 456 |  | 455 |  | 460
| Antimony | E1 | ug/dscm | y | nd | 0.83 | nd | 0.88 | nd | 0.91 |  | 0.87333
| Arsenic | E1 | ug/dscm | y | nd | 2.05 | nd | 2.46 | nd | 1.28 |  | 1.93
| Barium | E1 | ug/dscm | y |  | 49.2 |  | 54.19 |  | 58.67 |  | 54.02
| Beryllium | E1 | ug/dscm | y | nd | 0.07 | nd | 0.06 | nd | 0.11 |  | 0.08
| Cadmium | E1 | ug/dscm | y |  | 0.37 |  | 0.26 |  | 0.36 |  | 0.33
| Chromium | E1 | ug/dscm | y |  | 22.69 |  | 34.07 |  | 32.98 |  | 29.9133
| Lead | E1 | ug/dscm | y |  | 24.57 |  | 17.3 |  | 26.36 |  | 22.7433
| Mercury | E1 | ug/dscm | y | nd | 0.27 | nd | 0.29 | nd | 0.41 |  | 0.32333
| Silver | E1 | ug/dscm | y | nd | 0.61 | nd | 1.88 | nd | 0.43 |  | 0.97333
| Thallium | E1 | ug/dscm | y | nd | 1.33 | nd | 0.59 | nd | 1.46 |  | 1.1267
| SVM | E1 | ug/dscm | y |  | 24.94 |  | 17.56 |  | 26.72 |  | 23.0733
| LVM | E1 | ug/dscm | y |  | 23.75 |  | 35.33 |  | 33.675 |  | 30.9183
| Chromium (Hex) | E2 | ug/dscm | y |  | 4.78 |  | 36.82 |  | 3.25 |  | 14.95
| 911C11 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
| CO (RA) | E1 | ppmv | y |  | 34.9 |  | 26.2 |  | 11 |  | 24.0333
| HCl | E1 | ppmv | y |  | 70.0116 |  | 82.0961 |  | 79.9683 |  | 77.3587
| Cl2 | E1 | ppmv | y |  | 20.889 |  | 17.4895 |  | 17.1902 |  | 18.5229
| Total Chlorine | E1 | ppmv | y |  | 111.7896 |  | 117.0752 |  | 114.3486 |  | 114.4045
| Sampling Train | HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 29795 |  | 28677 |  | 29091 |  | 29187.6667
| O2 |  | % |  |  | 1.9 |  | 3 |  | 2.5 |  | 2.4667
| Moisture |  | % |  |  | 13.3 |  | 13.2 |  | 13.1 |  | 13.2
| Temperature |  | °F |  |  | 466 |  | 454 |  | 463 |  | 461
| Sampling Train | Metals | E2
| Stack Gas Flowrate |  | dscfm |  |  | 29882 |  | 31925 |  | 31672 |  | 31159.6667
| O2 |  | % |  |  | 2.8 |  | 4.9 |  | 3.6 |  | 3.7667
| Moisture |  | % |  |  | 12.6 |  | 12.8 |  | 12.6 |  | 12.6667
| Temperature |  | °F |  |  | 500 |  | 503 |  | 499 |  | 500.6667
| Antimony | E2 | ug/dscm | y | nd | 0.74 | nd | 3.12 | nd | 0.75 |  | 1.5367
| Arsenic | E2 | ug/dscm | y | nd | 0.94 |  | 4.96 | nd | 2.06 |  | 2.6533
| Barium | E2 | ug/dscm | y |  | 45.75 |  | 49.53 |  | 48.95 |  | 48.0767
| Beryllium | E2 | ug/dscm | y | nd | 0.05 |  | 0.1 | nd | 0.09 |  | 0.08
| Cadmium | E2 | ug/dscm | y |  | 0.45 | nd | 0.74 |  | 0.31 |  | 0.5
| Chromium | E2 | ug/dscm | y |  | 9.8 |  | 48.21 |  | 21.19 |  | 26.4
| Lead | E2 | ug/dscm | y |  | 9.46 |  | 23.76 |  | 20.03 |  | 17.75
| Mercury | E2 | ug/dscm | y | nd | 0.12 | nd | 0.132 | nd | 0.13 |  | 0.12733
| Silver | E2 | ug/dscm | y | nd | 0.27 | nd | 0.019 | nd | 0.27 |  | 0.18633
| Thallium | E2 | ug/dscm | y | nd | 0.5 | nd | 0.08 | nd | 0.85 |  | 0.47667
| SVM | E2 | ug/dscm | y |  | 9.91 |  | 24.13 |  | 20.34 |  | 18.1267
| LVM | E2 | ug/dscm | y |  | 10.295 |  | 53.27 |  | 22.265 |  | 28.61
| Chromium (Hex) | E3 | ug/dscm | y |  | 10.86 |  | 9.89 |  | 22.17 |  | 14.3067
| 911C12 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
sootblow
| CO (RA) | E1 | ppmv | y |  | 4.2 |  | 2.2 |  | 1.4 |  | 2.6
| Sampling Train |  | E1
| Stack Gas Flowrate |  | dscfm |  |  | 31121 |  | 31779 |  | 33461 |  | 32120.3333
| O2 |  | % |  |  | 3.3 |  | 2.9 |  | 3.7 |  | 3.3
| Moisture |  | % |  |  | 12.9 |  | 12.5 |  | 12.5 |  | 12.6333
| Temperature |  | °F |  |  | 508 |  | 507 |  | 497 |  | 504
| 911C13 |  |  |  |  | R1 |  | R2 |  | R3 | R4 | Cond Avg
sootblow
| CO (RA) | E1 | ppmv | y |  | 0 |  | 0 |  | 0.1 |  | 0.033333
| Sampling Train |  | E1
| Stack Gas Flowrate |  | dscfm |  |  | 20458 |  | 21582 |  | 19498 |  | 20512.6667
| O2 |  | % |  |  | 6.9 |  | 5.3 |  | 10.1 |  | 7.4333
| Moisture |  | % |  |  | 8.4 |  | 8.5 |  | 8 |  | 8.3
| Temperature |  | °F |  |  | 394 |  | 403 |  | 388 |  | 395

## feed
Feedstreams
* | 911C1 |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | Spike | Spike | Spike | Spike | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 2499 |  | 2522 |  | 2522 |  | 2514.3333
| Feed Rate |  | ft3/hr | [12 empty] | 117100 | 1170000 | 117100 | 117100
| Heating Value |  | Btu/lb |  | 15774 |  | 15910 |  | 15717 |  | 15800
| Density |  | g/cc |  | 1.11 |  | 1.12 |  | 1.12 |  | 1.12
| Ash |  | g/hr |  | 2494 |  | 2288 |  | 2631 |  | 2471
| Chlorine |  | g/hr |  | 272.1 |  | 217.4 |  | 112.1 |  | 200.5333
| Antimony |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Arsenic |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Barium |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Beryllium |  | ppmw | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Cadmium |  | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Chromium |  | ppmw |  | 8.4 |  | 12.6 |  | 7.6 |  | 9.5
| Lead |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Mercury |  | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Silver |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Thallium |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Stack Gas Flowrate |  | dscfm |  | 32257 |  | 32410 |  | 32305 |  | 32324 |  |  |  | 32324 | [11 empty] | 32324
| Oxygen |  | % |  | 3.8 |  | 4.17 |  | 3.3 |  | 3.7567 |  |  |  | 3.7567 | [11 empty] | 3.7567
| Thermal Feedrate |  | MMBtu/hr |  | 39.4192 |  | 40.125 |  | 39.6383 |  | 39.7265 |  |  |  |  | 117.1 | 1170 | 117.1 | 117.1 |  | 156.5192 |  | 1210.125 |  | 156.7383 |  | 156.8265
| Estimated Firing Rate |  | MMBtu/hr | [23 empty] | 176.944
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 37.0625 |  | 34.5846 |  | 37.9375 |  | 36.5282 | [8 empty] | 0 | 37.0625 | 0 | 34.5846 | 0 | 37.9375 | 0 | 36.5282
| Chlorine |  | ug/dscm |  | 4043.584 |  | 3286.1452 |  | 1616.4153 |  | 2982.0482 | [8 empty] | 0 | 4043.584 | 0 | 3286.1452 | 0 | 1616.4153 | 0 | 2982.0482
| Antimony |  | ug/dscm | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925 | [8 empty] | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925
| Arsenic |  | ug/dscm | 100 | 8.43 | 100 | 8.6536 | 100 | 8.255 | 100 | 8.4462 | [8 empty] | 100 | 8.43 | 100 | 8.6536 | 100 | 8.255 | 100 | 8.4462
| Barium |  | ug/dscm | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925 | [8 empty] | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925
| Beryllium |  | ug/dscm | 100 | 5.058 | 100 | 5.1922 | 100 | 4.953 | 100 | 5.0677 | [8 empty] | 100 | 5.058 | 100 | 5.1922 | 100 | 4.953 | 100 | 5.0677
| Cadmium |  | ug/dscm | 100 | 1.686 | 100 | 1.7307 | 100 | 1.651 | 100 | 1.6892 | [8 empty] | 100 | 1.686 | 100 | 1.7307 | 100 | 1.651 | 100 | 1.6892
| Chromium |  | ug/dscm |  | 141.6248 |  | 218.0714 |  | 125.4763 |  | 161.7242 | [8 empty] | 0 | 141.6248 | 0 | 218.0714 | 0 | 125.4763 | 0 | 161.7242
| Lead |  | ug/dscm | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925 | [8 empty] | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925
| Mercury |  | ug/dscm | 100 | 1.686 | 100 | 1.7307 | 100 | 1.651 | 100 | 1.6892 | [8 empty] | 100 | 1.686 | 100 | 1.7307 | 100 | 1.651 | 100 | 1.6892
| Silver |  | ug/dscm | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925 | [8 empty] | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925
| Thallium |  | ug/dscm | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925 | [8 empty] | 100 | 16.8601 | 100 | 17.3073 | 100 | 16.51 | 100 | 16.8925
| SVM |  | ug/dscm | 100 | 18.5461 | 100 | 19.038 | 100 | 18.1611 | 100 | 18.5817 | [8 empty] | 100 | 18.5461 | 100 | 19.038 | 100 | 18.1611 | 100 | 18.5817
| LVM |  | ug/dscm | 8.6957 | 155.1129 | 5.9701 | 231.9172 | 9.5238 | 138.6844 | 7.7118 | 175.2382 | [8 empty] | 8.6957 | 155.1129 | 5.9701 | 231.9172 | 9.5238 | 138.6844 | 7.7118 | 175.2382
*
| 911C2 |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | Spike | Spike | Spike | Spike | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 3923 |  | 3923 |  | 3923 |  | 3923
| Feed Rate |  | ft3/hr | [12 empty] | 117100 | 117000 | 106600 | 106933
| Heating Value |  | Btu/lb |  | 15571 |  | 15686 |  | 15540 |  | 15599
| Density |  | g/cc |  | 1.12 |  | 1.12 |  | 1.12 |  | 1.12
| Ash |  | g/hr |  | 3915 |  | 3203 |  | 2313 |  | 3143.6667 | 6287 | 6287 | 6291 | 6288
| Chlorine |  | g/hr |  | 391.5 |  | 391.5 |  | 113.5 |  | 298.8333 | 712 | 712 | 712 | 712
| Antimony |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Arsenic |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Barium |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Beryllium |  | ppmw | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Cadmium |  | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Chromium |  | ppmw |  | 7.6 |  | 6.6 |  | 4.4 |  | 6.2
| Lead |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Mercury |  | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Silver |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Thallium |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Stack Gas Flowrate |  | dscfm |  | 30500 |  | 31292 |  | 31695 |  | 31162.3333 | 30500 | 31292 | 31695 | 31162.3333 | [5 empty] | 30500 |  | 31292 |  | 31695 |  | 31162.3333
| Oxygen |  | % |  | 3.2 |  | 3.67 |  | 3.2 |  | 3.3567 | 3.2 | 3.67 | 3.2 | 3.3567 | [5 empty] | 3.2 |  | 3.67 |  | 3.2 |  | 3.3567
| Thermal Feedrate |  | MMBtu/hr |  | 61.085 |  | 61.5362 |  | 60.9634 |  | 61.1949 |  |  |  |  | 117.1 | 117 | 106.6 | 106.933 |  | 178.185 |  | 178.5362 |  | 167.5634 |  | 168.1279
| Estimated Firing Rate |  | MMBtu/hr | [17 empty] | 172.3492 |  | 172.1557 |  | 179.1019 |  | 174.542
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 59.4569 |  | 48.6985 |  | 33.803 |  | 47.3195 | 95.4803 | 95.5877 | 91.9389 | 94.2958 |  |  |  |  | 0 | 154.9372 | 0 | 144.2862 | 0 | 125.7419 | 0 | 141.6152
| Chlorine |  | ug/dscm |  | 5945.6902 |  | 5952.3743 |  | 1658.7291 |  | 4518.9312 | 10813.107 | 10825.2631 | 10405.4193 | 10677.258 |  |  |  |  | 0 | 16758.7972 | 0 | 16777.6374 | 0 | 12064.1483 | 0 | 15196.1891
| Antimony |  | ug/dscm | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188 | [8 empty] | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188
| Arsenic |  | ug/dscm | 100 | 13.5243 | 100 | 13.5395 | 100 | 13.0144 | 100 | 13.3594 | [8 empty] | 100 | 13.5243 | 100 | 13.5395 | 100 | 13.0144 | 100 | 13.3594
| Barium |  | ug/dscm | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188 | [8 empty] | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188
| Beryllium |  | ug/dscm | 100 | 8.1146 | 100 | 8.1237 | 100 | 7.8086 | 100 | 8.0156 | [8 empty] | 100 | 8.1146 | 100 | 8.1237 | 100 | 7.8086 | 100 | 8.0156
| Cadmium |  | ug/dscm | 100 | 2.7049 | 100 | 2.7079 | 100 | 2.6029 | 100 | 2.6719 | [8 empty] | 100 | 2.7049 | 100 | 2.7079 | 100 | 2.6029 | 100 | 2.6719
| Chromium |  | ug/dscm |  | 205.5693 |  | 178.7214 |  | 114.5266 |  | 166.2724 | [9 empty] | 205.5693 |  | 178.7214 |  | 114.5266 |  | 166.2724
| Lead |  | ug/dscm | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188 | [8 empty] | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188
| Mercury |  | ug/dscm | 100 | 2.7049 | 100 | 2.7079 | 100 | 2.6029 | 100 | 2.6719 | [8 empty] | 100 | 2.7049 | 100 | 2.7079 | 100 | 2.6029 | 100 | 2.6719
| Silver |  | ug/dscm | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188 | [8 empty] | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188
| Thallium |  | ug/dscm | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188 | [8 empty] | 100 | 27.0486 | 100 | 27.079 | 100 | 26.0288 | 100 | 26.7188
| SVM |  | ug/dscm | 100 | 29.7535 | 100 | 29.7869 | 100 | 28.6317 | 100 | 29.3907 | [8 empty] | 100 | 29.7535 | 100 | 29.7869 | 100 | 28.6317 | 100 | 29.3907
| LVM |  | ug/dscm | 9.5238 | 227.2082 | 10.8108 | 200.3846 | 15.3846 | 135.3496 | 11.3911 | 187.6475 | [8 empty] | 9.5238 | 227.2082 | 10.8108 | 200.3846 | 15.3846 | 135.3496 | 11.3911 | 187.6475
* | 911C3 |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | Spike | Spike | Spike | Spike | Natural Gas | Natural Gas | Natural Gas | Natural Gas | [7 empty] | Total
| Feed Rate |  | lb/hr |  | 5604 |  | 5604 |  | 5655 |  | 5621
| Feed Rate |  | ft3/hr | [12 empty] | 90100 | 90100 | 90200 | 90100
| Heating Value |  | Btu/lb |  | 15299 |  | 15427 |  | 15700 |  | 15475
| Density |  | g/cc |  | 1.12 |  | 1.12 |  | 1.13 |  | 1.12
| Ash |  | g/hr |  | 3305 |  | 3051 |  | 3334 |  | 3230 | 4681 | 4690 | 4690 | 4687
| Chlorine |  | g/hr |  | 381.3 |  | 254.2 |  | 179.5 |  | 271.6667 | 1012 | 1016 | 1016 | 1014.6667
| Antimony |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Arsenic |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Barium |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Beryllium |  | ppmw | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Cadmium |  | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Chromium |  | ppmw |  | 4.2 |  | 4.6 |  | 4.5 |  | 4.4
| Lead |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Mercury |  | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Silver |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Thallium |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Stack Gas Flowrate |  | dscfm |  | 32250 |  | 32301 |  | 31451 |  | 32000.6667 | 32250 | 32301 | 31451 | 32000.6667 | [5 empty] | 32250 |  | 32301 |  | 31451 |  | 32000.6667
| Oxygen |  | % |  | 3.2 |  | 3.53 |  | 3.8 |  | 3.51 | 3.2 | 3.53 | 3.8 | 3.51 | [5 empty] | 3.2 |  | 3.53 |  | 3.8 |  | 3.51
| Thermal Feedrate |  | MMBtu/hr |  | 85.7356 |  | 86.4529 |  | 88.7835 |  | 86.985 |  |  |  |  | 90.1 | 90.1 | 90.2 | 90.1 |  | 175.8356 |  | 176.5529 |  | 178.9835 |  | 177.085
| Estimated Firing Rate |  | MMBtu/hr | [17 empty] | 182.2381 |  | 179.1424 |  | 171.7324 |  | 177.6799
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 47.4692 |  | 44.5783 |  | 50.8151 |  | 47.6209 | 67.2325 | 68.5258 | 71.4826 | 69.0457 | [5 empty] | 114.7017 |  | 113.1042 |  | 122.2977 |  | 116.6666
| Chlorine |  | ug/dscm |  | 5476.5548 |  | 3714.1293 |  | 2735.8476 |  | 3975.5106 | 14535.2043 | 14844.8285 | 15485.3545 | 14947.3742 | [5 empty] | 20011.7591 |  | 18558.9578 |  | 18221.2021 |  | 18922.8848
| Antimony |  | ug/dscm | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155 | [8 empty] | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155
| Arsenic |  | ug/dscm | 100 | 18.2711 | 100 | 18.5868 | 100 | 19.5653 | 100 | 18.8077 | [8 empty] | 100 | 18.2711 | 100 | 18.5868 | 100 | 19.5653 | 100 | 18.8077
| Barium |  | ug/dscm | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155 | [8 empty] | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155
| Beryllium |  | ug/dscm | 100 | 10.9627 | 100 | 11.1521 | 100 | 11.7392 | 100 | 11.2846 | [8 empty] | 100 | 10.9627 | 100 | 11.1521 | 100 | 11.7392 | 100 | 11.2846
| Cadmium |  | ug/dscm | 100 | 3.6542 | 100 | 3.7174 | 100 | 3.9131 | 100 | 3.7615 | [8 empty] | 100 | 3.6542 | 100 | 3.7174 | 100 | 3.9131 | 100 | 3.7615
| Chromium |  | ug/dscm |  | 153.4772 |  | 170.9989 |  | 176.0875 |  | 166.8545 | [9 empty] | 153.4772 |  | 170.9989 |  | 176.0875 |  | 166.8545
| Lead |  | ug/dscm | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155 | [8 empty] | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155
| Mercury |  | ug/dscm | 100 | 3.6542 | 100 | 3.7174 | 100 | 3.9131 | 100 | 3.7615 | [8 empty] | 100 | 3.6542 | 100 | 3.7174 | 100 | 3.9131 | 100 | 1.8808
| Silver |  | ug/dscm | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155 | [8 empty] | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155
| Thallium |  | ug/dscm | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155 | [8 empty] | 100 | 36.5422 | 100 | 37.1737 | 100 | 39.1305 | 100 | 37.6155
| SVM |  | ug/dscm | 100 | 40.1964 | 100 | 40.891 | 100 | 43.0436 | 100 | 41.377 | [8 empty] | 100 | 40.1964 | 100 | 40.891 | 100 | 43.0436 | 100 | 41.377
| LVM |  | ug/dscm | 16 | 182.711 | 14.8148 | 200.7378 | 15.0943 | 207.3919 | 15.2794 | 196.9469 | [8 empty] | 16 | 182.711 | 14.8148 | 200.7378 | 15.0943 | 207.3919 | 15.2794 | 196.9469
* | 911C4 |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | LHC waste |  | LHC waste |  | LHC waste |  | LHC waste | Spike | Spike | Spike | Spike | Natural Gas | Natural Gas | Natural Gas | Natural Gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 9555 |  | 9611 |  | 9475 |  | 9547
| Feed Rate |  | ft3/hr | [12 empty] | 22300 | 21400 | 27400 | 23700
| Heating Value |  | Btu/lb |  | 17277 |  | 17287 |  | 17018 |  | 17144
| Density |  | g/cc |  | 0.905 |  | 0.906 |  | 0.906 |  | 0.906
| Ash |  | g/hr | [7 empty] | 0 | 9562 | 9553 | 9562 | 9559
| Chlorine |  | g/hr |  | 1907 |  | 959 |  | 1633 |  | 1500 | 1288 | 1288 | 1288 | 1288
| Antimony |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Arsenic |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Barium |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Beryllium |  | ppmw | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Cadmium |  | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Chromium |  | ppmw |  | 0.1 |  | 0.1 |  | 0.1 |  | 0.1
| Lead |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Mercury |  | ppmw | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Silver |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Thallium |  | ppmw | nd | 1 | nd | 1 | nd | 1 |  | 1
| Stack Gas Flowrate |  | dscfm |  | 32000 |  | 33243 |  | 32819 |  | 32687.3333 | 32000 | 33243 | 32819 | 32687.3333 | [5 empty] | 32000 |  | 33243 |  | 32819 |  | 32687.3333
| Oxygen |  | % |  | 4.4 |  | 4.6 |  | 4.37 |  | 4.4567 | 4.4 | 4.6 | 4.37 | 4.4567 | [5 empty] | 4.4 |  | 4.6 |  | 4.37 |  | 4.4567
| Thermal Feedrate |  | MMBtu/hr |  | 165.0817 |  | 166.1454 |  | 161.2456 |  | 163.6738 |  |  |  |  | 22.3 | 21.4 | 27.4 | 23.7 |  | 187.3817 |  | 187.5454 |  | 188.6456 |  | 187.3738
| Estimated Firing Rate |  | MMBtu/hr | [17 empty] | 168.6349 |  | 173.0747 |  | 173.2635 |  | 171.669
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 0 |  | 0 |  | 0 |  | 0 | 148.4161 | 144.4728 | 144.4513 | 145.7472 | [5 empty] | 148.4161 |  | 144.4728 |  | 144.4513 |  | 145.7472
| Chlorine |  | ug/dscm |  | 29599.4047 |  | 14503.2355 |  | 24669.4201 |  | 22924.0201 | 19991.6273 | 19478.7981 | 19457.5708 | 19638.2914 | [5 empty] | 49591.032 |  | 33982.0336 |  | 44126.991 |  | 42562.3115
| Antimony |  | ug/dscm | nd | 67.3316 | nd | 65.9889 | nd | 64.9842 |  | 33.0508 | [9 empty] | 33.6658 |  | 32.9944 |  | 32.4921 |  | 33.0508
| Arsenic |  | ug/dscm | nd | 33.6658 | nd | 32.9944 | nd | 32.4921 |  | 16.5254 | [9 empty] | 16.8329 |  | 16.4972 |  | 16.2461 |  | 16.5254
| Barium |  | ug/dscm | nd | 67.3316 | nd | 65.9889 | nd | 64.9842 |  | 33.0508 | [9 empty] | 33.6658 |  | 32.9944 |  | 32.4921 |  | 33.0508
| Beryllium |  | ug/dscm | nd | 20.1995 | nd | 19.7967 | nd | 19.4953 |  | 9.9152 | [9 empty] | 10.0997 |  | 9.8983 |  | 9.7476 |  | 9.9152
| Cadmium |  | ug/dscm | nd | 6.7332 | nd | 6.5989 | nd | 6.4984 |  | 3.3051 | [9 empty] | 3.3666 |  | 3.2994 |  | 3.2492 |  | 3.3051
| Chromium |  | ug/dscm |  | 6.7332 |  | 6.5989 |  | 6.4984 |  | 6.6102 | [9 empty] | 6.7332 |  | 6.5989 |  | 6.4984 |  | 6.6102
| Lead |  | ug/dscm | nd | 67.3316 | nd | 65.9889 | nd | 64.9842 |  | 33.0508 | [9 empty] | 33.6658 |  | 32.9944 |  | 32.4921 |  | 33.0508
| Mercury |  | ug/dscm | nd | 6.7332 | nd | 6.5989 | nd | 6.4984 |  | 3.3051 | [9 empty] | 3.3666 |  | 3.2994 |  | 3.2492 |  | 3.3051
| Silver |  | ug/dscm | nd | 67.3316 | nd | 65.9889 | nd | 64.9842 |  | 33.0508 | [9 empty] | 33.6658 |  | 32.9944 |  | 32.4921 |  | 33.0508
| Thallium |  | ug/dscm | nd | 67.3316 | nd | 65.9889 | nd | 64.9842 |  | 33.0508 | [9 empty] | 33.6658 |  | 32.9944 |  | 32.4921 |  | 33.0508
| SVM |  | ug/dscm |  | 37.0324 |  | 36.2939 |  | 35.7413 |  | 36.3559 | [9 empty] | 37.0324 |  | 36.2939 |  | 35.7413 |  | 36.3559
| LVM |  | ug/dscm |  | 33.6658 |  | 32.9944 |  | 32.4921 |  | 33.0508 | [9 empty] | 33.6658 |  | 32.9944 |  | 32.4921 |  | 33.0508
911C5
[5 empty] | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW
| Feed Class 2 |  |  |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | LHC waste |  | LHC waste |  | LHC waste |  | LHC waste
| Feed Rate |  | lb/hr |  | 4534 |  | 4534 |  | 4534 |  | 4534
| Heating Value |  | Btu/lb
| Density |  | g/cc |  | 0.906 |  | 0.906 |  | 0.906
| Ash |  | g/hr | nd | 2.265 | nd | 2.265 | nd | 2.265
| Chlorine |  | g/hr |  | 502 |  | 564 |  | 589
| Antimony |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Arsenic |  | g/hr | nd | 1.03 | nd | 1.03 | nd | 1.03
| Barium |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Beryllium |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Cadmium |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Chromium |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Lead |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Mercury |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Silver |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Thallium |  | g/hr | nd | 2.06 | nd | 2.06 | nd | 2.06
| Stack Gas Flowrate |  | dscfm |  | 33499 |  | 32993 |  | 32674 |  | 33055.3333
| Oxygen |  | % |  | 3.97 |  | 3.95 |  | 3.88 |  | 3.9333
| Thermal Feedrate |  | MMBtu/hr |  | 75.5 |  | 74 |  | 75.3 |  | 74.9333
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 0.032735 |  | 0.033198 |  | 0.033385 |  | 0.033106
| Chlorine |  | ug/dscm |  | 7255.1697 |  | 8266.5303 |  | 8681.5962 |  | 8067.7654
| Antimony |  | ug/dscm | nd | 29.7722 | nd | 30.1934 | nd | 30.3635 |  | 15.0548
| Arsenic |  | ug/dscm | nd | 14.8861 | nd | 15.0967 | nd | 15.1817 |  | 7.5274
| Barium |  | ug/dscm | nd | 29.7722 | nd | 30.1934 | nd | 30.3635 |  | 15.0548
| Beryllium |  | ug/dscm | nd | 29.7722 | nd | 30.1934 | nd | 30.3635 |  | 15.0548
| Cadmium |  | ug/dscm | nd | 29.7722 | nd | 30.1934 | nd | 30.3635 |  | 20.1154
| Chromium |  | ug/dscm | nd | 29.7722 | nd | 30.1934 |  | 30.3635 |  | 30.1097
| Lead |  | ug/dscm | nd | 29.7722 | nd | 30.1934 | nd | 30.3635 |  | 15.0548
| Mercury |  | ug/dscm | nd | 29.7722 | nd | 30.1934 | nd | 30.3635 |  | 15.0548
| Silver |  | ug/dscm | nd | 29.7722 | nd | 30.1934 | nd | 30.3635 |  | 15.0548
| Thallium |  | ug/dscm | nd | 29.7722 | nd | 30.1934 | nd | 30.3635 |  | 15.0548
| SVM |  | ug/dscm |  | 44.6583 |  | 45.29 |  | 45.5452 |  | 45.1645
| LVM |  | ug/dscm |  | 37.2153 |  | 37.7417 |  | 53.1361 |  | 42.6977
| 911C6 | ?? |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW
| Feed Class 2 |  |  |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | LHC waste |  | LHC waste |  | LHC waste |  | LHC waste
| Feed Rate |  | lb/hr |  | 2267 |  | 2267 |  | 2267 |  | 2267
| Thermal Feedrate |  | MMBtu/hr |  | 37 |  | 37 |  | 37 |  | 37.15
911C7
[5 empty] | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | Spike | Spike | Spike | Spike | Total | Total | Total | Total
| Feed Rate |  | lb/hr |  | 4534 |  | 4534 |  | 4534 |  | 4534
| Density |  | g/cc |  | 0.906 |  | 0.906 |  | 0.906
| Ash |  | g/hr |  | 254 |  | 509 |  | 254 |  | 339 | 7670 | 7670 | 7660 | 7666.6667 | 7924 | 8179 | 7914 | 8005.6667
| Chlorine |  | g/hr |  | 549 |  | 318 |  | 321
| Antimony |  | g/hr | nd | 2.54 | nd | 2.54 | nd | 2.54
| Arsenic |  | g/hr | nd | 1.27 | nd | 1.27 | nd | 1.27
| Barium |  | g/hr | nd | 2.54 | nd | 2.54 | nd | 2.54
| Beryllium |  | g/hr | nd | 0.254 | nd | 0.254 | nd | 0.254
| Cadmium |  | g/hr | nd | 0.254 | nd | 0.254 | nd | 0.254
| Chromium |  | g/hr |  | 1.02 |  | 0.763 |  | 1.02
| Lead |  | g/hr | nd | 2.54 | nd | 2.54 | nd | 2.54
| Mercury |  | g/hr | nd | 0.254 | nd | 0.254 | nd | 0.254
| Silver |  | g/hr | nd | 2.54 | nd | 2.54 | nd | 2.54
| Thallium |  | g/hr | nd | 2.54 | nd | 2.54 | nd | 2.54
| Stack Gas Flowrate |  | dscfm |  | 32302 |  | 31918 |  | 33179 |  | 32466.3333
| Oxygen |  | % |  | 2.8 |  | 3.3 |  | 3.3 |  | 3.1333
| Thermal Feedrate |  | MMBtu/hr |  | 88.5 |  | 88.4 |  | 88.6 |  | 88.5 |  |  |  |  | 88.5 | 88.4 | 88.6 | 88.5
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 3.5622 |  | 7.4285 |  | 3.5661 |  | 4.8523 | 107.5685 | 111.9378 | 107.5431 | 109.0165 | 111.1307 | 119.3663 | 111.1092 | 113.8687
| Chlorine |  | ug/dscm |  | 7699.4888 |  | 4640.9676 |  | 4506.7018 |  | 5615.7194 |  |  |  |  | 7699.4888 | 4640.9676 | 4506.7018 | 5615.7194
| Antimony |  | ug/dscm | nd | 35.6224 | nd | 37.0694 | nd | 35.6605 |  | 18.0587 |  |  |  |  | 35.6224 | 37.0694 | 35.6605 | 36.1174
| Arsenic |  | ug/dscm | nd | 17.8112 | nd | 18.5347 | nd | 17.8303 |  | 9.0294 |  |  |  |  | 17.8112 | 18.5347 | 17.8303 | 18.0587
| Barium |  | ug/dscm | nd | 35.6224 | nd | 37.0694 | nd | 35.6605 |  | 18.0587 |  |  |  |  | 35.6224 | 37.0694 | 35.6605 | 36.1174
| Beryllium |  | ug/dscm | nd | 3.5622 | nd | 3.7069 | nd | 3.5661 |  | 1.8059 |  |  |  |  | 3.5622 | 3.7069 | 3.5661 | 3.6117
| Cadmium |  | ug/dscm | nd | 3.5622 | nd | 3.7069 | nd | 3.5661 |  | 1.8059 |  |  |  |  | 3.5622 | 3.7069 | 3.5661 | 3.6117
| Chromium |  | ug/dscm |  | 14.3051 |  | 11.1354 |  | 14.3204 |  | 13.2536 |  |  |  |  | 14.3051 | 11.1354 | 14.3204 | 13.2536
| Lead |  | ug/dscm | nd | 35.6224 | nd | 37.0694 | nd | 35.6605 |  | 18.0587 |  |  |  |  | 35.6224 | 37.0694 | 35.6605 | 36.1174
| Mercury |  | ug/dscm | nd | 3.5622 | nd | 3.7069 | nd | 3.5661 |  | 1.8059 |  |  |  |  | 3.5622 | 3.7069 | 3.5661 | 3.6117
| Silver |  | ug/dscm | nd | 35.6224 | nd | 37.0694 | nd | 35.6605 |  | 18.0587 |  |  |  |  | 35.6224 | 37.0694 | 35.6605 | 36.1174
| Thallium |  | ug/dscm | nd | 35.6224 | nd | 37.0694 | nd | 35.6605 |  | 18.0587 |  |  |  |  | 35.6224 | 37.0694 | 35.6605 | 36.1174
| SVM |  | ug/dscm |  | 19.5923 |  | 20.3881 |  | 19.6133 |  | 19.8646 |  |  |  |  | 19.5923 | 20.3881 | 19.6133 | 19.8646
| LVM |  | ug/dscm |  | 24.9918 |  | 22.2562 |  | 25.0185 |  | 24.0888 |  |  |  |  | 24.9918 | 22.2562 | 25.0185 | 24.0888
911C8
[5 empty] | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | NG | NG | NG | NG | Total | Total | Total | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF | Total | Total | Total | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Total | Total | Total | Total
| Feed Rate |  | lb/hr |  | 5448 |  | 5592 |  | 5574 |  | 5538
| Heating Value |  | Btu/lb |  | 15620 |  | 15620 |  | 15620 |  | 15620
| Ash |  | g/hr |  | 2177.28 |  | 3538.08 |  | 2177.28 |  | 2630.88
| Ash |  | mg/dscm | y | 62.6478 |  | 91.3959 |  | 66.0242 |  | 73.356 |  |  |  |  | 62.6478 | 91.3959 | 66.0242 | 73.356
| Stack Gas Flowrate | E1 | dscfm |  | 18136 |  | 19462 |  | 18248 |  | 18615.3333
| Oxygen |  | % |  | 5.2 |  | 4.6 |  | 6.1 |  | 5.3
| Thermal Feedrate |  | MMBtu/hr |  | 85.0978 |  | 87.347 |  | 87.0659 |  | 86.5036 | 2.7 | 0 | 1.3 | 1.3333 | 87.7978 | 87.347 | 88.3659 | 87.8369
911C9
[5 empty] | R1 |  | R2 |  | R3 |  | R4 | Cond Avg | R1 | R2 | R3 | R4 | Cond Avg | R1 | R2 |  | R3 |  | R4 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F1 | F2 | F2 | F2 | F2 | F2 | F3 | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Liq HW | NG | NG | NG | NG | NG | Total | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | HW | MF | MF | MF | MF | MF | Total | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | HHC waste | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Total | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 5580 |  | 5580 |  | 5580 |  | 5580 | 5580
| Heating Value |  | Btu/lb |  | 15620 |  | 15620 |  | 15620 |  | 15620 | 15620
| Ash |  | g/hr |  | 2177.28 |  | 3538.08 |  | 2177.28 |  | 2177.28 | 2517.48
| Ash |  | mg/dscm | y | 31.8526 |  | 54.0975 |  | 31.9235 |  | 31.8043 | 37.4195 | [5 empty] | 31.8526 | 54.0975 |  | 31.9235 |  | 31.8043 |  | 37.4195
| Stack Gas Flowrate |  | dscfm |  | 30797 |  | 29148 |  | 30233 |  | 31533 | 30427.75
| Oxygen |  | % |  | 2.7 |  | 2.5 |  | 2.4 |  | 3.1 | 2.675
| Thermal Feedrate |  | MMBtu/hr |  | 87.1596 |  | 87.1596 |  | 87.1596 |  | 87.1596 | 87.1596 | 63.8 | 63.9 | 65.8 | 65.9 | 64.85 | 150.9596 | 151.0596 |  | 152.9596 |  | 153.0596 |  | 152.0096
911C10
[5 empty] | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | NG | NG | NG | NG | Total | Total | Total | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF | Total | Total | Total | Total
| Feedstream Description |  |  |  | LHC waste |  | LHC waste |  | LHC waste |  | LHC waste | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Total | Total | Total | Total
| Feed Rate |  | lb/hr |  | 4374 |  | 4380 |  | 4374 |  | 4376
| Heating Value |  | Btu/lb |  | 17240 |  | 17240 |  | 17240 |  | 17240
| Ash |  | g/hr |  | 1088.64 |  | 1088.64 |  | 272.16 |  | 816.48
| Chlorine |  | g/hr |  | 168.7 |  | 151 |  | 156.8 |  | 158.8333
| Antimony |  | g/hr | nd | 0.99 | nd | 0.99 | nd | 0.99 |  | 0.99
| Arsenic |  | g/hr | nd | 0.99 | nd | 0.99 | nd | 0.99 |  | 0.99
| Barium |  | g/hr | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Beryllium |  | g/hr | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Cadmium |  | g/hr | nd | 0.2 | nd | 0.2 | nd | 0.2 |  | 0.2
| Chromium |  | g/hr | nd | 0.99 | nd | 0.99 | nd | 0.99 |  | 0.99
| Lead |  | g/hr | nd | 0.99 | nd | 0.99 | nd | 0.99 |  | 0.99
| Mercury |  | g/hr | nd | 0.04 | nd | 0.04 | nd | 0.04 |  | 0.04
| Silver |  | g/hr | nd | 0.4 | nd | 0.4 | nd | 0.4 |  | 0.4
| Thallium |  | g/hr | nd | 0.99 | nd | 0.99 | nd | 0.99 |  | 0.99
| Stack Gas Flowrate |  | dscfm |  | 28658 |  | 29951 |  | 29548 |  | 29385.6667
| Oxygen |  | % |  | 3.4 |  | 5.1 |  | 5.1 |  | 4.5333
| Thermal Feedrate |  | MMBtu/hr |  | 75.4078 |  | 75.5112 |  | 75.4078 |  | 75.4422 | 77 | 76.5 | 75.5 | 76.3333 | 152.4078 | 152.0112 | 150.9078 | 151.7756
Feedrate MTEC Calculations
| Ash |  | mg/dscm |  | 17.7957 |  | 18.848 |  | 4.7763 |  | 13.8067 |  |  |  |  | 17.7957 | 18.848 | 4.7763 | 13.8067
| Chlorine |  | ug/dscm |  | 2757.6992 |  | 2614.3206 |  | 2751.7641 |  | 2707.9279 |  |  |  |  | 2757.6992 | 2614.3206 | 2751.7641 | 2707.9279
| Antimony |  | ug/dscm | nd | 16.1833 | nd | 17.1402 | nd | 17.374 |  | 8.4496 |  |  |  |  | 16.1833 | 17.1402 | 17.374 | 8.4496
| Arsenic |  | ug/dscm | nd | 16.1833 | nd | 17.1402 | nd | 17.374 |  | 8.4496 |  |  |  |  | 16.1833 | 17.1402 | 17.374 | 8.4496
| Barium |  | ug/dscm | nd | 4.904 | nd | 5.194 | nd | 5.2649 |  | 2.5605 |  |  |  |  | 4.904 | 5.194 | 5.2649 | 2.5605
| Beryllium |  | ug/dscm | nd | 4.904 | nd | 5.194 | nd | 5.2649 |  | 2.5605 |  |  |  |  | 4.904 | 5.194 | 5.2649 | 2.5605
| Cadmium |  | ug/dscm | nd | 3.2694 | nd | 3.4627 | nd | 3.5099 |  | 1.707 |  |  |  |  | 3.2694 | 3.4627 | 3.5099 | 1.707
| Chromium |  | ug/dscm | nd | 16.1833 | nd | 17.1402 | nd | 17.374 |  | 8.4496 |  |  |  |  | 16.1833 | 17.1402 | 17.374 | 8.4496
| Lead |  | ug/dscm | nd | 16.1833 | nd | 17.1402 | nd | 17.374 |  | 8.4496 |  |  |  |  | 16.1833 | 17.1402 | 17.374 | 8.4496
| Mercury |  | ug/dscm | nd | 0.65387 | nd | 0.69254 | nd | 0.70198 |  | 0.3414 |  |  |  |  | 0.65387 | 0.69254 | 0.70198 | 0.3414
| Silver |  | ug/dscm | nd | 6.5387 | nd | 6.9254 | nd | 7.0198 |  | 3.414 |  |  |  |  | 6.5387 | 6.9254 | 7.0198 | 3.414
| Thallium |  | ug/dscm | nd | 16.1833 | nd | 17.1402 | nd | 17.374 |  | 8.4496 |  |  |  |  | 16.1833 | 17.1402 | 17.374 | 8.4496
| SVM |  | ug/dscm |  | 9.7263 |  | 10.3015 |  | 10.442 |  | 10.1566 |  |  |  |  | 9.7263 | 10.3015 | 10.442 | 10.1566
| LVM |  | ug/dscm |  | 18.6353 |  | 19.7373 |  | 20.0064 |  | 19.4597 |  |  |  |  | 18.6353 | 19.7373 | 20.0064 | 19.4597
911C11
[5 empty] | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | NG | NG | NG | NG | Total | Total | Total | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF | Total | Total | Total | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Total | Total | Total | Total
| Feed Rate |  | lb/hr |  | 5580 |  | 5556 |  | 5580 |  | 5572
| Heating Value |  | Btu/lb |  | 15620 |  | 15620 |  | 15620 |  | 15620
| Ash |  | g/hr | nd | 544.32 | nd | 544.32 | nd | 544.32 |  | 544.32
| Chlorine |  | g/hr
| Antimony |  | g/hr | nd | 1.27 | nd | 1.26 | nd | 1.26 |  | 1.2633
| Arsenic |  | g/hr | nd | 1.27 | nd | 1.26 | nd | 1.26 |  | 1.2633
| Barium |  | g/hr | nd | 0.38 | nd | 0.38 | nd | 0.61 |  | 0.45667
| Beryllium |  | g/hr | nd | 0.38 | nd | 0.38 | nd | 0.38 |  | 0.38
| Cadmium |  | g/hr | nd | 0.25 | nd | 0.25 | nd | 0.25 |  | 0.25
| Chromium |  | g/hr |  | 1.49 |  | 1.89 |  | 1.49 |  | 1.6233
| Lead |  | g/hr | nd | 1.27 | nd | 1.26 | nd | 1.26 |  | 1.2633
| Mercury |  | g/hr | nd | 0.05 | nd | 0.05 | nd | 0.05 |  | 0.05
| Silver |  | g/hr | nd | 0.51 | nd | 0.5 | nd | 0.51 |  | 0.50667
| Thallium |  | g/hr | nd | 1.27 | nd | 1.26 | nd | 1.26 |  | 1.2633
| Stack Gas Flowrate |  | dscfm |  | 29882 |  | 31925 |  | 31672 |  | 31159.6667
| Oxygen |  | % |  | 2.8 |  | 4.9 |  | 3.6 |  | 3.7667
| Thermal Feedrate |  | MMBtu/hr |  | 87.1596 |  | 86.7847 |  | 87.1596 |  | 87.0346 | 73 | 75.7 | 75.4 | 74.7 | 160.1596 | 162.4847 | 162.5596 | 161.7346
Feedrate MTEC Calculations
| Ash |  | mg/dscm | nd | 8.2521 | nd | 8.7315 | nd | 8.1437 |  | 8.3757 |  |  |  |  | 8.2521 | 8.7315 | 8.1437 | 8.3757
| Chlorine |  | ug/dscm
| Antimony |  | ug/dscm | nd | 19.2536 | nd | 20.2118 | nd | 18.8511 |  | 9.7194 |  |  |  |  | 19.2536 | 20.2118 | 18.8511 | 9.7194
| Arsenic |  | ug/dscm | nd | 19.2536 | nd | 20.2118 | nd | 18.8511 |  | 9.7194 |  |  |  |  | 19.2536 | 20.2118 | 18.8511 | 9.7194
| Barium |  | ug/dscm | nd | 5.7609 | nd | 6.0956 | nd | 9.1263 |  | 3.4971 |  |  |  |  | 5.7609 | 6.0956 | 9.1263 | 3.4971
| Beryllium |  | ug/dscm | nd | 5.7609 | nd | 6.0956 | nd | 5.6852 |  | 2.9236 |  |  |  |  | 5.7609 | 6.0956 | 5.6852 | 2.9236
| Cadmium |  | ug/dscm | nd | 3.7901 | nd | 4.0103 | nd | 3.7403 |  | 1.9234 |  |  |  |  | 3.7901 | 4.0103 | 3.7403 | 1.9234
| Chromium |  | ug/dscm |  | 22.5889 |  | 30.3176 |  | 22.2921 |  | 25.0662 |  |  |  |  | 22.5889 | 30.3176 | 22.2921 | 25.0662
| Lead |  | ug/dscm | nd | 19.2536 | nd | 20.2118 | nd | 18.8511 |  | 9.7194 |  |  |  |  | 19.2536 | 20.2118 | 18.8511 | 9.7194
| Mercury |  | ug/dscm | nd | 0.75802 | nd | 0.80205 | nd | 0.74806 |  | 0.38469 |  |  |  |  | 0.75802 | 0.80205 | 0.74806 | 0.38469
| Silver |  | ug/dscm | nd | 7.7318 | nd | 8.0205 | nd | 7.6302 |  | 3.8971 |  |  |  |  | 7.7318 | 8.0205 | 7.6302 | 3.8971
| Thallium |  | ug/dscm | nd | 19.2536 | nd | 20.2118 | nd | 18.8511 |  | 9.7194 |  |  |  |  | 19.2536 | 20.2118 | 18.8511 | 9.7194
| SVM |  | ug/dscm |  | 11.5219 |  | 12.111 |  | 11.2957 |  | 11.6429 |  |  |  |  | 11.5219 | 12.111 | 11.2957 | 11.6429
| LVM |  | ug/dscm |  | 35.0962 |  | 43.4713 |  | 34.5603 |  | 37.7093 |  |  |  |  | 35.0962 | 43.4713 | 34.5603 | 37.7093
911C12
[5 empty] | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | NG | NG | NG | NG | Total | Total | Total | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | MF | MF | MF | MF | Total | Total | Total | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Total | Total | Total | Total
| Feed Rate |  | lb/hr |  | 5580 |  | 5586 |  | 5598 |  | 5588
| Heating Value |  | Btu/lb |  | 15620 |  | 15620 |  | 15620 |  | 15620
| Ash |  | g/hr |  | 3810.24 |  | 3538.08 |  | 3265.92 |  | 3538.08
| Ash |  | mg/dscm | y | 57.0316 |  | 91.3959 |  | 99.0363 |  | 82.4879 |  |  |  |  | 57.0316 | 91.3959 | 99.0363 | 82.4879
| Stack Gas Flowrate | E1 | dscfm |  | 31121 |  | 31779 |  | 33461 |  | 32120.3333
| Oxygen |  | % |  | 3.3 |  | 2.9 |  | 3.7 |  | 3.3
| Thermal Feedrate |  | MMBtu/hr |  | 87.1596 |  | 87.2533 |  | 87.4408 |  | 87.2846 | 67.8 | 67.9 | 67.5 | 67.7 | 154.9596 | 155.1533 | 154.9408 | 155.0179
911C13
[5 empty] | R1 |  | R2 |  | R3 |  | R4 | Cond Avg | R1 | R2 | R3 | R4 | Cond Avg | R1 | R2 |  | R3 |  | R4 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F1 | F2 | F2 | F2 | F2 | F2 | F3 | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Liq HW | NG | NG | NG | NG | NG | Total | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | HW | MF | MF | MF | MF | MF | Total | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | HHC waste |  | HHC waste |  | HHC waste |  | HHC waste | HHC waste | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Natural Gas | Total | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 5610 |  | 5604 |  | 5604 |  | 5580 | 5599.5
| Heating Value |  | Btu/lb |  | 15620 |  | 15620 |  | 15620 |  | 15620 | 15620
| Ash |  | g/hr |  | 3810.24 |  | 3810.24 |  | 3810.24 |  | 2177.28 | 3402
| Ash |  | mg/dscm | y | 55.7421 |  | 58.2589 |  | 55.8661 |  | 31.8043 | 50.4179 | [5 empty] | 55.7421 | 58.2589 |  | 55.8661 |  | 31.8043 |  | 50.4179
| Stack Gas Flowrate |  | dscfm |  | 20458 |  | 21582 |  | 19498 |  | 20512.6667 | 20512.6667
| Oxygen |  | % |  | 6.9 |  | 5.3 |  | 10.1 |  | 7.4333 | 7.4333
| Thermal Feedrate |  | MMBtu/hr |  | 87.6282 |  | 87.5345 |  | 87.5345 |  | 87.1596 | 87.4642 | 1.7 | 0.2 | 1.7 | 1.4 | 1.25 | 89.3282 | 87.7345 |  | 89.2345 |  | 88.5596 |  | 88.7142
Units No. 911 and 912 separately
| BIF Feedrate Limits | Adjusted Tier 1 | [8 empty] | LHC Feed for 911
| Ash |  | g/hr | [7 empty] | 2060
| Chlorine |  | g/hr | [7 empty] | 3130
| Arsenic |  | g/hr | [7 empty] | 1.44
| Beryllium |  | g/hr | [7 empty] | 0.46
| Cadmium |  | g/hr | [7 empty] | 0.438
| Chromium |  | g/hr | [7 empty] | 0.735
| Antimony |  | g/hr | [7 empty] | 2350
| Barium |  | g/hr | [7 empty] | 391000
| Lead |  | g/hr | [7 empty] | 704
| Mercury |  | g/hr | [7 empty] | 626
| Silver |  | g/hr | [7 empty] | 23500
| Thallium |  | g/hr | [7 empty] | 2350
Units No. 911 and 912 separately
| BIF Feedrate Limits | Adjusted Tier 1 | [8 empty] | HHC Feed for 911
| Ash |  | g/hr | [7 empty] | 8000
| Chlorine |  | g/hr | [7 empty] | 3130
| Arsenic |  | g/hr | [7 empty] | 4.32
| Beryllium |  | g/hr | [7 empty] | 1.18
| Cadmium |  | g/hr | [7 empty] | 1.31
| Chromium |  | g/hr | [7 empty] | 21.9
| Antimony |  | g/hr | [7 empty] | 2350
| Barium |  | g/hr | [7 empty] | 391000
| Lead |  | g/hr | [7 empty] | 704
| Mercury |  | g/hr | [7 empty] | 626
| Silver |  | g/hr | [7 empty] | 23500
| Thallium |  | g/hr | [7 empty] | 2350

## df c1
PCDD/PCDF
N
Facility Name and ID: |  | Aristech, 2001 UB
Condition ID: |  | 911C13
Condition/Test Date: |  | Trial burn, Nov 15-16, 2001
|  | I-TEF |  | Run 1 |  |  |  |  | Run 2 |  |  |  |  | Run 3
|  | Wght Fact |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ
|  |  |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND
Detected in sample volume (pg)
| 2,3,7,8-TCDD | 1 | nd | 19.1 | 19.1 | 9.55 | 9.55 | nd | 32.78 | 32.78 | 16.39 | 16.39 | nd | 14.89 | 14.89 | 7.445 | 7.445
| Total TCDD | 0 | nd | 94 | 0 | 47 | 0 | nd | 466.58 | 0 | 233.29 | 0 | nd | 148.89 | 0 | 74.445 | 0
| 1,2,3,7,8-PCDD | 0.5 | nd | 11.56 | 5.78 | 5.78 | 2.89 | nd | 33.96 | 16.98 | 16.98 | 8.49 | nd | 23.82 | 11.91 | 11.91 | 5.955
| Total PCDD | 0 | nd | 74.72 | 0 | 37.36 | 0 | nd | 33.96 | 0 | 16.98 | 0 | nd | 96.52 | 0 | 48.26 | 0
| 1,2,3,4,7,8-HxCDD | 0.1 | nd | 20.95 | 2.095 | 10.475 | 1.0475 | nd | 28.1 | 2.81 | 14.05 | 1.405 | nd | 32 | 3.2 | 16 | 1.6
| 1,2,3,6,7,8-HxCDD | 0.1 | nd | 19.62 | 1.962 | 9.81 | 0.981 | nd | 29.85 | 2.985 | 14.925 | 1.4925 | nd | 30 | 3 | 15 | 1.5
| 1,2,3,7,8,9-HxCDD | 0.1 | nd | 18.4 | 1.84 | 9.2 | 0.92 | nd | 26.54 | 2.654 | 13.27 | 1.327 | nd | 28.1 | 2.81 | 14.05 | 1.405
| Total HxCDD | 0 | nd | 112.21 | 0 | 56.105 | 0 | nd | 312.63 | 0 | 156.315 | 0 | nd | 28.2 | 0 | 14.1 | 0
| 1,2,3,4,6,7,8-HpCDD | 0.01 | nd | 76.41 | 0.7641 | 38.205 | 0.38205 | nd | 97.01 | 0.9701 | 48.505 | 0.48505 | nd | 25.79 | 0.2579 | 12.895 | 0.12895
| Total HpCDD | 0 | nd | 147.11 | 0 | 73.555 | 0 | nd | 187.91 | 0 | 93.955 | 0 | nd | 25.79 | 0 | 12.895 | 0
| OCDD | 0.001 | nd | 140 | 0.14 | 70 | 0.07 | nd | 71.5 | 0.0715 | 35.75 | 0.03575 | nd | 38.2 | 0.0382 | 19.1 | 0.0191
| 2,3,7,8-TCDF | 0.1 | nd | 23.29 | 2.329 | 11.645 | 1.1645 | nd | 18.1 | 1.81 | 9.05 | 0.905 | nd | 8.84 | 0.884 | 4.42 | 0.442
| Total TCDF | 0 | nd | 428.29 | 0 | 214.145 | 0 | nd | 422.2 | 0 | 211.1 | 0 | nd | 171.3 | 0 | 85.65 | 0
| 1,2,3,7,8-PCDF | 0.05 | nd | 21.03 | 1.0515 | 10.515 | 0.52575 | nd | 19.71 | 0.9855 | 9.855 | 0.49275 | nd | 16.22 | 0.811 | 8.11 | 0.4055
| 2,3,4,7,8-PCDF | 0.5 | nd | 25.81 | 12.905 | 12.905 | 6.4525 | nd | 23.5 | 11.75 | 11.75 | 5.875 | nd | 14.76 | 7.38 | 7.38 | 3.69
| Total PCDF | 0 | nd | 148.36 | 0 | 74.18 | 0 | nd | 145.25 | 0 | 72.625 | 0 | nd | 16.74 | 0 | 8.37 | 0
| 1,2,3,4,7,8-HxCDF | 0.1 | nd | 25.26 | 2.526 | 12.63 | 1.263 | nd | 22.07 | 2.207 | 11.035 | 1.1035 | nd | 10.61 | 1.061 | 5.305 | 0.5305
| 1,2,3,6,7,8-HxCDF | 0.1 | nd | 23.21 | 2.321 | 11.605 | 1.1605 | nd | 19.01 | 1.901 | 9.505 | 0.9505 | nd | 8.64 | 0.864 | 4.32 | 0.432
| 2,3,4,6,7,8-HxCDF | 0.1 | nd | 26.16 | 2.616 | 13.08 | 1.308 | nd | 26.95 | 2.695 | 13.475 | 1.3475 | nd | 10.25 | 1.025 | 5.125 | 0.5125
| 1,2,3,7,8,9-HxCDF | 0.1 | nd | 13.54 | 1.354 | 6.77 | 0.677 | nd | 11.26 | 1.126 | 5.63 | 0.563 | nd | 11.96 | 1.196 | 5.98 | 0.598
| Total HxCDF | 0 | nd | 137.86 | 0 | 68.93 | 0 | nd | 124.44 | 0 | 62.22 | 0 | nd | 10.23 | 0 | 5.115 | 0
| 1,2,3,4,6,7,8-HpCDF | 0.01 | nd | 59.71 | 0.5971 | 29.855 | 0.29855 | nd | 57.89 | 0.5789 | 28.945 | 0.28945 | nd | 14.02 | 0.1402 | 7.01 | 0.0701
| 1,2,3,4,7,8,9-HpCDF | 0.01 | nd | 19.85 | 0.1985 | 9.925 | 0.09925 | nd | 18.99 | 0.1899 | 9.495 | 0.09495 | nd | 12.63 | 0.1263 | 6.315 | 0.06315
| Total HpCDF | 0 | nd | 107.13 | 0 | 53.565 | 0 | nd | 90.93 | 0 | 45.465 | 0 | nd | 14.48 | 0 | 7.24 | 0
| OCDF | 0.001 | nd | 59.6 | 0.0596 | 29.8 | 0.0298 |  | 71.5 | 0.0715 | 71.5 | 0.0715 | nd | 34.2 | 0.0342 | 17.1 | 0.0171
| Gas sample volume (dscf) |  |  |  | 83.685 | 83.685 | 83.685 |  |  | 111.12 | 111.12 | 111.12 |  |  | 28.234 | 28.234 | 28.234
| O2 (%) |  |  |  | 6.9 | 6.9 | 6.9 |  |  | 5.3 | 5.3 | 5.3 |  |  | 10.1 | 10.1 | 10.1
| PCDD/PCDF (ng in sample) |  |  |  | 0.057639 | 0.72464 | 0.028819 |  |  | 0.082565 | 0.9992 | 0.041318 |  |  | 0.049628 | 0.29227 | 0.024814
| PCDD/PCDF (ng/dscm @ 7% O2) |  | 100 |  | 0.024165 | 0.30381 | 0.012083 | 99.9134 |  | 0.023413 | 0.28334 | 0.011716 | 100 |  | 0.079775 | 0.46982 | 0.039888
| TEQ Cond Avg | 0.021229
| Total Cond Avg | 0.35232
NOTE: sample gas volumes were inferred from using reported O2 and TEQ concenratations at 7% O2.