## 25F nomo
Murray-Custer 230kV line O/S
NI Separation scheme armed @ 100MW
Winter 2006
North-to-South (NS)
Light Loads
Outage: |  | 457
Temp: |  | 25 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 3470.3473
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3201.39 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 650 | 3205.12 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3205.23 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3251.02 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3205.12 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 3076.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3240.22 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 650 | 2521.41 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3240.93 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 650 | 2384.64 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3251.02 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3205.23 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3069.24 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 380 | 3240.93 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3073.47 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 380 | 3073.47 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3076.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 380 | 2508.28 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2520.43 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 380 | 2374.97 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2508.28 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 100 | 3201.39 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2521.41 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 100 | 3240.22 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2366.08 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 100 | 3069.24 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2374.97 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 100 | 2520.43 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2384.64 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 100 | 2366.08 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Murray-Custer 230kV line O/S
NI Separation scheme armed @ 100MW
Winter 2006
North-to-South (NS)
Light Loads
Outage: |  | 457
Temp: |  | 35 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2913.66
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3168.28 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 650 | 3182.8 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3178.53 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3210.91 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3182.8 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 2686.73 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3207.83 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 650 | 2387.12 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3217.3 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 650 | 2208.6 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3210.91 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3178.53 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2673.82 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 380 | 3217.3 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2678.63 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 380 | 2678.63 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2686.73 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 380 | 2383.19 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2375.04 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 380 | 2207.71 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2383.19 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 100 | 3168.28 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2387.12 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 100 | 3207.83 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2192.68 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 100 | 2673.82 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2207.71 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 100 | 2375.04 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2208.6 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 100 | 2192.68 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Murray-Custer 230kV line O/S
NI Separation scheme armed @ 100MW
Winter 2006
North-to-South (NS)
Light Loads
Outage: |  | 457
Temp: |  | 45 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2621.418
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3111.61 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 650 | 3132.07 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3120.51 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3096.65 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3132.07 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 2624.05 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3080.2 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 650 | 2247.38 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3088.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 650 | 2080.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3096.65 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3120.51 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2615.85 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 380 | 3088.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2621.88 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 380 | 2621.88 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2624.05 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 380 | 2243.62 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2237.92 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 380 | 2069.46 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2243.62 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 100 | 3111.61 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2247.38 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 100 | 3080.2 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2063.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 100 | 2615.85 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2069.46 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 100 | 2237.92 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2080.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 100 | 2063.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Murray-Custer 230kV line O/S
NI Separation scheme armed @ 100MW
Winter 2006
North-to-South (NS)
Light Loads
Outage: |  | 457
Temp: |  | 60 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 2973.4713
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3029.27 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 650 | 3047.26 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3040.88 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3047.76 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3047.26 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 2619.06 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 3036.73 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 650 | 2209.34 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3046.29 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 650 | 2034.68 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3047.76 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 3040.88 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2612.06 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 380 | 3046.29 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2614.99 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 380 | 2614.99 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2619.06 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 380 | 2204.5 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2198.04 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 380 | 1981.48 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2204.5 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 100 | 3029.27 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2209.34 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 100 | 3036.73 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1878.58 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 100 | 2612.06 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1981.48 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 100 | 2198.04 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2034.68 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 100 | 1878.58 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Murray-Custer 230kV line O/S
NI Separation scheme armed @ 100MW
Winter 2006
North-to-South (NS)
Light Loads
Outage: |  | 457
Temp: |  | 70 Fahrenheit
|  |  | Average Puget Sound Net Area Load = | 3531.7733
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2975.17 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 650 | 2988.51 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2977.96 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 650 | 3018.21 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2988.51 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 650 | 2605.6 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2997.42 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 650 | 2174.94 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 3008.59 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 650 | 1618.51 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 3018.21 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 380 | 2977.96 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2597.42 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 380 | 3008.59 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2599.58 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 380 | 2599.58 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2605.6 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 380 | 2170.74 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2162.99 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 380 | 1536.08 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2170.74 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 100 | 2975.17 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2174.94 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 100 | 2997.42 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1420.38 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 100 | 2597.42 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1536.08 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 100 | 2162.99 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1618.51 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 100 | 1420.38 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
Description: |  | Murray-Custer 230kV line O/S
NI Separation scheme armed @ 100MW
Season/Year: |  | Winter 2006
Direction: |  | North-to-South (NS)
Case Loads: |  | Light Loads
Outage: |  | 457
Power World: |  | 11.0 (*.exe Date: 9/26/05)
File Location: |  | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2006\Winter06
Study Person: |  | JLJ5166
Temp: | 25 Fahrenheit |  | Average Puget Sound Net Area Load = 3470 MW
Gen. | Transfer | Worst | Limiting | PASTE RESULTS BELOW
Pattern | Limit | Contingency | Facility | 25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208)
1 | 3201.39 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G0 | 3217.76 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -847.17 | -846.68 | 3507.37 | 3201.39 | 1876.56
2 | 3205.23 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G1 | 3218.82 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -845.2 | -847.04 | 3444.12 | 3205.23 | 1899.98
3 | 3205.12 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G2 | 3223.85 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -843.98 | -846.4 | 3418.17 | 3205.12 | 1924.41
4 | 3240.22 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G3 | 3257.23 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -852.59 | -853.47 | 3514.27 | 3240.22 | 1960.9
5 | 3240.93 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G4 | 3257.7 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -851.76 | -852.59 | 3450.8 | 3240.93 | 1980.09
6 | 3251.02 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G5 | 3266.21 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -851.68 | -853.58 | 3424.86 | 3251.02 | 2019.09
7 | 3069.24 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G6 | 3082.61 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -841.87 | -842.83 | 3519.4 | 3069.24 | 1978.42
8 | 3073.47 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G7 | 3086.88 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -841.37 | -843.4 | 3455.74 | 3073.47 | 2021.86
9 | 3076.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G8 | 3089.68 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -838.82 | -840.76 | 3430.81 | 3076.55 | 2036.81
10 | 2520.43 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G9 | 2532.65 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 858.31 | 855.57 | 3523.64 | 2520.43 | 1863.92
11 | 2508.28 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G10 | 2520.56 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 855.45 | 852.77 | 3459.25 | 2508.28 | 1892.9
12 | 2521.41 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G11 | 2532.72 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 842.68 | 840.18 | 3434.32 | 2521.41 | 1926.21
13 | 2366.08 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G12 | 2376.08 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.03 | -855.61 | -856.28 | 3540.81 | 2366.08 | 1936.6
14 | 2374.97 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G13 | 2383.65 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.03 | -855.94 | -858.48 | 3478.71 | 2374.97 | 1957.6
15 | 2384.64 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G14 | 2392.77 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.03 | -855.33 | -857.79 | 3452.94 | 2384.64 | 2003.2
Temp: | 35 Fahrenheit |  | Average Puget Sound Net Area Load = 2914 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208)
1 | 3168.28 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G0 | 3183.3 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -830.21 | -831.17 | 2953.81 | 3168.28 | 1895.74
2 | 3178.53 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G1 | 3193.01 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -829.44 | -830.3 | 2890.77 | 3178.53 | 1928.88
3 | 3182.8 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G2 | 3196.36 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -828.05 | -830.41 | 2865.58 | 3182.8 | 1954.03
4 | 3207.83 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G3 | 3222.27 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -832.79 | -834.12 | 2957.79 | 3207.83 | 1984.03
5 | 3217.3 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G4 | 3232.07 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -833.5 | -834.55 | 2894.85 | 3217.3 | 2015.23
6 | 3210.91 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G5 | 3224.74 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -831.89 | -832.67 | 2870.82 | 3210.91 | 2038.69
7 | 2673.82 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G6 | 2683.13 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 847.93 | 845.45 | 2955.94 | 2673.82 | 1789.62
8 | 2678.63 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G7 | 2691.1 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 848.66 | 846.52 | 2892.07 | 2678.63 | 1826.23
9 | 2686.73 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G8 | 2698.34 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 847.87 | 845.93 | 2867.51 | 2686.73 | 1857.39
10 | 2375.04 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G9 | 2382.59 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -826.47 | -828.11 | 2967.39 | 2375.04 | 1838.72
11 | 2383.19 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G10 | 2389.82 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -829.83 | -831.39 | 2904.77 | 2383.19 | 1860.36
12 | 2387.12 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G11 | 2397.53 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -827.56 | -829.22 | 2878.65 | 2387.12 | 1894.75
13 | 2192.68 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G12 | 2200.58 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -826.9 | -829.1 | 2984.47 | 2192.68 | 1875.42
14 | 2207.71 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G13 | 2213.93 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -828.35 | -829.61 | 2922.45 | 2207.71 | 1912.1
15 | 2208.6 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G14 | 2215.87 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -823.84 | -824.94 | 2898.03 | 2208.6 | 1936.58
Temp: | 45 Fahrenheit |  | Average Puget Sound Net Area Load = 2621 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208)
1 | 3111.61 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G0 | 3126.08 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -795.37 | -795.63 | 2661.68 | 3111.61 | 1915.15
2 | 3120.51 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G1 | 3136.11 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -797.57 | -797.58 | 2598.95 | 3120.51 | 1934.05
3 | 3132.07 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G2 | 3144.57 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -802.44 | -802.37 | 2574.69 | 3132.07 | 1961.32
4 | 3080.2 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G3 | 3095.23 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -784.46 | -785.72 | 2666.46 | 3080.2 | 1937.32
5 | 3088.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G4 | 3102.94 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -783.73 | -785.18 | 2603.04 | 3088.95 | 1978.24
6 | 3096.65 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G5 | 3109.44 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -783.64 | -785.08 | 2578.91 | 3096.65 | 2006.59
7 | 2615.85 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G6 | 2628.3 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 821.62 | 819.6 | 2661.55 | 2615.85 | 1796.96
8 | 2621.88 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G7 | 2633.46 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 820.1 | 817.63 | 2598.95 | 2621.88 | 1826.06
9 | 2624.05 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G8 | 2634.91 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 816.73 | 813.92 | 2574.24 | 2624.05 | 1851.31
10 | 2237.92 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G9 | 2245.98 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -797.09 | -798.11 | 2673.38 | 2237.92 | 1797.31
11 | 2243.62 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G10 | 2251.5 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -797.31 | -798.34 | 2611.3 | 2243.62 | 1815.54
12 | 2247.38 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G11 | 2257.18 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -796.01 | -797.1 | 2586.4 | 2247.38 | 1844.49
13 | 2063.55 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G12 | 2071.42 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -793.3 | -794.51 | 2693.65 | 2063.55 | 1834.78
14 | 2069.46 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G13 | 2078.14 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -792.74 | -794 | 2631.05 | 2069.46 | 1868.15
15 | 2080.95 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G14 | 2088 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -794.27 | -795.38 | 2607.02 | 2080.95 | 1903.07
Temp: | 60 Fahrenheit |  | Average Puget Sound Net Area Load = 2973 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208)
1 | 3029.27 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G0 | 3043.06 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -758.87 | -760.51 | 3013.8 | 3029.27 | 1827.79
2 | 3040.88 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G1 | 3055.54 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -760.75 | -761.89 | 2951.17 | 3040.88 | 1860.15
3 | 3047.26 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G2 | 3061.62 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -766.06 | -767.94 | 2926.06 | 3047.26 | 1880.57
4 | 3036.73 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G3 | 3048.7 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -731.62 | -733.18 | 3018.04 | 3036.73 | 1906.74
5 | 3046.29 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G4 | 3058.51 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -732.91 | -733.43 | 2954.94 | 3046.29 | 1925.33
6 | 3047.76 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G5 | 3063.64 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -732.26 | -734.1 | 2929.67 | 3047.76 | 1951.35
7 | 2612.06 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G6 | 2621.14 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 789.45 | 776.81 | 3015.47 | 2612.06 | 1766.7
8 | 2614.99 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G7 | 2622.81 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 73.28 | 609.48 | 768.4 | 2952.57 | 2614.99 | 1792.34
9 | 2619.06 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G8 | 2630.74 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 788.2 | 776.72 | 2926.33 | 2619.06 | 1829.11
10 | 2198.04 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G9 | 2203.35 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -744.67 | -745.69 | 3027.01 | 2198.04 | 1736.7
11 | 2204.5 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G10 | 2210.95 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -745.2 | -746.15 | 2964.04 | 2204.5 | 1767.65
12 | 2209.34 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G11 | 2216.88 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -744.31 | -745.33 | 2939.35 | 2209.34 | 1794.8
13 | 1878.58 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G12 | 1884.33 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -739.36 | -741.81 | 3041.14 | 1878.58 | 1700.07
14 | 1981.48 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G13 | 1990.93 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -739.43 | -741.98 | 2982.77 | 1981.48 | 1782.97
15 | 2034.68 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G14 | 2043.9 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -741.94 | -743.16 | 2959.71 | 2034.68 | 1847.24
Temp: | 70 Fahrenheit |  | Average Puget Sound Net Area Load = 3532 MW
Gen. | Transfer | Worst | Limiting
Pattern | Limit | Contingency | Facility | 70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208)
1 | 2975.17 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G0 | 2987.36 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -739.59 | -739.69 | 3575.92 | 2975.17 | 1785.15
2 | 2977.96 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G1 | 2992.4 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -737.63 | -737.84 | 3512.41 | 2977.96 | 1812.32
3 | 2988.51 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G2 | 3001.8 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -737.97 | -738.09 | 3485.72 | 2988.51 | 1851.41
4 | 2997.42 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G3 | 3009.86 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -695.65 | -697.03 | 3579.75 | 2997.42 | 1860.78
5 | 3008.59 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G4 | 3021.09 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.93 | -697.95 | -699.36 | 3516.27 | 3008.59 | 1891.83
6 | 3018.21 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | G5 | 3031.04 | Branch BELLNGHM (40095) TO CUSTER W (40321) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -81.18 | -742.06 | -744.01 | 3490.02 | 3018.21 | 1936.93
7 | 2597.42 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G6 | 2608.41 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 776.03 | 751.97 | 3578.9 | 2597.42 | 1747.21
8 | 2599.58 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G7 | 2609.66 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 777.87 | 754.5 | 3513.95 | 2599.58 | 1780.84
9 | 2605.6 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G8 | 2614.25 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 73.28 | 601.49 | 748.38 | 3488.34 | 2605.6 | 1814.68
10 | 2162.99 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G9 | 2169.53 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -708.31 | -709.32 | 3589.07 | 2162.99 | 1701.16
11 | 2170.74 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G10 | 2176.42 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -707.87 | -709.49 | 3525.89 | 2170.74 | 1735.22
12 | 2174.94 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G11 | 2182.38 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -707.19 | -708.26 | 3499.43 | 2174.94 | 1768.15
13 | 1420.38 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G12 | 1425.93 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -703.52 | -706.12 | 3587.58 | 1420.38 | 1428.07
14 | 1536.08 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G13 | 1541.01 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -705.2 | -707.78 | 3527.85 | 1536.08 | 1524.35
15 | 1618.51 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | G14 | 1624.91 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.02 | -703.91 | -706.53 | 3505.5 | 1618.51 | 1592.93

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 457 | Murray-Custer 230kV line O/S
PSE Gen |  | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25 Fahrenheit | 3470.3473 | 3201.39 | 3205.23 | 3205.12 | 3240.22 | 3240.93 | 3251.02 | 3069.24 | 3073.47 | 3076.55 | 2520.43 | 2508.28 | 2521.41 | 2366.08 | 2374.97 | 2384.64
35 Fahrenheit | 2913.66 | 3168.28 | 3178.53 | 3182.8 | 3207.83 | 3217.3 | 3210.91 | 2673.82 | 2678.63 | 2686.73 | 2375.04 | 2383.19 | 2387.12 | 2192.68 | 2207.71 | 2208.6
45 Fahrenheit | 2621.418 | 3111.61 | 3120.51 | 3132.07 | 3080.2 | 3088.95 | 3096.65 | 2615.85 | 2621.88 | 2624.05 | 2237.92 | 2243.62 | 2247.38 | 2063.55 | 2069.46 | 2080.95
60 Fahrenheit | 2973.4713 | 3029.27 | 3040.88 | 3047.26 | 3036.73 | 3046.29 | 3047.76 | 2612.06 | 2614.99 | 2619.06 | 2198.04 | 2204.5 | 2209.34 | 1878.58 | 1981.48 | 2034.68
70 Fahrenheit | 3531.7733 | 2975.17 | 2977.96 | 2988.51 | 2997.42 | 3008.59 | 3018.21 | 2597.42 | 2599.58 | 2605.6 | 2162.99 | 2170.74 | 2174.94 | 1420.38 | 1536.08 | 1618.51