CONCURRENCE SHEET

SAMPLING REQUIREMENTS AND MAXIMUM ALLOWABLE IMPURITIES

FOR SSC FLUIDS AND FLUID SYSTEMS

Richard J. Gilbrech	04/27/00	Samuel Dale McCarty 		  04/27/00

NASA PROPULSION 	DATE		NASA CENTER OPERATIONS	  DATE

TEST DIRECTORATE			DIRECTORATE

John L. Gasery, Jr.	04/27/00	Issued CEF      		  04/28/00

NASA S&MA			DATE		CENTRAL ENGINEERING FILES	  DATE

CHANGE RECORD

| REVISION | DATE | PAGE | DESCRIPTION |
| --- | --- | --- | --- |
| H | 26 Apr 00 | All | Complete rewrite including title change. Implements change for waiver NA49 (dated 4/10/92) re: LOX moisture analyses. |

CONTENTS

Section	Page

1.0	INTRODUCTION	1

1.1	PURPOSE	1

1.2	SCOPE	1

1.3	RESPONSIBILITIES	1

1.3.1  SSC Activities	1

1.3.2  Quality Control	1

2.0	REFERENCED DOCUMENTS	2

3.0	GENERAL REQUIREMENTS	2

3.1	SAFETY	2

3.2	CONTROLLED ENVIRONMENTS	2

3.3	PROCEDURES	3

3.4	PERSONNEL INSTRUCTION	3

3.5	SAMPLING	3

3.6	CERTIFICATION RECORDS	3

3.7	REPORTS	3

3.8	ANALYSIS EQUIPMENT	4

4.0	MAXIMUM ALLOWABLE IMPURITIES	4

5.0	FLUID SUPPLY SYSTEM CLEANLINESS REQUIREMENTS	6

5.1	CERTIFICATION OF FLUID SYSTEMS	6

5.1.1	Initial Certification	6

5.1.2	Periodic Certification	6

5.1.3	Cylinder Supplied Gas Certification	7

5.1.4	Intermittent Certification of Usage Points	7

5.1.5	Testing, Drying and Preservation	7

5.2	RECERTIFICATION OF SYSTEMS	8

5.2.1	Required	8

5.2.2	Not Required	8

6.0	RECORDS AND FORMS	9

APPENDIX A  ACRONYMS AND ABBREVIATIONS	10

APPENDIX B  DEFINITIONS	11

TABLES

No.	Title	Page

1	PROPELLANTS AND PRESSURANTS MAXIMUM

ALLOWABLE IMPURITIES	4

# 1.0	INTRODUCTION

## 1.1	PURPOSE

This SSC standard (STD) establishes the maximum allowable impurities and sampling criteria for the fluids (gases, liquids) used as propellants and pressurants to clean, test, dry, or preserve test systems, subsystems, assemblies, components, and support equipment at Stennis Space Center (SSC).

## 1.2	SCOPE

This STD applies to site-wide facility systems (including offsite procurements) associated with the following services.

- High Pressure (Missile Grade) Air (HPA)

- Helium (He)

- Hydrogen, Gas (GH2) and Liquid (LH2)

- Nitrogen, Gas (GN2) and Liquid (LN2)

- Oxygen, Gas (GOX) and Liquid (LOX)

## 1.3	RESPONSIBILITIES

### 1.3.1  SSC Activities

This standard shall be implemented by NASA and Contractor personnel responsible for engineering design, manufacture, fabrication, analysis, inspection, or test operations.  NASA and the Contractor shall ensure compliance with the requirements of this standard through surveillance, auditing, and process verification.  The SSC Propulsion Test Directorate (PTD) Test Engineering Division and the Center Operations and Support Directorate Facilities Engineering Division (FED) are responsible for the content of this SSC STD.  Revision or cancellation of this STD shall be reviewed and approved as specified in SLP-05 and SSC STD 99-008.

### 1.3.2  Quality Control

NASA and/or Contractor QA are responsible for verifying the certification of systems.  The scheduling and the frequency of sampling shall be as indicated in Section 5.0.

# 2.0	REFERENCED DOCUMENTS

The referenced documents form an integral part of this standard and the latest issues shall apply unless otherwise specified.

FED-STD 209	Airborne Particulate Cleanliness Classes in Clean Rooms and Clean Zones

MIL-PRF-25508	Performance Specification, Propellant, Oxygen (Grade A)

MIL-PRF-27201	Performance Specification, Propellant, Hydrogen

MIL-PRF-27401	Performance Specification, Propellant Pressurizing Agent, Nitrogen (Grade B)

MIL-PRF-27407	Performance Specification, Propellant Pressurizing Agent, Helium (Grade A)

SLP-05		Document and Data Control

SLP-16		Control of Quality Records

SPG 8715.1	NASA/SSC Safety and Health Procedures and Guidelines

SSC STD 79-001	Surface Cleanliness Requirements for SSC Facility Fluid Systems

SSC STD 99-008	Guide for the Preparation, Approval and Release of SSC Standards

# GENERAL REQUIREMENTS

## 3.1	SAFETY

All procedures in this standard shall be performed in accordance with applicable requirements in SPG 8715.1.

## 3.2	CONTROLLED ENVIRONMENTS

Areas where particulate samples are analyzed shall conform to requirements for controlled environment areas per FED-STD-209.

## 3.3	PROCEDURES

The performing unit shall work to approved procedures for performing all sampling and analyses.  The NASA Monitor/Project Engineer and the NASA Quality Assurance Representative responsible for system integrity shall approve these procedures prior to work.

## 3.4	PERSONNEL INSTRUCTION

Personnel involved in obtaining and analyzing test samples shall be trained and/or certified and shall wear proper personal protective equipment (PPE).  Precautions must be taken to prevent introduction of contaminants into test samples.

## 3.5	SAMPLING

Samples shall be taken at the gas user interface point downstream of filters, regulators, valves, and any other equipment normally installed in a line.  If maintenance is performed without contamination control (79-001), or when contamination is suspected, then additional samples shall be taken at the next downstream user interface point.  Unless otherwise specified, gas sample volume shall be a minimum of 0.850 standard cubic meter.

## 3.6	CERTIFICATION RECORDS

Logs or databases shall be used to document all sampling at each use point in order to monitor trends and/or failures.  The data from these logs or databases will be maintained by the performing organization and may be used to determine if the sampling frequency as required by Section 5.1.2 needs to be modified.

## 3.7	REPORTS

All data gathered as a result of this standard shall be documented by the performing organization as designated by NASA QA, and shall include pertinent information recorded in logs or databases per section 3.6.

## 3.8	ANALYSIS EQUIPMENT

The equipment used to perform the analyses specified herein shall be approved for contamination testing by the performing organization as designated by NASA QA.

CAUTION

Prior to use, hand tools, materials, and equipment that may come into contact with significant surfaces or the service media shall be certified cleaned to the required system or component clean level in accordance with SSC STD 79-001.

# 4.0	MAXIMUM ALLOWABLE IMPURITIES

Requirements for maximum allowable impurities in the SSC Facility Transfer Systems at the receiving and user interface points are specified in Table 1.  (Note that service fluid purity levels differ from system and component clean levels specified by SSC STD 79-001.)

###### NOTE

The impurities in all fluid samples shall be analyzed in the gaseous state.

TABLE 1. PROPELLANTS AND PRESSURANTS MAXIMUM ALLOWABLE IMPURITIES

| PROPELLANT/PRESSURANT | REQUIREMENTS* |
| --- | --- |
| PARAMETER | RECEIVING | USER INTERFACe POINTS |
| HELIUM, GAS (He) Ref MIL-PRF-27407 (Grade A) |
| Purity Total Impurities Specific Impurities H2 N2 and Argon (receiving only) O2 and Argon (UIP only) H2O Hydrocarbon** Neon CO CO2 Particulate (gas) Particulate (liquid) | 99.995% He (min.) 50 N/A 1 14 3 9 (-61.1(C Dew Point) 5 23 1 1 N/A N/A | 99.994% He (min.) N/A 60 N/A 36 10 9 (-61.1(C Dew Point) 5 N/A N/A N/A 30(-100(: 25; >100(: 0 N/A |

TABLE 1. (Continued)

| PROPELLANT/PRESSURANT | REQUIREMENTS* |
| --- | --- |
| PARAMETER | RECEIVING | USER INTERFACe POINTS |
| HYDROGEN, GAS OR LIQUID (H2) Ref MIL-PRF-27201 |
| Purity Total Impurities Specific Impurities Selected Impurities: Parahydrogen N2, H2O, Hydrocarbon** O2 and Argon He CO2 plus CO Particulate (gas) Particulate (liquid) | 99.995% H2 (min.) 50 N/A 95.0% (liquid H2 only) 9 (-61.1(C Dew Point) 1 39 1 N/A N/A | 99.993% H2 (min.) N/A 70 N/A 20 (9 for H2O) (-61.1(C Dew Point) 5 45 N/A N/A N/A |
| NITROGEN, GAS OR LIQUID (N2) Ref MIL-PRF-27401 (Grade B) |
| Purity Total Impurities Specific Impurities Selected Impurities: O2 Hydrocarbon** H2O Particulate (gas) Particulate (liquid) | 99.99% N2 (min.) 100 N/A 50 5 6*** (-64.0(C Dew Point) N/A 1 mg/liter | 99.989% N2 (min.) N/A 111 100 5 6.0***(-64.0(C Dew Point) 30(-100(: 25; >100(: 0 N/A |
| OXYGEN, GAS (GOX) OR LIQUID (LOX) Ref MIL-PRF-25508 (Grade A) |
| Purity Total Impurities H2O Hydrocarbon** (C2H2) Acetylene Particulate (gas) Particulate (liquid) | 99.6% O2 (min.) 4000 3 (-69.0(C Dew Point) 50 0.25 ppm by weight N/A 1 mg/liter | 99.6% O2 (min.) N/A 20 (-55.2(C Dew Point) 50 N/A 30(-100(: 25; >100(: 0 N/A |
| HIGH PRESSURE AIR (HPA) |
| Purity H2O Hydrocarbon** Particulate (gas) Particulate (liquid) | N/A N/A N/A N/A N/A | 18% O2 (min.) 24 (-53.9(C Dew Point) 15 30(-100(: 25; >100(: 0 N/A |
| *Unless otherwise specified, requirement levels are total ppm by volume. **Total hydrocarbons expressed as Methane (CH4). ***The maximum H2O content is 6 ppm verified from the delivery manifest. This is less than the 11.5 ppm allowed in MIL-PRF-27401; however, historical data documents receipt of product within the lower limit. |

# 5.0	FLUID SUPPLY SYSTEM CLEANLINESS REQUIREMENTS

NOTE

Taking gas and/or liquid samples certifies systems, but the impurities in all fluid samples are analyzed in a gaseous state.

## 5.1	CERTIFICATION OF FLUID SYSTEMS

Certification of a fluid system shall require testing of the sample fluid as described in sections 5.1.1, 5.1.2 and 5.1.3.

### 5.1.1	Initial Certification

For certification of a new system, except cylinder supplied gas as defined in 5.1.3, the following requirements must be satisfied.

- Two consecutive samples at each user interface point in the system, taken 8 to 72 hours apart, shall comply with the user interface point requirements in Table 1.

- Two additional samples taken consecutively at 5-to-10-day intervals from each user interface point shall comply with the hydrocarbon, moisture and particulate user interface point requirements in Table 1.

### 5.1.2	Periodic Certification

After initial certification of a fluid system, periodic certifications are required as follows.

NOTE

When contamination is suspected, tests shall be performed to verify the impurity levels of the fluid. If these tests indicate that contamination levels exceed the requirements of 5.1.2-a or -b, then necessary corrective action shall be taken to clean and purge the system. If three consecutive samples fail, the system shall be certified as specified in 5.1.1.

- A supply fluid sample taken at the storage vessel, at 6-month intervals, shall comply with the user interface point requirements in Table 1.

- A sample taken at each user interface point at 3-month intervals shall comply with the hydrocarbon, moisture and particulate user interface point requirements in Table 1.

### 5.1.3	Cylinder Supplied Gas Certification

A gas system may consist of a cylinder, or a bank of cylinders, equipped with one or more user interface points.

- Initial certification shall require a sample obtained from the user interface point downstream from the cylinder gas system.  This sample must meet the contamination level user interface point requirements specified in Table 1.  The certification sample shall be taken with all bottle valves in the open position.

- Periodic certification is not required; however, following cylinder replacement or maintenance the provisions of Section 5.2 shall apply.

### 5.1.4	Intermittent Certification of Usage Points

User interface points shall be initially certified in accordance with 5.1.1, and periodically certified in accordance with 5.1.2. If an initially certified user interface point has not subsequently been periodically certified, then (a) a sample shall comply with the user interface requirements in Table 1; and (b) a second sample, taken 8 to 72 hours later, shall comply with the hydrocarbon, particulate and moisture user interface point requirements in Table 1.

### 5.1.5	Testing, Drying and Preservation

Gases used in the testing, drying and preservation of components, assemblies and support/test equipment shall meet the hydrocarbon, moisture and particulate user interface point requirements specified in Table 1. When used for testing, drying and preservation, gas user interface points that are used daily shall be tested weekly; if used intermittently, they shall be verified at the time of use.

## 5.2	RECERTIFICATION OF SYSTEMS

### 5.2.1	Required

A fluid system requires recertification when any part has been disassembled, recleaned, or modified. Recertification requires the following.

- If a positive pressure flow is not maintained, then a sample shall be obtained from the next downstream user interface point and tested to verify that all parameters comply with the user interface point requirements in Table 1.  If this test fails, then necessary corrective action shall be taken to clean and purge the system.  If three consecutive samples fail, the system shall be certified as specified in 5.1.1.

- If a positive flow is maintained, the media shall be tested to verify that hydrocarbon, moisture and particulate meet the user interface point requirements in Table 1. If this test fails, then necessary corrective action shall be taken to clean and purge the system.  If three consecutive samples fail, the system shall be certified as specified in 5.1.1.

### 5.2.2	Not Required

Recertification of a system is not required if all of the following are verified.

- A positive purge is maintained on the system when the system is disassembled.

- The system is disassembled for removal of a component or instrument for recertification or recalibration.

- The instrument or component is installed in an open loop configuration.

# 6.0	RECORDS AND FORMS

Records and forms identified in this standard shall be maintained in accordance with SLP-16.  For Quality Records refer to the SSC Master Records Index.  All forms are assumed to be the latest edition unless otherwise specified and may be obtained from the SSC Electronic Forms repository or from the NASA SSC Forms Management Officer.

# APPENDIX A

# ACRONYMS AND ABBREVIATIONS

C2H2		Acetylene

CO		Carbon Monoxide

CO2		Carbon Dioxide

FED		Federal

H2		Hydrogen

H2O		Water

He		Helium

LH		Liquid Hydrogen

LN		Liquid Nitrogen

LOX		Liquid Oxygen

IPA		Isopropyl Alcohol

MIL		Military

N2		Nitrogen

NASA		National Aeronautics and Space Administration

NVR		Nonvolatile Residue

O2		Oxygen

PRF		Performance (spec)

PPE		Personal Protective Equipment

ppm		Parts per million (p/m)

QA		Quality Assurance

SLP		System Level Procedure

Spec		Specification

SPG		SSC Procedures and Guidelines

SSC		Stennis Space Center

STD		Standard

UIP		User Interface Point

# APPENDIX B

# DEFINITIONS

Certification - The attesting (in writing) that requirements are verified as having been met.

Dew Point - The temperature at which a gas becomes saturated with water vapor and condensation begins (usually atmospheric pressure.)

Fluid – Any gas or liquid used to clean, test, dry, or preserve test systems, subsystems, assemblies, components, and support equipment.

Hydrocarbon - Any compound containing carbon and hydrogen bonds.

Interface Point – A specific location where systems intersect.

Micron - Dimension of length equal to 0.001 millimeter (0.0000394 inch).

Moisture - The residual liquid/gas resulting from cleaned components or systems, measured in parts-per-million (PPM).

Nonvolatile Residue (NVR) - The residue remaining after filtration and controlled evaporation of the final flushing solvent.  NVR is specified in milligrams (mg) per square meter or square foot of significant surface.  The predominant constituents of NVR are hydrocarbons.

Particulate - Fibers or units of matter with observable length, width, and thickness, usually measured in microns.

Significant Surfaces - Those surfaces of components, piece-parts, assemblies, subsystems, systems, and ground support equipment that come in contact with test solvents.

Standard Cubic Meter - Volume of one cubic meter of gas at one atmosphere of pressure (i.e., 760 mm of mercury) at 70ºF (21.1ºC).

APPENDIX B (continued)

DEFINITIONS

Testing - The process of acquiring and analyzing samples to determine the impurities and purity levels.

User Interface Point – Any specific service port where commodities are extracted from the system.  In some cases, the user interface point may be the specific port where commodities are injected into the system.

Verification - The process whereby one or more of the following methods is used for the purpose of certification: performing visual inspection, obtaining samples, analyzing/testing samples and reviewing inspection/test data.