## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 724
EPA ID No. | TXD008106999
Facility Name | Merichem Company
Facility Location
City | Houston
State | TX
Unit ID Name/No. | Boiler No. 4
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Nebraska Boiler Company (series WTS), 55,000 lb/hr of 240 psig, 68.5 MMBtu/hr; extended fire-box, single North America low NOx burner.
Capacity (MMBtu/hr) | 68
Soot Blowing | ?
APCS Detailed Acronym | Q/ME
APCS General Class | WQ
APCS Characteristics | Quench, wet scrubber, candlefilter-type mist eliminator (appears wet scrubber not operated during either testing. 5 tray, 2 stage scrubber/adsorber, CECO candlefilter-type mist eliminator
Hazardous Wastes | Liq
Haz Waste Description | Liquid chemical wastes, residue, liquid waste, nap fuel
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft)
Height (ft)
Gas velocity (ft/sec)
Gas temperature (°F)
Permitting Status | Tier III - As, Cr, Pb; Tier IA - Sb, Ba, Be, Cd, Hg, Ag, & chlorine
HWC Burn Status (Date if Terminated)

## cond
Cond Description
724C1
Report Name/Date | Recertification of Compliance (ReCOC) for Merichem; report provided begins at section 2.0 (no date)
Report Prepare | Merichem Company
Testing Firm | Focus Environmental, Inc (Ramcon Environmental Corporation)
Laboratory | Texas Oiltech Laboratories / Triangle Laboratories
Testing Dates | 1996-05-22
Cond Dates | 1996-05-01
Condition Descr | CoC; min combustion temp; Wet Scrubber not used
Content | PM, CO
724C2
Report Name/Date | Recertification of Compliance (ReCOC) for Merichem; report provided begins at section 2.0 (no date)
Report Prepare | Merichem Company
Testing Firm (coordinators) | Focus Environmental, Inc (Ramcon Environmental Corporation)
Testing Dates | July 16-17, 1996
Cond Dates | 1996-07-01
Condition Descr | CoC; max waste feed (spiked ash, chlorine, metals), Wet Scrubber not used
Content | PM, HCl/Cl2, metals, CO; ash, metals, chlorine in feeds

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
10 | 724C1 |  |  |  |  | R1 |  | R2 |  | R3 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0075 |  | 0.0019 |  | 0.0049 | 0.0047667
| CO (RA) | E1 | ppmv | y |  | 36.2 |  | 37.1 |  | 42.9 | 38.7333
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  |  | 13701 |  | 14321 |  | 13657 | 13893
| O2 |  | % |  |  | 5.5 |  | 4.8 |  | 4.6 | 4.9667
| Moisture |  | % |  |  | 9.39 |  | 8.78 |  | 9.44 | 9.2033
| Temperature |  | °F |  |  | 151 |  | 166 |  | 184 | 167
11 | 724C2 |  |  |  |  | R1 |  | R2 |  | R3 | Cond Avg
| PM | E1 | gr/dscf | y |  | 0.0051 |  | 0.0015 |  | 0.0031 | 0.0032333
| CO (RA) | E1 | ppmv | y |  | 10.1 |  | 10.2 |  | 10.1 | 10.1333
| HCl |  | ppmv | n |  | 13.3254 |  | 10.2909 |  | 3.1005 | 8.9056
| Cl2 |  | ppmv | n |  | 0.033921 |  | 0.033921 |  | 0.033921 | 0.033921
| Arsenic |  | lb/hr |  |  | 0.00026455 |  | 0.00019842 |  | 0.00019842
| Chromium |  | lb/hr |  |  | 0.0022267 |  | 0.0016535 |  | 0.001433
| Chromium (Hex) |  | lb/hr |  | nd | 1.89e-05 | nd | 2.24e-05 | nd | 2.11e-05
| Lead |  | lb/hr |  |  | 0.0020944 |  | 0.0012566 |  | 0.0012125
| Sampling Train | PM, HCl,Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  |  | 13701 |  | 14321 |  | 13657 | 13893
| O2 |  | % |  |  | 5.5 |  | 4.8 |  | 4.6 | 4.9667
| Moisture |  | % |  |  | 20.7 |  | 20.5 |  | 19.7 | 20.3
| Temperature |  | °F |  |  | 168 |  | 169 |  | 168 | 168.3333
| Sampling Train | Metals | E2
| Stack Gas Flowrate |  | dscfm |  |  | 13596 |  | 13912 |  | 13681 | 13729.6667
| O2 |  | % |  |  | 5.5 |  | 4.8 |  | 4.6 | 4.9667
| Moisture |  | % |  |  | 20.1 |  | 19.94 |  | 18.23 | 19.4233
| Temperature |  | °F |  |  | 171 |  | 170 |  | 170 | 170.3333
| HCl | E1 | ppmv | y |  | 12.0359 |  | 8.8934 |  | 2.6467 | 7.8587
| Cl2 | E1 | ppmv | y |  | 0.030639 |  | 0.029315 |  | 0.028957 | 0.029637
| Total Chlorine | E2 | ppmv | y |  | 12.0971 |  | 8.952 |  | 2.7047 | 7.9179
| Arsenic | E2 | µg/dscm | y |  | 4.6991 |  | 3.2955 |  | 3.3102 | 3.7683
| Chromium | E2 | µg/dscm | y |  | 39.5511 |  | 27.4623 |  | 23.9074 | 30.3069
| Chromium (Hex) | E2 | µg/dscm | y |  | 0.33571 |  | 0.37204 |  | 0.35202 | 0.35326
| Lead | E2 | µg/dscm | y |  | 37.2015 |  | 20.8713 |  | 20.2293 | 26.1007
| SVM | E2 | µg/dscm | y |  | 37.2015 |  | 20.8713 |  | 20.2293 | 26.1007 | Pb only
| LVM | E2 | µg/dscm | y |  | 44.2502 |  | 30.7577 |  | 27.2176 | 34.0752 | No Be

## feed
Feedstreams
* | 724C1 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Total | Total | Total | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW | Total | Total | Total | Total
| Feedstream Description |  |  | Waste Res |  | Waste Res |  | Waste Res |  | Waste Res | Total | Total | Total | Total
| Feed Rate | lb/hr |  | 1126.5606 |  | 1126.5606 |  | 1128.7652 |  | 1127.2955
| Heating Value | Btu/lb |  | 14975 |  | 14789 |  | 14818 |  | 14861
| Ash | g/hr |  | 220 |  | 250 |  | 67 |  | 180
| Gas Flowrate | dscfm |  | 13701 |  | 14321 |  | 13657 |  | 13893
| Oxygen | % |  | 5.5 |  | 4.8 |  | 4.6 |  | 4.9667
| Thermal Feedrate | MMBtu/hr |  | 16.8702 |  | 16.6607 |  | 16.726 |  | 16.7527 | 16.8702 | 16.6607 | 16.726 | 16.7527
| Estimated Firing Rate | MMBtu/hr | [8 empty] | 67.4176 | 73.6509 | 71.1031 | 70.7146
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 8.5414 |  | 8.8847 |  | 2.4664 |  | 6.6626 | 8.5414 | 8.8847 | 2.4664 | 6.6626
* | 724C2 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 |  | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Res |  | Waste Res |  | Waste Res |  | Waste Res | Spikes | Spikes | Spikes | Spikes |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 3791.9456 |  | 3836.038 |  | 3615.5761 |  | 3747.8533 | 80.1511 | 77.2057 | 76.5984 | 77.9851
| Heating Value | Btu/lb |  | 14767 |  | 14818 |  | 14784 |  | 14789.6667
| Specific Gravity |  |  | 1.1259 |  | 1.1269 |  | 1.127 |  | 1.1266
| Ash | g/hr |  | 2530 |  | 2770 |  | 140 |  | 1813.3333 | 8300 | 8200 | 8300 | 8266.6667
| Chlorine | g/hr |  | 37.2 |  | 37.4 |  | 43.4 |  | 39.3333 | 3268 | 2855 | 2785 | 2969.3333
| Antimony | g/hr | nd | 1.7 | nd | 1.7 | nd | 1.6 |  | 1.6667
| Arsenic | g/hr |  | 4.7 |  | 4.7 |  | 5.2 |  | 4.8667 | 9.1 | 9.1 | 9.1 | 9.1
| Barium | g/hr | nd | 1.7 | nd | 1.7 | nd | 1.6 |  | 1.6667
| Beryllium | g/hr | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Cadmium | g/hr | nd | 0.1 | nd | 0.1 | nd | 0.1 |  | 0.1
| Chromium | g/hr |  | 20.8 |  | 17 |  | 23.7 |  | 20.5 | 105.9 | 105.4 | 105.6 | 105.6333
| Mercury | g/hr | nd | 0.9 | nd | 0.9 | nd | 0.8 |  | 0.86667
| Lead | g/hr | nd | 1.7 | nd | 1.7 | nd | 1.6 |  | 1.6667 | 601.9 | 599.1 | 600 | 600.3333
| Silver | g/hr | nd | 1.7 | nd | 1.7 | nd | 1.6 |  | 1.6667
| Thallium | g/hr | nd | 1.7 | nd | 1.7 | nd | 1.6 |  | 1.6667
| Stack Gas Flowrate | dscfm |  | 13701 |  | 14321 |  | 13657 |  | 13893 | 13701 | 14321 | 13657 | 13893
| Oxygen | % |  | 5.5 |  | 4.8 |  | 4.6 |  | 4.9667 | 5.5 | 4.8 | 4.6 | 4.9667
| Thermal Feedrate | MMBtu/hr |  | 16.6359 |  | 16.6934 |  | 16.6877 |  | 16.6723 | [5 empty] | 16.6359 |  | 16.6934 |  | 16.6877 |  | 16.6723
| Estimated Firing Rate | MMBtu/hr | [13 empty] | 60.8933 |  | 63.6489 |  | 60.6978 |  | 61.7467
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 98.2261 |  | 98.4423 |  | 5.1537 |  | 67.274 | 322.2437 | 291.4176 | 305.5409 | 306.4007 | 0 | 420.4698 | 0 | 389.8599 | 0 | 310.6946 | 0 | 373.6748
| Chlorine | µg/dscm |  | 1444.2731 |  | 1329.1488 |  | 1597.6473 |  | 1457.0231 | 126878.6161 | 101463.0944 | 102521.8399 | 110287.8501 | 0 | 128322.8892 | 0 | 102792.2431 | 0 | 104119.4873 | 0 | 111744.8732
| Antimony | µg/dscm | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723 |  |  |  |  | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723
| Arsenic | µg/dscm |  | 182.4754 |  | 167.0321 |  | 191.4232 |  | 180.3102 | 353.3034 | 323.4025 | 334.9906 | 337.2321 | 0 | 535.7787 | 0 | 490.4346 | 0 | 526.4138 | 0 | 517.5424
| Barium | µg/dscm | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723 |  |  |  |  | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723
| Beryllium | µg/dscm | 100 | 3.8825 | 100 | 3.5539 | 100 | 3.6812 | 100 | 3.7058 |  |  |  |  | 100 | 3.8825 | 100 | 3.5539 | 100 | 3.6812 | 100 | 3.7058
| Cadmium | µg/dscm | 100 | 3.8825 | 100 | 3.5539 | 100 | 3.6812 | 100 | 3.7058 |  |  |  |  | 100 | 3.8825 | 100 | 3.5539 | 100 | 3.6812 | 100 | 3.7058
| Chromium | µg/dscm |  | 807.5506 |  | 604.1585 |  | 872.448 |  | 761.3857 | 4111.5194 | 3745.7829 | 3887.3631 | 3914.8885 | 0 | 4919.07 | 0 | 4349.9414 | 0 | 4759.8111 | 0 | 4676.2742
| Mercury | µg/dscm | 100 | 34.9421 | 100 | 31.9849 | 100 | 29.4497 | 100 | 32.1256 |  |  |  |  | 100 | 34.9421 | 100 | 31.9849 | 100 | 29.4497 | 100 | 32.1256
| Lead | µg/dscm | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723 | 23368.4942 | 21291.2574 | 22087.2905 | 22249.014 | 0.28164 | 23434.4959 | 0.28296 | 21351.6732 | 0.26596 | 22146.1899 | 0.27687 | 22310.7864
| Silver | µg/dscm | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723 |  |  |  |  | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723
| Thallium | µg/dscm | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723 |  |  |  |  | 100 | 66.0017 | 100 | 60.4159 | 100 | 58.8994 | 100 | 61.7723
| SVM | µg/dscm | 100 | 69.8842 | 100 | 63.9697 | 100 | 62.5807 | 100 | 65.4782 | 23368.4942 | 21291.2574 | 22087.2905 | 22249.014 | 0.29816 | 23438.3784 | 0.29955 | 21355.2271 | 0.28253 | 22149.8711 | 0.29343 | 22314.4922
| LVM | µg/dscm | 0.39063 | 993.9084 | 0.45872 | 774.7445 | 0.34483 | 1067.5524 | 0.39199 | 945.4017 | 4464.8228 | 4069.1854 | 4222.3537 | 4252.1206 | 0.071124 | 5458.7312 | 0.073368 | 4843.9299 | 0.069589 | 5289.9061 | 0.0713 | 5197.5224
BIF Feedrate Limits
| Antimony | g/hr |  | 725
| Arsenic | g/hr |  | Tier III
| Barium | g/hr |  | 121000
| Beryllium | g/hr |  | 1
| Cadmium | g/hr |  | 1.3
| Chromium | g/hr |  | Tier III
| Lead | g/hr |  | Tier III
| Mercury | g/hr |  | 193.3
| Silver | g/hr |  | 7248
| Thallium | g/hr |  | 1208
| Chlorine | g/hr |  | Tier III

## process
Process Information
|  | Run 1 | Run 2 | Run 3 | Cond Avg
724C10
Steam Flowrate | lb/hr | 19857 | 19639 | 20014 | 19836.6667
Comb Chamb Temp | °F | 1591 | 1606 | 1619 | 1605.3333
Candlefilter Mist Elim Temp | °F | 153 | 155 | 167 | 158.3333
Candlefilter Mist Elim Press Drop | in w.c. | 6.9 | 7.2 | 7.9 | 7.3333
724C11
Steam Flowrate | lb/hr | 53421 | 52851 | 50871 | 52381
Comb Chamb Temp | °F | 2473 | 2468 | 2450 | 2463.6667
Candlefilter Mist Elim Temp | °F | 178 | 187 | 178 | 181
Candlefilter Mist Elim Press Drop | in w.c. | 11.8 | 12.8 | 8.8 | 11.1333