## 25F nomo
Monroe-Sammamish #1 230kV Line & Custer-Ingledow #1 500kV Line
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 190
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3340.6127
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3232.63 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3043.67 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3145.24 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3354.53 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3043.67 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3553.94 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 3413.13 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3019.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3435.6 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 936.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3354.53 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3145.24 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3568.56 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3435.6 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3577.19 | T-1: Custer 500/230kV Bank#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3577.19 | T-1: Custer 500/230kV Bank#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
525 | 775 | 3553.94 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3120.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 3217.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 1041.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3120.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3232.63 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3019.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3413.13 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1150.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3568.56 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1041.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3217.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 936.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1150.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Monroe-Sammamish #1 230kV Line & Custer-Ingledow #1 500kV Line
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 190
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2652.108
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3257.14 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 3058.97 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3176.91 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3340.94 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3058.97 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3518.09 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 3389.46 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2293.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3422.7 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 182.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3340.94 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3176.91 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3548.99 | T-1: Custer 500/230kV Bank#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3422.7 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3528.49 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3528.49 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
525 | 775 | 3518.09 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 2401.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2500.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 272.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2401.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3257.14 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2293.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3389.46 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 390.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3548.99 | T-1: Custer 500/230kV Bank#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1400 | 460 | 272.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2500.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 182.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 390.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Monroe-Sammamish #1 230kV Line & Custer-Ingledow #1 500kV Line
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 190
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2407.808
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3247.14 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2978.93 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 3194.51 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 3073.15 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2978.93 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3397.26 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 3328.81 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1324 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3333.81 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -1060.59 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3073.15 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3194.51 | BFR: Horse Ranch 230kV Bus | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 3418.76 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3333.81 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3416.65 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3416.65 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
525 | 775 | 3397.26 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 1425.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1542.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -1016.92 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1425.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3247.14 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1324 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3328.81 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -896.56 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3418.76 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1400 | 460 | -1016.92 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1542.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -1060.59 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -896.56 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Monroe-Sammamish #1 230kV Line & Custer-Ingledow #1 500kV Line
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 190
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2926.0927
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2742.3 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2788.57 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2761.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2871.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2788.57 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 3081.67 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2840.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1762.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2862.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -452.45 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2871.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2761.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3017.87 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2862.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3020.54 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3020.54 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3081.67 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 1854.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1975.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -421.43 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1854.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2742.3 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1762.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2840.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -370.58 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3017.87 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -421.43 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1975.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -452.45 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -370.58 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Monroe-Sammamish #1 230kV Line & Custer-Ingledow #1 500kV Line
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 190
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3277.866
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2627.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2633.12 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2622.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2765.99 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2633.12 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2937.92 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2737.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1829.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2754.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -372.49 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2765.99 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2622.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2891.25 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2754.44 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2928.18 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2928.18 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2937.92 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 1940.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2055.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -273.13 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1940.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2627.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1829.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2737.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -234.33 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2891.25 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -273.13 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2055.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -372.49 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -234.33 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Monroe-Sammamish #1 230kV Line & Custer-Ingledow #1 500kV Line
G0 | 3232.63 | 3257.14 | 3247.14 | 2742.3 | 2627.14
G1 | 3145.24 | 3176.91 | 3194.51 | 2761.19 | 2622.18 | Season/Year: | WINTER 2009
G2 | 3043.67 | 3058.97 | 2978.93 | 2788.57 | 2633.12 | Direction: | South-to-North (SN)
G3 | 3413.13 | 3389.46 | 3328.81 | 2840.41 | 2737.57 | Case Loads: | Light Loads
G4 | 3435.6 | 3422.7 | 3333.81 | 2862.38 | 2754.44 | Outage: | 190
G5 | 3354.53 | 3340.94 | 3073.15 | 2871.91 | 2765.99 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3568.56 | 3548.99 | 3418.76 | 3017.87 | 2891.25 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3577.19 | 3528.49 | 3416.65 | 3020.54 | 2928.18 | Study Person: | JGO7470
G8 | 3553.94 | 3518.09 | 3397.26 | 3081.67 | 2937.92 | Source: | 190WINTER09v2SNL(COV-CRES BYP)
G9 | 3217.82 | 2500.72 | 1542.02 | 1975.04 | 2055.71
G10 | 3120.59 | 2401.81 | 1425.95 | 1854.52 | 1940.95
G11 | 3019.13 | 2293.87 | 1324 | 1762.83 | 1829.59
G12 | 1150.77 | 390.39 | -896.56 | -370.58 | -234.33
G13 | 1041.45 | 272.6 | -1016.92 | -421.43 | -273.13
G14 | 936.95 | 182.92 | -1060.59 | -452.45 | -372.49
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 190 | Monroe-Sammamish #1 230kV Line & Custer-Ingledow #1 500kV Line
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3340.6127 | 3232.63 | 3145.24 | 3043.67 | 3413.13 | 3435.6 | 3354.53 | 3568.56 | 3577.19 | 3553.94 | 3217.82 | 3120.59 | 3019.13 | 1150.77 | 1041.45 | 936.95
35F | 2652.108 | 3257.14 | 3176.91 | 3058.97 | 3389.46 | 3422.7 | 3340.94 | 3548.99 | 3528.49 | 3518.09 | 2500.72 | 2401.81 | 2293.87 | 390.39 | 272.6 | 182.92
45F | 2407.808 | 3247.14 | 3194.51 | 2978.93 | 3328.81 | 3333.81 | 3073.15 | 3418.76 | 3416.65 | 3397.26 | 1542.02 | 1425.95 | 1324 | -896.56 | -1016.92 | -1060.59
60F | 2926.0927 | 2742.3 | 2761.19 | 2788.57 | 2840.41 | 2862.38 | 2871.91 | 3017.87 | 3020.54 | 3081.67 | 1975.04 | 1854.52 | 1762.83 | -370.58 | -421.43 | -452.45
70F | 3277.866 | 2627.14 | 2622.18 | 2633.12 | 2737.57 | 2754.44 | 2765.99 | 2891.25 | 2928.18 | 2937.92 | 2055.71 | 1940.95 | 1829.59 | -234.33 | -273.13 | -372.49

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3232.74 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 512.31 | 512.01 | 3412.24 | 3232.63 | -2040.06 | FULL
G1 | 3145.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 520.02 | 519.82 | 3334.32 | 3145.24 | -1954.6 | FULL
G2 | 3043.7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 518.85 | 519.07 | 3337.31 | 3043.67 | -1858.05 | FULL
G3 | 3413.29 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -65.54 | -2645.86 | -2646.24 | 3411.69 | 3413.13 | -2077.72 | CTG_FAIL_IN_FULL
G4 | 3435.81 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -65.54 | -2644.77 | -2646.55 | 3342.44 | 3435.6 | -2053.98 | CTG_FAIL_IN_FULL
G5 | 3354.68 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 529.02 | 529.25 | 3349.36 | 3354.53 | -1979.32 | FULL
G6 | 3568.7 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -65.54 | -2639.58 | -2639.94 | 3408.11 | 3568.56 | -2040.19 | CTG_FAIL_IN_FULL
G7 | 3577.33 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | T-1: Custer 500/230kV Bank#2 | 100 | 3614.51 | 3615.47 | 3337.73 | 3577.19 | -2018.2 | FULL
G8 | 3554.59 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3591.7 | 3593.38 | 3350.58 | 3553.94 | -1973.06 | FULL
G9 | 3217.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -483.58 | -483.56 | 3371.82 | 3217.82 | -1629.69 | FULL
G10 | 3120.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -481.1 | -481.27 | 3297.06 | 3120.59 | -1540.53 | FULL
G11 | 3018.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -481.89 | -481.87 | 3306.36 | 3019.13 | -1446.03 | FULL
G12 | 1151.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -458.3 | -458.2 | 3322.97 | 1150.77 | -265.52 | FULL
G13 | 1042.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -457.44 | -457.35 | 3255.95 | 1041.45 | -172.5 | FULL
G14 | 936.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -457.24 | -457.17 | 3271.25 | 936.95 | -84.41 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3257.6 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 510.36 | 510.65 | 2723.83 | 3257.14 | -1997.09 | FULL
G1 | 3178.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 514.79 | 515.08 | 2647.27 | 3176.91 | -1925.24 | FULL
G2 | 3059.4 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 509.74 | 509.37 | 2652.46 | 3058.97 | -1830.18 | FULL
G3 | 3390.73 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -65.54 | -2586.48 | -2587.64 | 2721.29 | 3389.46 | -2025.02 | CTG_FAIL_IN_FULL
G4 | 3422.95 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -65.54 | -2594.73 | -2596.47 | 2652.01 | 3422.7 | -2010.73 | CTG_FAIL_IN_FULL
G5 | 3342.53 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 515.5 | 515.6 | 2663.15 | 3340.94 | -1921.25 | FULL
G6 | 3550.05 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | T-1: Custer 500/230kV Bank#2 | 100 | 3585.52 | 3583.8 | 2717.32 | 3548.99 | -2000.02 | FULL
G7 | 3530.2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3565.56 | 3564.16 | 2648.07 | 3528.49 | -1947.64 | FULL
G8 | 3519.8 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3555.18 | 3553.56 | 2660.92 | 3518.09 | -1911.04 | FULL
G9 | 2500.96 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -464.24 | -464.23 | 2663.02 | 2500.72 | -1158.93 | FULL
G10 | 2402.8 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -464.93 | -464.83 | 2592.63 | 2401.81 | -1065.46 | FULL
G11 | 2294.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -462.28 | -462.23 | 2604.27 | 2293.87 | -975.74 | FULL
G12 | 390.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -444.77 | -444.67 | 2648.43 | 390.39 | 217.4 | FULL
G13 | 273.84 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -445.07 | -445.07 | 2584.46 | 272.6 | 313.79 | FULL
G14 | 183.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -446.36 | -446.46 | 2602.49 | 182.92 | 395.32 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3248.17 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -65.54 | -2521.92 | -2521.32 | 2473.85 | 3247.14 | -1969.47 | CTG_FAIL_IN_FULL
G1 | 3194.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 12.69 | 490.74 | 490.83 | 2403.71 | 3194.51 | -1912.97 | FULL
G2 | 2978.6 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -14.45 | -453.91 | -453.64 | 2406.79 | 2978.93 | -1750.05 | FULL
G3 | 3328.4 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -65.54 | -2516.07 | -2515.69 | 2472.88 | 3328.81 | -1952.02 | CTG_FAIL_IN_FULL
G4 | 3333.49 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -65.54 | -2503.11 | -2502.8 | 2404.38 | 3333.81 | -1922.63 | CTG_FAIL_IN_FULL
G5 | 3073.53 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -14.45 | -455.73 | -450.47 | 2408.1 | 3073.15 | -1738.27 | FULL
G6 | 3420.39 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3453.07 | 3451.97 | 2468.18 | 3418.76 | -1885.77 | FULL
G7 | 3417.1 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3449.76 | 3448.67 | 2399 | 3416.65 | -1850.26 | FULL
G8 | 3397.4 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3429.93 | 3428.73 | 2412.21 | 3397.26 | -1801.64 | FULL
G9 | 1542.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -415.85 | -415.75 | 2404.01 | 1542.02 | -569.9 | FULL
G10 | 1428.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -414.42 | -414.32 | 2336.02 | 1425.95 | -472.81 | FULL
G11 | 1325.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -413.85 | -413.75 | 2350.75 | 1324 | -384.59 | FULL
G12 | -895.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -422.56 | -422.51 | 2427.45 | -896.56 | 966.46 | FULL
G13 | -1016.23 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -422.34 | -422.25 | 2365.27 | -1016.92 | 1063.05 | FULL
G14 | -1061.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -423.9 | -423.85 | 2384.52 | -1060.59 | 1110.89 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2742.5 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2185.95 | -2187.77 | 2986.17 | 2742.3 | -1706.17 | FULL
G1 | 2761.39 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2187.88 | -2186.19 | 2916.63 | 2761.19 | -1688.42 | FULL
G2 | 2788.75 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -68.99 | -2202.11 | -2200.88 | 2929.05 | 2788.57 | -1676.43 | FULL
G3 | 2838.92 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2180.93 | -2182.89 | 2985.13 | 2840.41 | -1700.99 | FULL
G4 | 2862.51 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2186.34 | -2187.87 | 2917.01 | 2862.38 | -1686.68 | FULL
G5 | 2872.05 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2171.77 | -2170.35 | 2930.02 | 2871.91 | -1649.13 | FULL
G6 | 3017.25 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -68.99 | -2200.86 | -2198.81 | 2984.18 | 3017.87 | -1681.61 | FULL
G7 | 3019.91 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -68.99 | -2191.35 | -2192.38 | 2915.17 | 3020.54 | -1658.76 | FULL
G8 | 3081.17 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -68.99 | -2227.58 | -2229.48 | 2927.76 | 3081.67 | -1663.13 | FULL
G9 | 1975.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -425.62 | -425.53 | 2938.83 | 1975.04 | -854.21 | FULL
G10 | 1854.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -422.6 | -422.52 | 2868.83 | 1854.52 | -754.41 | FULL
G11 | 1763.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -421.86 | -421.79 | 2880.94 | 1762.83 | -670.51 | FULL
G12 | -370.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -416.28 | -416.19 | 2941.06 | -370.58 | 639.92 | FULL
G13 | -421.31 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -418.04 | -417.95 | 2876.35 | -421.43 | 698.61 | FULL
G14 | -452.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -420.52 | -420.56 | 2894.26 | -452.45 | 746 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2627.47 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2120.7 | -2119.44 | 3335.91 | 2627.14 | -1638.6 | FULL
G1 | 2622.56 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2110.13 | -2111.11 | 3265.71 | 2622.18 | -1608.16 | FULL
G2 | 2633.33 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2095.01 | -2095.3 | 3279.53 | 2633.12 | -1582.22 | FULL
G3 | 2738.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2130.49 | -2131.81 | 3335.27 | 2737.57 | -1639.94 | FULL
G4 | 2755.05 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2123.7 | -2122.85 | 3265.49 | 2754.44 | -1612.4 | FULL
G5 | 2766.28 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.39 | -2132.68 | -2131.1 | 3277.86 | 2765.99 | -1600.57 | FULL
G6 | 2892.01 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -68.99 | -2129.51 | -2128.5 | 3333.65 | 2891.25 | -1612.83 | FULL
G7 | 2928.51 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -68.99 | -2148.59 | -2149.47 | 3264.59 | 2928.18 | -1603.1 | FULL
G8 | 2938.37 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | -68.99 | -2141.07 | -2139.68 | 3277.74 | 2937.92 | -1573.68 | FULL
G9 | 2056.58 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -425.58 | -425.48 | 3296.78 | 2055.71 | -900.87 | FULL
G10 | 1941.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -423.31 | -423.18 | 3225.92 | 1940.95 | -805.44 | FULL
G11 | 1829.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.63 | -421.42 | -421.35 | 3238.01 | 1829.59 | -710.66 | FULL
G12 | -234.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -416.51 | -416.47 | 3294.9 | -234.33 | 561.65 | FULL
G13 | -273.16 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -418.66 | -418.61 | 3229.47 | -273.13 | 613.53 | FULL
G14 | -372.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -4.06 | -419.04 | -418.97 | 3247.16 | -372.49 | 697.79 | FULL
190WINTER09v2SNL(COV-CRES BYP)