July 22, 1994

Contract # TW0592

SPECIAL SPECIFICATION

SECTION 15865

AXIAL FANS

Page

PART 1 - GENERAL

1.01 Description..	2

1.02Related Work..	2

1.03Quality Assurance...	2

1.04References.	2

1.05Submittals..	3

1.06 Delivery, Storage, and Handling..	4

1.07Sequencing..	4

1.08 Extra Materials..	4

PART 2 - PRODUCTS

2.01Acceptable Manufacturers..	5

2.02 Fans.	5

2.03 Vaneaxial Fans..	6

2.04 Motors...	7

PART 3 - EXECUTION

3.01 Inspection...	10

3.02 Installation/Application/Erection..	10

3.03 Field Quality Control...	10

3.04 Adjusting and Cleaning..	11

3.05 Commissioning....	11

3.06 Demonstration.	11

SPECIAL SPECIFICATION

SECTION 15865

AXIAL FANS

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This Section includes vaneaxial-type axial fans.

1.02	RELATED WORK

A.  	Section 01300

B.  	Section 15010

C.  	Section 15200

D.  	Section 15901

E.  	Section 15995

F.  	Division 16 Section "Circuit and Motor Disconnects" for disconnect switches.

G.  	Division 16 Section "Motor Controllers" for motor starters.

H.  	Division 16 Section "Motor Control Centers" for starters and fusible switches.

1.03	QUALITY ASSURANCE

A.  	Provide motors and electrical accessories that comply with National Electrical Manufacturers Association (NEMA) standards.

B.  	Provide components according to National Fire Protection Association (NFPA) 70 "National Electrical Code."

1.04	REFERENCES

A.  	Anti-Friction Bearing Manufacturers Association (AFBMA) Standard 9 for ball bearings

B.  	AFBMA Standard 11 for roller bearings

C.  	Air Movement Contractors Association (AMCA) Standard 210/American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) Standard 51, Laboratory Methods of Testing Fans for Rating

D.  	AMCA Standard 300, Test Code for Sound Rating

E.  	AMCA Standard 301, Method for Calculating Fan Sound Ratings From Laboratory Test Data

F.  	Institute of Electrical and Electronic Engineers (IEEE) Standard 112, Test Method B

G.  	NEMA 1

H.  	NEMA Standard MG 1

I.  	NFPA 70, National Electrical Code

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15010, and Section 01300.

B.  	Provide product data for selected models, including specialties, accessories, and the following:

1.  	Certified fan performance curves with system operating conditions indicated.  All performance curves shall be corrected for an altitude of 5,200 ft.

2.  	Certified fan sound power ratings.

3.  	Motor ratings and electrical characteristics plus motor and fan accessories.

4.  	Materials gages and finishes, including color charts.

C.  	Provide shop drawings from manufacturer detailing equipment assemblies and indicating dimensions, weights, required clearances, components, and location and size of field connections.

D.  	Provide wiring diagrams that detail power, signal, and control wiring. Differentiate between manufacturer-installed wiring and field- installed wiring.

E.  	Provide maintenance data in operating and maintenance manuals as specified in Section 01300.

1.06	DELIVERY, STORAGE, AND HANDLING

A.  	Deliver fan units as a factory-assembled unit to the extent allowable by shipping limitations, with protective crating and covering.

B.  	See Section 15010.

1.07	SEQUENCING

A.  	Coordinate the size and location of structural steel support members.

1.08	EXTRA MATERIALS

A.  	Furnish one additional complete set of belts for each belt-driven fan.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Provide products by one of the following:

1.  	Vaneaxial Fans:

a. 	Trane Co.

b. 	Barry Blower

c. 	Peerless

2.02	FANS

A.  	Provide fans that are factory fabricated and assembled, factory tested, and factory finished with indicated capacities and characteristics.

B.  	Fans and Shafts:  Statically and dynamically balanced and designed for continuous operation at the maximum rated fan speed and motor horsepower.

1.  	Fan Shaft:  Turned, ground, and polished steel designed to operate at no more than 70 percent of the first critical speed at the top of the speed range of the fan's class.

C.  	Belt Drives:  Factory mounted, with final alignment and belt adjustment made after installation.

1.  	Service Factor:  1.4.

D.  	Belts:  Oil-resistant, nonsparking, and nonstatic.

E.  	Motors and Fan Wheel Pulleys:  Adjustable pitch for use with motors through 15 horsepower (hp); fixed pitch for use with motors larger than 15 hp. Select pulley so that pitch adjustment is at the middle of the adjustment range at fan design conditions.

1.  	Belt Guards:  Provide steel belt guards for motors mounted on the outside of the fan cabinet.

F.  	Shaft Bearings:  Provide type indicated, having a median life "Rating Life" (AFBMA (L50)) of 200,000, calculated in accordance with AFBMA Standard 9 for ball bearings and AFBMA Standard 11 for roller bearings.

G.  	Factory Finish:  The following finishes are required:

1.  	Sheet Metal Parts:  Prime coating prior to final assembly.

2.  	Exterior Surfaces:  Baked-enamel finish coat after assembly.

H.  	The following factory tests are required:

1.  	Sound Power Level Ratings:  Comply with AMCA Standard 301 "Method for Calculating Fan Sound Ratings From Laboratory Test Data." Test fans in accordance with AMCA Standard 300 "Test Code for Sound Rating." Fans shall be licensed to bear the AMCA Certified Sound Ratings Seal.

2.  	Fan Performance Ratings:  Establish flow rate, pressure, power, air density, speed of rotation, and efficiency shall be factory tested and ratings in accordance with AMCA Standard 210/ASHRAE Standard 51 - Laboratory Methods of Testing Fans for Rating.

2.03	VANEAXIAL FANS

A.  	General Description:  Belt-driven vaneaxial fans consisting of fan wheel and housing, straightening vane section, factory-mounted motor, an inlet cone section, and accessories as scheduled on the Drawings.

B.  	Housings:  Steel housing, 14-gage minimum, with inlet bell and diffuser sections.

1.  	Inlet and Outlet Connections:  Outer mounting frame and companion flanges; inlet cone shall be welded to the fan raceway.

2.  	Guide Vane Section:  Integral guide vanes downstream of the fan wheel designed to straighten the airflow.

C.  	Wheels:  Cast-aluminum, axial-flow type, with airfoil-shaped blades mounted on cast-iron wheel plate keyed to shaft with solid steel key.

D.  	Fan Hub and Blade Bearing Assemblies:  Cast aluminum, machined and fitted with threaded bearing wells to receive blade bearing assemblies.

1.  	Blades:  Replaceable, cast aluminum; factory-mounted and balanced to the hub assembly.

2.  	Fan Shaft:  Turned, ground, and polished steel.

3. 	Shaft Bearings:  Grease-lubricated, pillow block type; ball-bearings with double-locking collars and two-piece, cast-iron housing.

E.  	Belt-Drive Units:  Provide enclosure around belts and sheaves.

1.  	Motor Mounting:  Adjustable base.

2.  	Sheaves:  Adjustable.

3.  	Belts:  Oil-resistant, nonsparking, and nonstatic.

F.  	Accessories:  The following accessories are required as indicated:

1.  	Companion Flanges:  Rolled-steel flanges.

2.04	MOTORS

A.  	General

1.  	Apply requirements below to motors covered by this Section except as otherwise indicated.

2.  	Motors 1 horsepower (hp) and Larger:  Polyphase.

3.  	Frequency Rating:  60 Hz.

4.  	Voltage Rating:  Determined by voltage of circuit to which motor is connected for the following motor voltage ratings (utilization voltages):

a. 	Motors smaller than 1 hp: 120 V circuit, 115 V - motor rating.

b. 	Motors 1 hp and larger: 480 V circuit, 460 V - motor rating.

5.  	Service factors indicated for motors are minimum values and apply at frequency and utilization voltage at which motor is connected.  Provide motors which will not operate in service factor range when supply voltage is within 10 percent of motor voltage rating.

6.  	Provide permanent-split capacitor classification motors for shaft-mounted fans and capacitor start classification for belted fans.

7.  	Capacity:  Minimum size as indicated.  If not indicated, sufficient to start and operate connected loads at designated speeds in indicated environment, and with indicated operating sequence, without exceeding nameplate ratings.  Provide motors rated for continuous duty at 100 percent of rated capacity.

8.  	Temperature Rise:  50 degree (deg) Celsius (C) maximum temperature rise at 40 deg C ambient for continuous duty at full load (Class A Insulation).

9.  	Motor Speed:  Single, multiple, or variable as indicated.

10. 	Motor Construction:  NEMA Standard MG 1.

a. 	Bases:  Adjustable.

b. 	Bearings:  The following features are required:

1)  	Ball or roller bearings with inner and outer shaft seals.

2)  	Grease lubricated.

3)  		Designed to resist thrust loading where belt drives or other drives produce lateral or axial thrust in motor.

c. 		Enclosure Type:  The following features are required:

1)  		Open drip-proof motors where satisfactorily housed or remotely located during operation.

2)  		Guarded drip-proof motors where exposed to contact by employees or building occupants.

d. 		Noise rating:  Quiet.

e. 		Nameplate:  Indicate the full identification of manufacturer, ratings, characteristics, construction, and special features.

11. 	Starters, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16.

B.  	Polyphase Motors

1.  	Squirrel-cage, induction-type, general-purpose conforming to the following requirements except as otherwise indicated.

2.  	NEMA Design Letter Designation:  "B," unless specifically designated "C" for high starting torque.

3. 	Service Factor:  1.15.

4.  	Energy Efficient Motors:  Nominal efficiency equal to or greater than that stated in NEMA MG 1, table 12-6C for that type and rating of motor.

5.  	Variable Speed Motors for Use With Solid-State Drives:  Energy efficient, squirrel-cage induction, design B units with ratings, characteristics, and features coordinated with and approved by drive manufacturer.

6.  	Internal Thermal Overload Protection For Motors:  For motors so indicated, protection automatically opens control circuit arranged for external connection.  Protection operates when winding temperature exceeds safe value calibrated to the temperature rating of the motor insulation.

7.  	Bearings:  Double-shielded, pre-lubricated ball bearings suitable for radial and thrust loading of the application, unless noted otherwise.

PART 3 - EXECUTION

3.01	INSPECTION

A.  	Inspect areas and conditions, with Installer present, for compliance with requirements for installation tolerances, housekeeping pads, and other conditions affecting performance of fans.

B.  	Do not proceed until unsatisfactory conditions have been corrected.

3.02	INSTALLATION/APPLICATION/ERECTION

A.  	General

1.  	Install fans level and plumb, in accordance with manufacturer's written instructions.  Support units as described below, using the vibration control devices indicated.  Vibration control devices are specified in Section 15200.

2.  	Arrange installation of units to provide access space around units for service and maintenance.

B. 	Connections

1.  	Duct installations and connections are specified in other Division 15 sections.  Make final duct connections with flexible connections.

2.  	Electrical Connections:  The following requirements apply:

a. 	Electrical power wiring is specified in Division 16.

b. 	Temperature control wiring and interlock wiring is specified in Section 13943.

c. 	Grounding:  Connect unit components to ground in accordance with the National Electrical Code.

3.03	FIELD QUALITY CONTROL

A. 	Arrange and pay for a factory- authorized service representative to perform the following:

1.  	Inspect the field assembly of components and installation of fans including ductwork and electrical connections.

2.  	Prepare a written report on findings and recommended corrective actions.

3.04	ADJUSTING AND CLEANING

A.  	Adjust damper linkages for proper damper operation.

B.  	Clean unit cabinet interiors to remove foreign material and construction dirt and dust.  Vacuum clean fan wheel and cabinet.

3.05	COMMISSIONING

A.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.  Perform forms tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

3.06	DEMONSTRATION

A.  Provide a factory-authorized service representative to start-up equipment, to demonstrate operation, and to train personnel.

B.  	See Section 15995.

END OF SECTION