SPILL PREVENTION, CONTROL, AND COUNTERMEASURE PLAN

National Weather Service

Raleigh Forecast Office

1005 Capability Drive, Suite 300

Raleigh, North Carolina 27606

MANAGEMENT APPROVAL

This spill prevention, control, and countermeasure (SPCC) plan has been carefully thought out, was prepared in accordance with good engineering practices, and has the full approval of National Weather Service management at a level with the authority to commit the necessary resources for its implementation. In accordance with Title 40 of the Code of Federal Regulations Subpart 112.5 (40 CFR 112.5), this SPCC plan will be updated within 1 year of a change in facility design, construction, operation, or maintenance that materially affects the facility’s potential for discharge of oil to navigable waters or adjoining shorelines.  This plan will be implemented as described herein and will be reviewed and evaluated at least every 3 years to include more effective prevention and control technologies, if available.  This current plan replaces plans reviewed and/or revised every 3 years since the facility began operations in 1992.

Karl Lenzen, Environmental Focal Point

Printed Name and Title of Responsible Manager

Signature of Responsible Manager and Date Signed

PLAN CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of 40 CFR 112, I attest that this SPCC plan has been prepared in accordance with good engineering practices.

| Printed Name of Registered Engineer |  |
| --- | --- |
| Signature of Registered Engineer and Date Signed |  |
| Registration No. | State |

CONTENTS

Page

A.	GENERAL FACILITY INFORMATION	1

B.	SCHEDULE FOR IMPLEMENTATION - 112.7	1

C.	SPILL HISTORY - 112.7(a)	2

D.	POTENTIAL SPILLS -- PREDICTION AND CONTROL	2

1.	Facility Description	2

2.	Prediction of Potential Spills - 112.7(b)	2

3.	Spill Controls - 112.7(c)	3

G.	FACILITY TRANSFER OPERATIONS, PUMPING, AND IN-PLANT PROCESS - 
112.7(e)(3)	4

H.	FACILITY TANKER TRUCK UNLOADING RACK - 112.7(e)(4)	5

I.	INSPECTIONS AND RECORDS - 112.7(e)(8)	5

J.	SECURITY - 112.7(e)(9)	5

K.	PERSONNEL, TRAINING, AND SPILL PREVENTION PROCEDURES - 112.7(e)(10)	5

L.	SUBSTANTIAL HARM CRITERIA EVALAUATION – 112.20 (f)(1)	6

M.	SPILL COUNTERMEASURES AND REPORTING	6

1.	Spill Countermeasures	6

2.	Spill Notification Procedures	6

a.	General Notification Procedures For All Spills	7

b.	Federal Notifications	7

c.	State Notification	8

d.	Cleanup Contractor Notification	8

Appendix

A 	INSPECTION FORM

B	TRAINING OUTLINE AND COPY OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS Section 112.1-112.20-Oil Pollution Prevention

C	SPILL NOTIFICATION FORM

FIGURES

Figure	Page

1	SITE LOCATION	9

2	FACILITY LAYOUT AND SPILL PATH	10

TABLES

Table	Page

1	POTENTIAL SPILL SOURCES AND VOLUMES	3

2	DESCRIPTIVE INVENTORY OF BULK STORAGE TANKS	4

A.	GENERAL FACILITY INFORMATION

Name:	National Weather Service, Raleigh Forecast Office

Type:	Meteorological equipment, including an emergency backup power generator with one diesel fuel oil aboveground storage tank (AST) (1,000-gallon capacity)

Location:	1005 Capability Drive

Raleigh, Wake County, North Carolina 27606

Name and Address of Owner:

National Weather Service

Eastern Region Headquarters

Airport Corporate Center

630 Johnson Avenue

Bohemia, NY  11716

Designated Person Responsible for Spill Prevention at this Facility - 112.7(e)(10)

Karl Lenzen, Electronics Technician/Safety officer

Office:	(919) 515-8200

Mobile:	(919) 621-0344

Alternate:	(919) 515-8200 (24 hour)

Date of Initial Operation:

1992

B.	SCHEDULE FOR IMPLEMENTATION - 112.7

The following physical changes will materially affect the facility's potential to discharge oil and will be made within six months of the Responsible Manager's signature per 40 CFR 112.  Within 6 months of the implementation of the following physical changes, the SPCC plan will be amended to reflect the changes, and a Professional Engineer will certify amendments in accordance with 40 CFR Part 112.5(c).

- Several of the 90-degree elbows of the aboveground piping from the generator to the day tank are showing signs of corrosion and will be replaced and protected from corrosion.

2. 	The corrosion protection on the south side of the tank has deteriorated.  The tank will be protected from corrosion.

In addition, various improvements will be made to enhance spill prevention practices at this facility.  The following practices and procedures will be initiated:

3.	Diesel fuel oil unloading procedures describing actions to be taken before and after unloading will be implemented, as described in section H.  The facility will acquire visual signs and storm water catchment basin drain covers to satisfy tanker truck unloading rack regulatory requirements.

4.	A formal inspection program for the aboveground storage tanks, associated piping, foundations, secondary containment systems, and unloading rack area will be implemented, as described in section F.  Appendix A provides an inspection form to document inspection activities.

5.	A formal training program will be implemented, as described in section K.  Appendix B provides a training program outline.

6.	As a good management practice, spill cleanup contractors will be researched and identified to assist with cleanup efforts in the event a spill occurs, and additional spill response supplies will be acquired, as described in section D.3.

7.	A 6-foot-high chain-link security fence surrounds the facility; however, the gate is missing on the front (north side) and makes the tank possibly susceptible to vandalism.  NWS should work with the University security staff to resolve this issue to their mutual satisfaction.  This is necessary to comply with 40 CFR 112.7(e)(9).

C.	SPILL HISTORY - 112.7(a)

This facility has not had a reportable spill.  Should this facility have a reportable oil spill greater than 1,000 gallons in a single spill event or two reportable spills within any 12-month period, this SPCC plan and a report as outlined in 40 CFR 112.4 will be submitted to U.S. Environmental Protection Agency Regional Director and the State agency in charge of water pollution control activities within 60 days of the incident(s).

D.	POTENTIAL SPILLS -- PREDICTION AND CONTROL

1.	Facility Description

The facility is located in the southern portion of metropolitan Raleigh, North Carolina, approximately 2 miles southwest of downtown Raleigh on the campus of North Carolina State University (Figure 1). Figure 2 shows the layout of the facility, including the location of the 1,000-gallon diesel fuel oil AST and adjacent generator shed.  The generator shed houses an emergency backup power generator and a 100-gallon diesel fuel oil tank AST.  This rectangular, above-ground tank acts as a day tank for the generator, supplying diesel fuel oil as necessary.  A float pump in the day tank allows it to be refilled automatically through piping from the 1,000-gallon AST.

The Red Star Oil Company, a local commercial supplier, periodically fills the 1,000-gallon diesel fuel oil AST.  The estimated annual fuel usage is approximately 1,000 gallons per year.  This estimate is based on testing the generator once per week for 1 hour.  Fuel consumption would increase based on the frequency and duration of any power outages.

2.	Prediction of Potential Spills - 112.7(b)

The 1,000-gallon AST is located on a concrete pad at the facility.  The 100-gallon day tank is located inside the generator shed.  Small spills or leaks breaching the tanks’ secondary containment systems (described in paragraph D.3.) would flow in one of two directions due to the slope of the concrete.  Fuel oil flowing to the south would flow over 150 feet of a parking lot into a storm drain which flows into Walnut Creek.  As a result of the flat topography of the site, a small spill would most likely be contained before reaching the storm drain.

A leak or spill flowing to the northeast of the tank would flow into a storm water drain about 15 feet from the 1,000-gallon AST; the drain leads to Walnut Creek.

A release from the day tank would flow in the same directions because of its proximity to the AST.

The most probable causes for spills from the 1,000-gallon AST are from overfilling or loss of structural integrity.  The most probable cause for a spill from the 100-gallon day tank is malfunction of the supply pump.  Table 1 summarizes the potential failure types, potential spill volumes, estimated rates, and direction of spill flow.

TABLE 1

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1,000-gallon AST | Overfilling | 50 - 60 | 50 - 60 gallons per minute | South or Northeast | Operational procedures are in place to prevent overfilling. |
|  | Structural failure | 1,000 | Gradually to instantaneously, depending on size of hole | South or Northeast | Failure of both the primary and secondary tank shells is a low-probability event. |
| 100-gallon Day Tank | Failure of supply pump | 100 | Pump rate | South or Northeast | A low level/high level shutoff is in place. |

3.	Spill Controls - 112.7(c)

Appropriate containment and diversionary structures and equipment to prevent discharged oil from reaching navigable waters have been installed for the 1,000-gallon AST.  The AST is a double-walled tank, encased in a welded, steel plated, rectangular tank with an additional 10 percent (100 gallons) capacity.  A float-type level gauge visually indicates the fuel level.  The secondary tank completely encloses the AST and has a “dip stick” to verify whether any liquids are present in the secondary containment.  The secondary tank is bolted to its concrete foundation.

The 100-gallon day tank is totally enclosed inside the generator shed, protected from the elements. Containment capable of containing 110 percent of the volume of the day tank is in place, and a low level/high level shutoff is located on the pump.

This facility has found it practicable to install equipment and/or structures to prevent discharged oil from reaching navigable waters per 40 CFR Part 112.7(c)(10(i); therefore, an oil spill contingency plan that follows 40 CFR 109 is not required.  In addition, as explained in section B.6, the facility intends to purchase and store spill response supplies (for example, 100 pounds of granular oil absorbent, oil absorbent pads, a broom, and a shovel) to contain and quickly remove small leaks or spills that occur.  The North Carolina State University has a hazardous materials team would also respond to any spills.

E.	FACILITY DRAINAGE - 112.7(e)(1)

The secondary containment is fully enclosed around the tank so that there is no possibility for rainwater to enter.  The secondary containment is inspected on a monthly basis to ensure that there are no leaks in the tank.

Storm water in the areas surrounding the AST and generator flows to the adjacent property either via sheet flow or a storm water catchment basin.  Good management practices to include inspections, personnel training, and readily available spill response supplies prevent oil from reaching navigable waters in the event of equipment failure or human error at the facility.

F.	BULK STORAGE TANKS - 112.7(e)(2)

Both tanks are constructed of steel and are compatible with the product stored.  The interstitial space of the 1,000-gallon double-walled AST provides an additional 10 percent (110 gallons) of sufficiently impervious secondary containment.  The floor of the generator shed will provide adequate secondary containment for the day tank.

Both tanks and their foundations are visually integrity tested through monthly inspections for signs of deterioration and leaks that might cause a spill.  Documented records of these inspections are kept on site for a period of 3 years.  Copies of the inspection form are provided in Appendix A.

There are no buried, partially buried, internally heated, mobile, or portable tanks on this facility.

The 1,000-gallon AST is fail-safe engineered with a direct vision float-type gauge, indicating the fuel level in the tank.  As backup, the AST is stick-inventoried before unloading, and operators continuously monitor unloading operations.  Any leak from the tank is investigated to determine the cause of the leak and corrective actions are taken as appropriate.

TABLE 2

DESCRIPTIVE INVENTORY OF BULK FUEL STORAGE TANKS

| Tank | Product Stored | Nominal Capacity (Gallons) | Tank Type/Year | Failure/Cause |
| --- | --- | --- | --- | --- |
| Aboveground Storage Tank | Diesel fuel oil | 1,000 | Double-walled Steel/1992 | Not Applicable |
| Generator Day Tank | Diesel fuel oil | 100 | Rectangular Steel/1992 | Not Applicable |

G.	FACILITY TRANSFER OPERATIONS, PUMPING, AND IN-PLANT PROCESS - 112.7(e)(3)

A supply pipe made of schedule 40 black iron connects the 1000-gallon AST to the day tank.  The pipe is aboveground as it leaves the top of the AST then goes underground to the day tank.  A float pump installed in the day tank automatically controls the volume of oil pumped from the 1,000-gallon AST to the day tank.

There is no other underground piping on the facility.

H.	FACILITY TANKER TRUCK UNLOADING RACK - 112.7(e)(4)

Facility unloading procedures meet the minimum requirements and regulations established by the U.S. Department of Transportation (DOT), Title 49 of the CFR Subsection 177.834, to include the following:

1.	Smoking is not allowed during the unloading.

2.	The vehicle handbrake is set.

3.	Unloading material will be attended by a qualified person will at all times.

4.	All valves and other closures are closed and free of leaks before departure.

The unloading rack area is composed of an asphalt pad, sloped to a storm water catchment basin on the southeast corner of the property, with a 4-inch concrete berm.  The rack area is designed to hold the entire contents of the largest single compartment of the fuel oil delivery truck, provided the storm water catchment basin downgradient is covered.

Visual signs will be acquired and posted, as explained in section B.3, to describe actions to be taken before and after unloading.  Actions include satisfying DOT requirements, covering the storm water catchment basin before unloading product, and disconnecting the transfer lines and inspecting all drains and outlets on the tank truck for leakage before departure.  Monthly inspections will include inspecting the rack area for cracks in the pavement.

Note:  This facility is not an oil production, oil drilling, or workover facility; therefore, 40 CFR Parts 112.7(e)(5), (6), and (7) do not apply.

I.	INSPECTIONS AND RECORDS - 112.7(e)(8)

A formal inspection program will be implemented as explained in section B.4.  Documented inspection records will be maintained in the facility’s main office, in accordance with the written procedures discussed in section F.  Appendix A contains a copy of the inspection form.

J.	SECURITY - 112.7(e)(9)

A 6-foot-high chain-link security fence surrounds the facility; however, the gate is missing on the front and will need to be replaced in cooperation with the University, as explained in section B.8.  Access to the facility should be limited by means of a lock.  The generator is located in a weather-tight sheet metal enclosure that can be locked to restrict access.  The area around the tank is well lit to detect leaks and spills during nighttime hours and to deter vandalism.

K.	PERSONNEL, TRAINING, AND SPILL PREVENTION PROCEDURES - 112.7(e)(10)

A formal training program will be established as discussed in section B.5.  All facility personnel responsible for implementing the SPCC plan will be properly instructed in the operation and maintenance of all equipment and supplies used to prevent oil discharges as well as the applicable spill prevention regulations.  Refresher training will be provided annually or whenever physical or procedural changes occur at the facility.  Training will highlight and describe known spill events or failures, malfunctioning components, and recently developed precautionary measures.  The person accountable for the facility spill prevention and for training personnel is identified in section A.  Appendix B contains a training program outline.

L.	SUBSTANTIAL HARM CRITERIA EVALAUATION – 112.20 (f)(1)

This facility is not required to have a facility response plan under 40 CFR Part 112.20 since it does not:

- Transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons, or

- Have a total storage capacity over 1 million gallons.

M.	SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is prevention.  This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.  (This does not constitute a contingency plan under 40 CFR Part 109, nor is such a plan required for this facility.)  Should a spill occur that impacts navigable waters or adjacent shorelines, however, the following measures will be implemented.

1.	Spill Countermeasures

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasure activities will be undertaken until conditions are safe for workers.  The following general procedures should be implemented as countermeasures:

a.	Account for all personnel, and ensure their safety.

b.	Divert flow away from drainage channels, and cover storm drain with contents of spill kit.

c.	Attempt to seal or stop leak.

d.	Acquire necessary resources to contain and clean up all oil-contaminated areas.

e.	Make all necessary notifications as described in the following text.

2.	Spill Notification Procedures

- This section discusses the reporting procedures for spills of diesel fuel at the facility.  The people and organizations that are notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

- A spill reporting form that requests the information to be reported to all agencies in written form (to the extent known) is included in Appendix D.  Copies of the completed form should be sent to the NWS Environmental Compliance Officer and the National Oceanic and Atmospheric Administration (NOAA) Western Regional Compliance Officer (see following section).

a.	General Notification Procedures For All Spills

- The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

- First, call 515-3333 (area code 919) if there is an immediate emergency, to access University Public Safety.

- Next, notify the appropriate persons within the NWS:

- Mike Jacob, (301) 713-1838 Ext. 165, NWS Environmental Compliance Officer.

- Olga Kebis, (301) 713-1838 Ext. 173, NWS Safety Officer

- Frank Bain (817) 978-2367 Ext. 139, NWS Eastern Regional Environmental/ Safety Coordinator

- Lynnette Ansell, (757) 441-6298, NOAA Eastern Regional Compliance Officer

The form in Appendix C should be used to document notifications made after a spill has been discovered.

b.	Federal Notifications

- The Federal Clean Water Act, as described in 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  40 CFR Part 110.3 defines “may be harmful” as a discharge for which one of the following applies:

- Violates applicable water quality standards

- Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or cause a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines

- If either of these criteria is met, contact the following:

- The National Response Center (EPA and USCG):  (800) 424-8802.

- Under the SPCC regulations, spill information listed in 40 CFR 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

- A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shorelines in a single event

- Two spill events that cause visible sheens upon navigable waters or adjoining shorelines within any 12-month period

- Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA); therefore, no other notification to the EPA is required for discharges of diesel fuel other than those listed previously.

c.	State Notification

- The North Carolina Division of Emergency Management require notification if:

- Any quantity is spilled to a surface water, or

- Any spill to land exceeding 25 gallons.

- These spills must be reported to the North Carolina Department of Crime Control and Public Safety, Division of Emergency Management at 800-858-0368.

d.	Cleanup Contractor Notification

An emergency response contractor should also be notified to assist with the cleanup, if necessary.  Since the facility is located on the campus of North Carolina State University, the following number should be called to assist with as spill cleanup:

- {FACILITY TO INSERT APPROPRIATE TELEPHONE NUMBER}

FIGURES

FIGURE 1

SITE LOCATION

FIGURE 2

SITE LAYOUT

APPENDIX A

INSPECTION FORM

APPENDIX A

INSPECTION FORM

| MONTHLY INSPECTION CHECKLIST |  |  |  |
| --- | --- | --- | --- |
| Date of Inspection: | Inspector: |  |  |
| TANKS/FOUNDATIONS | YES | NO | COMMENTS |
| 1. Drip marks or stains on outside of tanks? |  |  |  |
| 2. Oil on the ground around tanks? |  |  |  |
| 3. Indications of corrosion (e.g., paint peeling, rust)? |  |  |  |
| 4. Raised spots or dents on the surface of the tanks? |  |  |  |
| 5. All vents clear to properly operate? |  |  |  |
| 6. Fuel gauge and alarms working properly? |  |  |  |
| 7. Foundation appear shifted or settled? |  |  |  |
| SECONDARY CONTAINMENT | YES | NO | COMMENTS |
| 8. Indications of corrosion (e.g., paint peeling, rust)? |  |  |  |
| 9. Presence of spilled or leaked material (standing liquid)? |  |  |  |
| 10. Rainwater present? (If yes, remove and inspect for sheen) |  |  |  |
| PIPING | YES | NO | COMMENTS |
| 11. Oil under aboveground piping, hoses, fittings, or valves? |  |  |  |
| 12. All piping, hoses, fittings, and valves working properly? |  |  |  |
| UNLOADING RACK AREA | YES | NO | COMMENTS |
| 13. Warning signs properly posted and legible? |  |  |  |
| 14. Visible cracks in the pavement? |  |  |  |
| SECURITY/SAFETY/SPILL RESPONSE | YES | NO | COMMENTS |
| 15. Security fencing/gate in good condition? |  |  |  |
| 16. Lights working properly to observe a spill during night? |  |  |  |
| 17. Spill kits easily accessible and complete? |  |  |  |
| Corrective Actions Required: |  |  |  |

APPENDIX B

TRAINING OUTLINE AND COPY OF TITLE 40

OF THE CODE OF FEDERAL REGULATIONS

Section 112.1-112.20-Oil Pollution Prevention

APPENDIX B

OUTLINE FOR SPILL PREVENTION, CONTROL,

AND COUNTERMEASURES TRAINING

I.	INITIAL TRAINING.  Initial training shall be provided for all facility personnel within their first week of employment to familiarize employees with the following information:

A.	Summary of spill prevention regulations (40 CFR 112)

B.	Purpose and application of system elements

1.	Tanks and associated piping

2.	Unloading rack area

3.	Accessory equipment (e.g., generator and pumps)

4.	Gauges/alarms

5.	Spill supplies

C.	Spill prevention

1.	Potential spill sources

2.	Procedures to prevent spills

3.	Inspections/documentation

D.	Spill control

1.	Spill flow direction and impact on navigable waters

2.	Secondary containment systems

3.	Overflow protection and leak detection systems

4.	Alarm recognition and response

E.	Spill countermeasures

1.	Personnel accountability

2.	Spill supplies/equipment use

3.	Methods to stop/seal leaks

4.	Emergency phone numbers and notifications

II.	REFRESHER TRAINING.  Annual refresher training shall be provided to highlight and describe, at a minimum, the following:

A.	Known spill events or failures

B.	Malfunctioning components

C.	Recently developed precautionary measures

III.	ON-GOING TRAINING.  On-the-job training or briefings shall be provided throughout the year whenever physical or procedural changes occur at the facility.

APPENDIX C

SPILL REPORTING FORM

APPENDIX C

SPILL REPORTING FORM

| GENERAL |  |  |  |
| --- | --- | --- | --- |
| Name of Facility: National Weather Service, Raleigh Forecast Office |  |  |  |
| Organization: Federal Government |  |  |  |
| Address: 1005 Capability Drive, Suite 300, Raleigh, North Carolina 27606 |  |  |  |
| REPORTING PARTY |  |  |  |
| Report Completed By: |  |  |  |
| Position: |  |  |  |
| Phone Number: |  |  |  |
| SPILL INFORMATION |  |  |  |
| Date: |  | Time: AM / PM |  |
| Substance spilled: Diesel Fuel Oil |  | Estimated Quantity: |  |
| Source and Cause: |  |  |  |
| OUTSIDE NOTIFICATIONS |  |  |  |
| Agencies | Recorder at Outside Agency |  | Date/Time |
| NRC: (800) 424-8802 |  |  |  |
| DESCRIPTION OF ENVIRONMENTAL DAMAGE |  |  |  |
| CLEANUP ACTION(S) TAKEN |  |  |  |
| CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |  |  |  |

Note: 	All information must be filled in.  If something is unknown, write “unknown.”

ATTACHMENT A

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS Section 112.1  - 112.20

Oil Pollution Prevention