Middle Columbia Transmission Overview and Constraints:

Geographically, the transmission system under discussion covers the Washington counties: Okanogan, Chelan, Douglas, Grant, Kittitas, and Yakima.  Loads in the area are winter peaking.  A normal, winter peak condition is characteristic of high east-to-west flows (West of Cascades-North and West of Cascades-South) and very light north-to-south (NS) flows (North of John Day).  A normal, summer peak condition is characteristic of moderate east-to-west flows and high NS flows (North of John Day and North of Hanford).  The summer pattern produces the highest stress for the area.  The normal, peak summer condition exposes the area to a number of thermal constraints.

The area load centers are: Okanogan PUD, Chelan and Douglas PUD, Grant PUD, and PAC-Yakima.

The transmission system must perform to provide power to the area load centers during different seasonal conditions while supporting the surplus power transfers from the Columbia River hydro generation interconnected in the area.  These hydro plants include Grand Coulee, Chief Joseph, Wells, Rocky Reach, Rock Island, Wanapum, and Priest Rapids.  The Northwest loads are winter peaking with a large portion of the total load located west of the Cascades in the Puget Sound and Portland/Vancouver/Willamette Valley load centers. During normal, peak winter conditions surplus Mid-Columbia generation transfers east-to-west across the Cascades.  During normal, peak summer conditions surplus generation transfers east-to-west across the Cascades, at low levels, and heavy NS transfers exist on the Mid-Columbia 500-kV and 230-kV system.  Summer power transfers to California and reduced loads in the Northwest produce heavy NS flows.

The summer NS transfers are apparent on both the 500-kV and the 230-kV transmission.  A large portion of the hydro generation in the area is connected at 230-kV and 115-kV:

| Major Generation | Connected | Owner | Max MW Capability |
| --- | --- | --- | --- |
| Grand Coulee | 500-kV | BPA | 4598 |
| Grand Coulee | 230-kV | BPA | 2250 |
| Chief Joe | 500-kV | BPA | 1265 |
| Chief Joe | 230-kV | BPA | 1320 |
| Wells | 230-kV | Douglas | 855 |
| Rocky Reach | 230-kV | Chelan | 1331 |
| Rock Island | 115-kV | Chelan | 646 |
| Wanapum | 230-kV | Grant | 1090 |
| Priest Rapids | 230-kV | Grant | 1006 |
| Total Connected at 500-kV | 5863 MW |
| Total Connected at 230-kV and 115-kV | 8499 MW |

The 230-kV and 115-kV generation will step up to the 500-kV system on 500/230-kV transformers (TXF) at Grand Coulee (1 TXF), Chief Joseph (1 TXF), Sickler (1 TXF), and Vantage (2 TXF's) substations.  The remainder of the surplus generation transfers NS on the 230-kV system to Midway substation and moves further south to Bonneville, Big Eddy, White Bluffs, and Benton substations.    The area 230-kV and 115-kV line loadings are highly sensitive to the generation levels at Wells, Rocky Reach, Rock Island, Wanapum, and Priest Rapids.  Grand Coulee and Chief Joe generation will impact the 230-kV and 115-kV loading, but to a lesser degree.

During the heavy NS pattern the 230-kV transmission is utilized to its full capacity.  The 230-kV transmission south of the Vantage/Wanapum substation is heavily stressed during low Priest Rapids generation in the spring and summer months.  The low Priest Rapids generation is a function of operating the Columbia River for biological/fish requirements.

Constraints on New Wind Generation Interconnections:

The Mid-Columbia area has been identified as a prime location for new wind generation.  However, during the spring and summer months, with heavy NS transfers on the 230-kV system and Columbia River Hydro operations necessary to meet biological/fish requirements, the existing transmission is at full capacity.  New wind generation interconnecting on the 230-kV or 115-kV transmission north of Midway will add to the local, surplus generation and will increase the NS transfers.  In order to provide a safe and reliable interconnected power system significant upgrades are required on the Mid-Columbia 230-kV system to support existing generation transfers and new wind generation interconnecting on the 230-kV or 115-kV transmission.