Scope of Work

for the

Hodgdon Meadow Water Treatment System Replacement

#### Description of Services:  The contractor shall provide all labor, materials, tools, equipment and supervision necessary to replace the water treatment facilities, connection appurtenances and well house which service the Hodgdon Meadow water system.  The contractor shall also connect the new system and demolish and remove the existing system.

Background: Hodgdon Meadow is located within Yosemite National Park near the Big Oak Flat Entrance and is open year around. The National Park Service operates and owns the water treatment system and distribution system that serves the Hodgdon Meadow residential area and portions of the Hodgdon Meadow Campground. Currently, the water at Hodgdon Meadow is aggressive and low in pH causing the copper piping and lead solder in the residences to leach into the water. The California Department of Health Services (CDHS) required a corrosion control study and a permanent solution since the water exceeds the mandated action levels.

The water supply for the Hodgdon Meadows residence area and campground is from a single well drilled next to the treatment facility. The pretreated water has a pH range of 6.3-6.5. Most of the distribution piping is asbestos cement, along with copper piping and lead soldering within dwellings. The slightly aggressive conditions of the water allow leaching of copper and lead solder. The existing water treatment system consists of a 12.5% chlorine injection point housed in a 60 square foot structure, as seen in Picture 1 in the attached Photos document. Treated water is sent directly to the distribution system, as well as to a 100,000 gallon storage tank.

The housing unit for the water treatment plant houses the control panels, piping and chlorine injection instruments, along with a 55 gallon storage tank of unused calcium hydroxide. The temporary portable emergency generator is located outside of the housing unit and does not reside at the treatment facility permanently.  The housing unit and generator are on a concrete pad on the edge of pavement of a residential road looking out at Hodgdon Meadow.

#### REQUIREMENTS AND SPECIFICATIONS: The items below are required of the Contractor:

#### - Existing Facilities:

#### The contractor shall allow all elements of the existing well, well house, water treatment equipment and connection appurtenances to remain intact and functioning until the new system is ready to be connected.  The contractor shall minimize system down time during connection and provide the COTR four weeks notice for any utility system shut-downs.  All system shut-downs and shut-down lengths must be approved by the COTR.

#### After the new system is online and approved by the COTR, the contractor shall remove and dispose of the existing treatment building, slab and all above ground water system facilities up-line of the new system connection point. All underground facilities which lie up-line of the new system connection point shall be abandoned in place.  Disposal of all demolition debris shall be at an out-of-park location or landfill in accordance with local, state and federal regulations and procedures.

- New Treatment Building:

- The new treatment building shall be installed in the location shown in the overall site plan and shall meet the intent of the Floor Plan (Exhibit 2) and the Elevation Plan (Exhibit 3).

- The building shall be stick built with dimensions of 10’ by 20.5’. The new housing unit will be comprised of two rooms and a shelter:

  - one room for chemical storage

  - one room for electrical controls, work station, and operations

  - roof shelter for generator

- Interior wall shall be covered with ¾ plywood sheathing and wall shall be insulated.

- The foundation shall be 6” thick slab on grade and be formed to have a continuous and smooth transition to the existing asphalt roadway and will be approximately 12x 22.5’ in size. Contractor means and methods for creating the smooth transition shall be approved by the COTR prior to execution.

#### Construction shall be stick-built with standard 2x4 framing to meet a snow load of 80 psf.  The roof shall have a 4 in 12 pitch and shall be a standing seam metal roof colored NPS brown.

- The building shall be painted “wosky” brown.

- The rooms for the water treatment equipment and electrical controls shall have standard 4-foot doorways leading outside. The locks shall be 6-pin core Best locks and the doors shall be painted brown.

- Chemical storage room will have an intake fan and exhaust vent to provide ventilation. Each room shall have a space heater to maintain rooms at a minimum of 60°F.

- The chemical storage room will have a drain for washdown and chemical spills that will drain to an open sump outside of the building. The sump shall be large enough to fit a portable pump for discharging any chemicals.

#### The temporary generator space will have a 4-foot wide gate for easy removal and replacement of the generator. The propane generator will be 20 kW, 3-phase, 60 amps. Propane for the new generator shall be supplied by the propane tank located adjacent to the existing building.  Connection to propane tank to be provided by contractor.

- Screened closable vents shall be provided at 2 locations in the upper section of the walls near the roof at the gable end.

- The contractor shall also provide lighting for the interior building. Interior lighting shall provide adequate coverage such that work may be performed in the structure without and addition lighting.  All lighting shall be controlled by a single interior switch per room.  The COTR shall verify lighting adequacy prior to approval.

#### - Treatment Equipment, Appurtenances and Service Connections:

#### The contractor shall provide and install the new treatment system per the Plumbing Schematic (Exhibit 1) and Floor Plan (Exhibit 2).

#### All components shall be installed per manufacturer’s recommendations.

- The new water treatment facility shall consist of a new chlorine system, static mixer, and a base chemical injection point to reduce corrosion.

- The selected static mixer is a wafer style requiring flanges. Monitoring equipment includes a pH meter with recorder and existing flow meter.

- The existing well and well pump will remain the same. The new treatment system will connect at the same above ground connection from the well as the existing treatment system.

- The piping will be galvanized steel and will be mounted along the wall of the operations room. Chemicals will be supplied/stored in the chemical storage room and piped through the adjoining wall to the treatment line using polyethylene tubing. Chemically resistant tanks and materials shall be used for the chlorine injection equipment and soda ash equipment.

  - Testing Piping: The work of installing piping and appurtenances shall be of such character as to leave all pipes and connections water-tight.  As soon as practical after any section of pipeline has been completed or when directed by the Contracting Officer, a hydrostatic test shall be placed on that section of pipe to determine water tightness.  Tests shall be conducted in conformance with the 2007 California Plumbing Code.  If test fail, replace pipe at no additional cost to the Government, and retest.

- The chlorine injection equipment shall consist of a 5 gallon polyethylene tank set on a mounted shelf along with a 0.16 gph (gallon per hour) ProMinent Beta BT4a 1601 metering pump, or approved equal, and tubing. The feed output required is 0.0134 gph to deliver the appropriate dosing. Chlorine dosing will be 0.04 gallons/day to achieve a residual concentration of 1 ppm (parts per million), based on a 12.5% chlorine solution.

  - Chlorine pumps shall be able to inject chemicals against pressures up to 160 psig.

  - Pump drive shall be totally enclosed with no exposed parts.

  - Pumps shall have adjustable stroke frequency and the flexibility of up to 1000:1 turndown ratio, and manually adjustable stroke length.

  - Pumps shall have priming valves and diaphragms and ramp style knobs that allow for hands free priming.

- The soda ash equipment consists of two 50 gallon polyethylene tanks suitable for the soda ash; one tank contains mixing equipment with a metering pump, which then dispenses into the second tank called the dosing tank. The two tank system will provide more effective mixing, which has been a problem with previous systems. The two tank system will also allow the system to stay in operation as the dosing tank will remain in service while the mixing tank is taken off line for refilling. The mixed tank allows thorough mixing and maturation prior to dosing. Another metering pump shall be located on top of the dosing tank where the solution is then injected into the water supply line. The two metering pumps are to supply 0.083 gph each. Metering pumps shall be ProMinent Beta Series, Model BT4a-1000, or approved equal.

  - Chemical feed pumps shall be able to inject chemicals against pressures up to 160 psig.

  - Pump drive shall be totally enclosed with no exposed parts.

  - Pumps shall have adjustable stroke frequency and the flexibility of up to 2500:1 turndown ratio, and manually adjustable stroke length.

  - Pumps shall have priming valves and diaphragms and ramp style knobs that allow for hands free priming.

  - Chemical feed system to be tested to ensure all components are operating correctly.

- Provide one steel table.  Table shall be made of 16 gauge steel.  Table shall be 30” in height, model number 2744I14 McMaster-Carr (708) 834-9600, or approved equivalent.

#### Government Provided Items: The government will provide the following items for this project:

#### -Final Construction Drawings and Specifications

#### Submittals:

#### The contractor shall submit manufacturer’s information on all tanks, pumps, metal roof, doors, windows, and piping components.

#### The NPS has 1 week to review and comment on all submittals.

#### BID FORMAT: The bid format for this contract is manufacturer preference with the minimum itemized bid components including, but not limited to the following:

#### Mobilization

#### 10x20.5 Building

#### Installation of Treatment Equipment, Appurtenances and Service Connection.

#### Demolition of Existing Structure & Equipment

#### Miscellaneous Clauses:

- Coordination with Other Contractors and Park Partners: The Contractor shall cooperate fully with other Contractors, Partners and Government employees. The Contractor shall not commit any act that shall interfere with the performance of work by any other Contractor, Partner or Government employee. The CO shall resolve work schedule conflicts between this contract and the additional work awarded to other Contractor(s) should unresolved conflicts arise. The Contractor does not have the authority to direct the work of government personnel, other contractors/consultants or Partners.

- Health and Safety:  Contractor shall comply with FAR 23 “Environment, Conservation, Occupational, Safety, and Drug Free Workplace”. The Contractor shall immediately report any accident, incident, or potentially hazardous situation to the CO and the COR. The Contractor shall adhere to all YNP work place safety rules and policies. The Contractor shall cooperate and provide full assistance to any investigation. Failure to do so shall be deemed as grounds for termination for default of the contract. Contractor personnel and property are subject to safety inspections in the performance of this contract.

- Contractor Safety Plan:   The Contracting Officer shall review and concur on all Safety Plans prior to the start of work or staging of supplies, equipment or personnel on United States Government property.  The contractor is solely responsible for insuring adequate lead-time is provided to permit review and concurrence of the safety plan. The Contractor shall complete the Safety Plan in accordance with OSHA and NPS requirements. If revisions are required, the Contractor shall include them in the Safety Plan with appropriate configuration control notations (i.e. change bars and revision numbers).

- Contractor Safety Violation Notification:  Under NO circumstances are unsafe working conditions permitted.  Upon notification, the contractor shall take immediate steps to correct the condition.  The contractor shall immediately contact the Contracting Officer or the Contracting Officer’s Representative upon receipt of a Safety Violation Notice.  Failure to correct unsafe conditions shall be cause for termination of the contract for default.  In addition, costs to the Government to correct contractor safety violations shall be charged against the contractor.  In accordance with Yosemite Safety Standard Operating Procedures, a copy of the Safety Concern Notice shall be placed in the permanent project and contract file and routed to the appropriate agencies for action.

- Identification and Change of Critical Contractor Personnel:  The Contractor shall submit an organizational chart displaying key personnel involved in the effort and their respective positions and disciplines. The Contractor shall immediately and expressly notify the CO of any changes in critical Contractor personnel. Critical Contractor personnel consist of all on-site personnel, any direct charge personnel, and any others in a management role. The Contractor shall obtain CO approval of any proposed changes in contract personnel along with the steps taken/proposed to ensure there are no impacts to the schedule or ability to maintain performance level associated with individual responsibilities. The Contractor shall identify to the CO all subcontractors to be used, prior to signing any contract or initiating any work. The Contractor shall provide subcontractor qualifications to the CO prior to subcontractor utilization.

- Post Award Meeting: After the issuance of the Contract, the Contractor shall attend a post award meeting at the location specified by the CO. The purpose of the meeting shall be to review all contract requirements, information, and/or site-specific data addressed under the Contract. As directed by the CO, all on-site Contractor staff shall attend the meeting prior to beginning work. The Contractor shall participate in and/or facilitate an on-site meeting to develop plans and alternatives as a working initiative to formulate the work required by the SOW.

- Sensitive Data:  In accordance with FAR 24  “Protection of Privacy and Freedom of Information”  Certain data is for official use only and shall not be released outside the appropriate lines of authority. Failure to do so shall be deemed as grounds for termination for default of this Contract.  The Contractor shall not publicize, or release in any manner, information or data regarding projects on which they may be working or negotiating with this office.  Nor shall they discuss, prior to public release by this office, a project, future program or planning item with anyone not directly affiliated with the design of the project.  Any inquiries in regard to these matters shall be referred to the Contracting Officer.  Contractor employees may review or be exposed to sensitive information including personnel, personal, competitive (to include Government independent estimates, budgetary planning documents, and private party data entrusted to the Government), other vendors’ proprietary data (to include cost, process and personnel) or legal documentation (to include attorney deliberative data and attorney work product). Competitive data shall be treated in accordance with the procedures stipulated in FAR 3.104-5, FAR 15.413 and all indentures. For the purposes of competitive data, the FAR considers contractor personnel as Government Personnel. Personnel information is subject to OPM guidelines. Personal information is subject to the Privacy Act of 1974 and FAR 24.1, Attorney products are subject to the Federal Rules of Evidence, Rule 501.  Freedom of information requests shall be immediately reported to the FOIA Monitor through the Contracting Officer.

- Sensitive Data (Cultural Resources):  The cultural resource information contained herein is protected from public disclosure under 16 U.S.C. section 470w-3, of the National Historic Preservation Act of 1966 as amended, and 16 U.S.C. Section 470 hh, of the Archaeological Resources Protection Act of 1979.

These data are provided to the Contractor strictly for the purposes of work specified in the contract.  These data are not to be duplicated, used secondarily for any purposes, or in any way disclosed to the public.  These data are to be protected from duplication and from any unauthorized use or access.  These data are to be returned to the Government upon completion of the contracted work.

- Photo Documentation:  The Contractor shall prepare photo documentation as a routine component of compliance management activities when managing compliance projects with ongoing field actions or in documenting project site compliance management decision making.

- Deliverables:   Deliverables consisting of all provided written and electronic reports, minutes, technical exchange data or other memoranda shall be delivered as 50% and 95% drafts.  Final approval and acceptance shall be provided only after all government comments are incorporated into the final 100% document.  Formats for deliverables will be provided by the COR.  Requests for use of contractor format shall be directed to the Contracting Officer.

- Review of Deliverables:  Assist in the technical review of deliverables generated during the course of projects. Provide complete technical justification for each comment generated and participate in or facilitate the technical discussion to resolve all open items. Use of technical augmentation staff shall be coordinated with the COR

- Technical Evaluation of Response to Solicitations:  Assist in the technical evaluation of other Contractor responses to solicitations. Provide complete information to establish the Government’s position for fair and reasonable compensation for the level of effort to be performed. The Contractor shall be responsible for safeguarding proprietary and other sensitive information in accordance with Sensitive Data paragraph above

- Changes:   All changes to the contract or order must be expressly made by an authorized representative of the Contractor and a duly warranted CO of the United States. No work is authorized to begin in advanced of a properly executed contract modification.

- Preservation of natural, cultural and archaeological resources:   No contractor shall violate any Park regulations regarding preservation of natural, cultural and archaeological resources.  Within the Park and the El Portal Administrative Site the following is prohibited:  (1) Possessing, destroying, injuring, defacing, removing, digging, or disturbing from its natural state, any fish or wildlife; plants or parts or products thereof; nonfossilized and fossilized paleontological specimens, cultural or archaeological resources, or the parts thereof; and any mineral resource or cave formation or the parts thereof.   (2) Walking on, climbing, entering, ascending, descending, or traversing an archaeological or cultural resource, except in designated areas and under conditions established by the superintendent.  (3) Possessing, destroying, injuring, defacing, removing, digging, or disturbing a structure or its furnishing or fixtures, or other cultural or archaeological resources.  These regulations are enforceable under 36 CFR Part 2.

- Discharge into Water Resources is Prohibited:  The Clean Water Act, 33 U.S.C. 1251 et. seq., prohibits any discharge of pollutants by any person into water of the U.S. without a permit.  "Pollutant" refers to soil sediments, solid waste, chemical or biological materials or even water that is at a different temperature than the receiving body of water.  "Person" is broadly defined to include individuals, corporations, partnerships, associations, states, municipalities, etc.

Reporting of any Spill of Oil or Hazardous Substance is Required and the failure to do so is criminally enforceable under 33 U.S.C 1321.

Contractor shall provide an Oil and Hazardous Materials Spill Prevention, Control, and Countermeasures Plan to address spill prevention and response measures for hazardous substances used on site, including fuels.  A copy of this Plan shall be maintained on site during construction and contractor and subcontractor employees should be trained on spill prevention and response measures.

Prior to the start of work, the Contractor shall submit a plan that complies with YNP, Federal and State requirements and allows contractors to properly notify officials in the event of an emergency occurring during construction activities. YNP requirements include at a minimum:

During non-work operations, stationary equipment shall be parked over specially prepared containment pads designed to trap any leaking oil, fuel, or hydraulic fluids.

Inspect construction site daily for proper storage of hazardous materials, proper parking of equipment on containment pads, and for hydraulic and oil leaks of equipment, tighten hoses, and ensure they are in good condition.  If equipment is leaking, it shall be immediately repaired or removed from the Park at Contractor’s expense.

Routine oiling, lubrication, and refueling shall be conducted with secondary containment using Best Management Practices (BMPs) at all times. Refueling of equipment in wetlands or stream channel areas is not allowed at any time.  Signs prohibiting refueling will be posted in environmentally sensitive areas as directed by the natural resource monitor.

Contractor shall maintain secondary containment for all equipment operating with fluids (such as drilling) or when direct discharge of leakage, spills, or other source of construction or equipment fluids can flow directly to any streambed, whether flowing with water or dry. Containment shall be designed and installed so as to prevent accidental spills into streambeds in the event of mechanical failure or hose breakage.

Contractor shall maintain spill response materials on the project site when using heavy equipment to ensure rapid response to spills. These materials shall include absorbent pads, booms, or other materials as appropriate to contain oil, hydraulic fluid, solvents, and hazardous material spills.  The contractor shall maintain adequate equipment to effectively respond to potential spillage at the site as determined by review of the COR.

Contractor shall provide names and phone numbers of appropriate contractor’s personnel to be contacted at any time (24 hours per day) regarding accidental release of hazardous substances to air, soil or water.  This list shall be submitted to the CO and a copy visibly displayed in work areas on site.

Contractor shall adhere to appropriate YNP staff notification procedures and shall rely on YNP to accomplish external notification. Contractor’s responsibility shall include immediate notification of all spills to the COR (or to park dispatch if the COR is not available). This notification will include specific details regarding spilled materials, amounts, and other relevant details as required by the park SPCC plan or as defined in advance in consultation with the COR.

Contractor shall digitally photograph or videotape the spill release at its source and photographically document the initial spill extent within 30 minutes of initial release.

- Any Damage to Park Resources Must be Reported:  The report should be relayed immediately to the COTR and to a Protection Division representative which may include the Resource Protection Office at 209-372-0218.

- Working in Bear Country:  Proper food storage is important to the welfare of the Yosemite bear population and it is required by law.

- If staying in a campsite, store all food and related items in metal food lockers provided in campgrounds, not in vehicles.

- Bears have a strong sense of smell and may break into vehicles with the slightest hint of food.  Dispose of your trash, food scraps, and recycling in a bear-proof receptacle.

- Be sure to check your vehicle daily and remove any item that may attract a bear. This includes canned food, drinks, soap, cosmetics, toiletries, trash, recycling, ice chests, grocery bags, and unwashed items used for preparing or eating meals.

- Close and latch any windows and doors in your hard-sided unit while you are away.

- Check job site at the end of each work day for trash or food

- Large open top bins/dumpsters used on the job site shall be covered and marked, “No Food /Trash.”

NPS Contracting Office shall provide “The bears are not to blame” brochure as courtesy for field personnel.

Use the Save-a-Bear hotline (209) 372-0322 to report overflowing trash containers, improperly stored food; bear sightings, or other information about bears.

#### - Heavy Equipment Cleaning:   All heavy equipment must pass an inspection prior to entering the park or park managed areas.  Inspections shall be provide by a resource monitor and scheduled through Victor Goldman, (209) 379-1181. Measures shall be taken to prevent the introduction of exotic species in the project area and staging areas.  All earth moving equipment and hand tools must enter the Park free of dirt, dust, mud, seeds, or other potential contaminant. Equipment exhibiting any dirt or other material attached to frame, tires, beds, wheels, or other parts shall be thoroughly cleaned by the Contractor before entering the Park.  Areas inspected shall include, but not be limited to, tracks, track guard/housings, belly pans/under covers, buckets, rippers, and other attachments.  Equipment should have belly pans/under covers minimally secured as these areas shall need to be easily accessed during inspection.  All equipment shall be directed to the El Portal Maintenance Facility for inspection prior to commencing work.  If vehicles are unable to drive to El Portal due to size or load restrictions, vehicles shall be inspected at a mutually agreed site by the Contracting Officer prior to entering the Park.  Equipment found to have entered the Park with potential contaminants shall be removed from the Park at the direction of the Contracting Officer at Contractor's sole expense.

- Estimates:  All estimates shall comply with the following guidelines. Deviations from this methodology must be documented and is subject to Government review and concurrence.

- Class A Estimate:  Based on complete working drawings and specifications, and prepared prior to calling competitive tenders, this estimate should be sufficient to allow a detailed reconciliation/negotiation with any contractors proffered tender.

- Class B Estimate (Substantive):  Based on design/preliminary drawings and outline specifications for the project, which include the designs of all major systems and subsystems, as well as the results of all site/installation investigations, this estimate should provide for the establishment of realistic cost objectives and be sufficient to obtain effective project approval.

- Class C Estimate (Indicative):  Based on a full description of the preferred option, construction/design experience, and market conditions, this estimate should be sufficient for making the correct investment decision, and obtaining preliminary project approval.

- Class D Estimate:  Based upon a statement of requirements, and an outline of potential solutions, this estimate is strictly an indication (rough order of magnitude) of the final project cost, and should be sufficient to provide an indication of cost and allow for ranking all the options being considered.

ACRONYMS

CAP		Contractor Acquired Property

CFR		Code of Federal Regulations

CO		Contracting Officer

COR		Contracting Officer Representative

COTR		Contracting Officer’s Technical Representative

FAR		Federal Acquisition Regulation

FTR		Federal Travel Regulations

FLER		Funds and Labor Hour Expenditure Report

FOIA		Freedom of Information Act

SOW		Statement of Work

USC		United States Code

YNP		Yosemite National Park