COMMERCIAL CLAUSES

| 1 | 144805-31 | Statement of Work/Specifications | April 1999 |
| --- | --- | --- | --- |

PART 1 - GENERAL

Provide labor, raw materials, equipment, system components, and services to manufacture and deliver a 4,000 gallon, double walled, aboveground, fire rated, aviation gasoline dispensing, fuel storage tank system and related appurtenances.  The assembled tank (system) shall be delivered to the Bettles, Alaska USFWS Hangar.  Please include in your proposal the method you intend to use to deliver the tank system and the cost for an alternate delivery method.

REFERENCES:

ANSI B31.4	-	Pipeline Transportation Systems for Liquid Hydrocarbons and Other Liquids o

API 1529	-	Aviation Fuelling Hose and Hose Assemblies

API 1581	- 	Specification and Qualification Procedures for Aviation Jet Fuel                                                      Filter/Separators

ASTM A36	-	Standard Specification for Carbon Structural Steel .

ASTM A395	-	Standard Specification for Ferritic Ductile Iron Pressure-Retaining Castings for Use at Elevated Temperatures

ASTM A569	-	Standard Specification for Steel, Carbon (0.15 Maximum, Percent), Hot-Rolled Sheet and Strip Commercial (Withdrawn 2000)

ATA 103	-	Standards for Jet Fuel Quality Control at Airports

NFPA 407	-	Standard for Aircraft Fuel Servicing,

NFPA 30	-	Flammable and Combustible Liquids Code

IP/EI 1583	-	Specification and qualification procedures for aviation fuel filter monitors.

UFC 24		-	Airports, Heliports and Helistops.

UFC 79		-	Flammable and Combustible Liquids

UL 79		-	Standard for Power-Operated Pumps for Petroleum Product Dispensing Systems.

UL 142		-	Aboveground Tank for Flammable Liquids on Supports

UL 157		-	Standard for Gaskets and Seals.

UL 525		-	Standard for Flame Arrestors for Use of Vents of Storage Tanks for Petroleum, Oil, and Gasoline

UL 2085 	-	Standard for Insulated Aboveground Tanks for Flammable and Combustible Liquids

40 CFR 112	-	Oil Pollution Prevention and Response; Non-Transportation-Related Onshore and Offshore Facilities

SYSTEM DESCRIPTION:

Tank :

The tank shall meet UL 2085 specifications equal to a Fireguard. Tank capacity shall be 4,000 gallons. The tank shall mounted on skids with the proper UL 142 nameplate for a supported tank system.  The skids shall be integral to the tank..  All tank openings shall be located on the tanks top. The tank fill port shall have a overfill containment basin with flowback drain integrated into the tank.  In addition ports are required for suction, interstitial monitoring, one normal vent for the primary tank , two emergency vents for the primary and secondary tank, one for the fuel quantity guage and alarm, and one spare plugged with an approved cast iron plug and a frost proof drain valve.  The tank shall have an approved ladder, fueling platform, lifting lugs, and ground points. The tank shall have a manhole large enough to allow personnel entry for tank inspection and cleaning.  Entire system shall be primed and painted with marine grade paint.  See attached photographs for an example of type of tank required.

Appurtenances:

Provide one hundred ten volt aviation gas approved pump, clock type fuel quantity gauge with overfill alarm, overfill prevention valve, proper fire extinguishers, aviation fuel filters, hose reel, static ground reel, aviation grade fuel hose, aviation nozzle, and keytrol type monitoring system are the primary appurtenances.  Provide drop tubes, normal pressure vacuum vent pipe long enough to be twelve (12) feet above ground level and set below the pressure of the emergency vents, emergency vent pipes long enough to be two feet above tank top, solenoid anti siphon valve, and isolation valves.  System shall arrive as completely assembled and as ready for use as possible. Contact with the Station Representative is critical to understanding the fuel delivery options available in Bettles so the proper appurtenances are proposed.

Fuel Distribution Manifold:

The pump, hose reel, ground reel, filters, piping, isolation valves, and electrical connections shall be mounted in a lockable enclosure (see attached photographs and drawings).  The enclosure shall be five feet to the top.  The enclosure may have other specific requirements than those shown and listed so please contact the Station Representative so you can be sure those requirements are included in the proposal.  The cabinet extension and the lockable attached storage box are critical items and need to be discussed and reviewed before your proposal can be evaluated.  No keyed locks are necessary.  Provide a welded on hasp for use with a 3/8 inch shackle pad lock.  Existing power source is the Bettles community electrical grid available at the hangar.  Contractor shall provide provisions for electrical connection to existing power source.  Entire system shall be primed and painted with marine grade paint as specified.

SUBMITTALS:

Contractor shall submit tank system and drawings, fuel manifold, and all appurtenances for  approval prior to manufacture.

Product Data:  Manufacturer's literature, printed installation instructions, shop drawings, test results and parts lists. Reference specific page number and paragraph from the government specifications for each item in the descriptive data.  Descriptive literature shall be exact, no assumptions are made and no substitutions are allowed without prior written approval from the Contracting Officer.  Provide data to include but not be limited to the following:

1.  The double wall tank system

2.  Coating system

3.  Access ladder

4.  Fuel distribution manifold (Clamshell enclosure)

5. Overfill prevention valve system set at 95%

6.  Anti-siphon valves

7.  Isolation valves

8.  ANSI B31 Piping

9.  Clock type fuel quantity gage with integral overflow alarm

10. Hand pump with drop tube to allow water removal from low (receipt) end of tank

11.  Two 80 BC fire extinguishers

12.  UL listed Aviation fuel pump

13.  The floating suction system tied to the dispensing pump system

14.  75 feet of API approved hose

15.   Hose reel to hold 75 feet of 1" hose.

16.  75 feet of static grounding reel

17.   Aviation approved fuel filters meeting Institute of Petroleum 1583 specifications

18.   Aviation approved nozzle

19.   One resetable mechanical meter located in the fuel dispensing cabinet

20.  Mechanical leak detection indicator for interstitial space port

21.  Gaging chart calibrated in 1/8" increments with dip stick

22.   Explosion proof wiring for hard-wired connection to hangar electric system.

23.  Electronic fuel monitoring system capable for up to five users. (keytrol type system)

Shop Drawings:  Schematic drawings of the tank system with type and size, include ports, vents, labeling, lifting lugs, ladders, skids, piping, connections, electrical wiring, grounding points etc.  Provide three hardcopy sets of drawings on 2' X 3' sheets and one electronic copy.

Certificates: A test certificate shall be provided for each coupled length of hose stating it meets API 1529 standards.  The coupling tests as specified in API 1529 shall be performed on each hose.  Each coupling of a coupled length of hose shall be permanently marked with a serial number corresponding to its hydrostatic test certificate.  The hose at the end of each coupling ferrule shall be permanently marked prior to hydrostatic testing to serve as a reference to determine whether a coupling has slipped during testing.  The hose shall be flexible to -65F.

INSPECTION, STORAGE, HANDLING and DELIVERY:

A minimum of ten working days written notice shall be given to the Contracting Officer (CO), Contracting Officers Technical Representative (COR), and the Station Representative (SR) when system is ready to be inspected. Send written notice by e-mail.  During storage and handling all pipe connection openings shall be plugged or tapped with cast iron fittings.  Tanks shall be carefully lifted and lowered by use of cables or chains of adequate length attached to the lifting lugs.  A spreader bar shall be used where necessary.  DO NOT use chains or slings around the tank shell.  Contractor is responsible for system until accepted by the government.  Contractor shall immediately notify CO, COR, and SR by written message when tank arrives on site.

PART 2 - PRODUCTS

TANK MANUFACTURERS:

Ace Tank and Equipment

143 Elliot Ave West

Seattle, WA 98119, 	1-800-426-2880

Anchorage Tank and Welding

2700 Porcupine Drive

Anchorage, AK 99501,   907-272-3543

Greer Tank, Incorporated

2921 West Int. Airport Road

Anchorage, AK 99502,   907-243-2455

Westeel Petroleum Products

Attn: Ken Mattson, Territory Sales Manager

509-997-1389 phone

509-679-9659 cell

TANK FABRICATION:  Fabricate tanks in accordance with UL 2085, Standard for Steel Aboveground Tanks for Flammable and Combustible Liquids with the UL 142 nameplate for supported tanks.  All ports shall be female threaded.  All ports shall be raised and broadened such that there are no depressions around port openings, to prevent ice, snow or liquids from pooling around tank openings.  Several items listed in these specifications may be deviations from your standard tanks and therefore careful review of these specifications, close contact with the COR and the SR, and careful review of the project requirements is critical for a successful proposal.

Ports (per tank):  Size ports per UL 142

Label all ports.

A fill port

A suction port

A fuel quantity gage port

A leak detection port,

A spare 2" port

One normal vent port for the primary tank.  The vent for the primary tank shall be a vacuum pressure vent.  Tank vents for normal venting shall be of a length to terminate a minimum of twelve feet above grade or as code allows.

Two emergency vent ports, one each for the primary and secondary tank. Tank vents for emergency venting shall be of a length to terminate a minimum of two feet above the top of the tank or as code allows.

Spill containment basin:  Containment basin shall be integral to tank system. It shall hold a minimum of seven gallons.  It shall have a push-type access drain for spilled product and a lockable lid.  The overfill sump shall not extend into the top of the main tank such that filling of the main tank is restricted from normal fill rates.  Sump shall be less than 12" above top of the tank.

Access ladder and platform:  Ladders shall comply with the construction requirements in accordance with the current edition of Occupational Safety and Health Standards, Title 29 of the Code of Federal Regulations, Part 1910, Subpart D, Section 1910.27 - Fixed Ladders.  Ladders shall support a static load of 1000 pounds.  The tank system requires a catwalk to allow safe access to the top of tank.

Labeling: Mark each tank with the manufacturer's name, trade name, or trademark or other descriptive marking by which the organization responsible for the product can be identified.  If a manufacturer produces tanks at more than one factory, each tank shall have a distinctive marking by which it can be identified as the product of a particular factory.  If a manufacturer produces tanks at more than one factory, each tank shall have a distinctive marking by which it can be identified as the product of a particular factory. Each tank shall be marked with:

The manufacturer's name, trade name, or trademark or other descriptive marking by which the organization responsible for the product can be identified.

"NO SMOKING" signs on each side

"TYPE (Avgas)" signs on each side

"SIZE (4,000)" Gallons signs on each side

UL 42 and UL 2085 nameplates permanently attached to the tank system

NFPA Chemical hazard label

The required marking shall be embossed, etched, stamped on a nameplate of corrosion resistant metal, or as described below.  The markings shall be in a size and style of type corresponding to 18 point Franklin Gothic [1/4 inch high letters] or the equivalent.  The nameplate shall be attached by welding or brazing or by attaching it by drive screws, rivets, welding, or brazing to a bracket or holder that is then welded or brazed to the tank.

If a pressure-sensitive label, ink or paint stenciling, or other method is used, it shall comply with the requirements in the Standard for Marking and Labeling Systems, UL 969; be suitable for outdoor use and exposure to fuels and gasoline; and have a minimum surface temperature rating of 140o F.

For primary and secondary tanks, the nameplate shall be secured to the tank.

APPURTENANCE MANUFACTURERS and SUPPLIERS:

Most appurtenances available locally in Anchorage or Fairbanks

Ace Supply Inc.

2425 East 5th Ave

Anchorage, AK 99501

(907) 277-4113?

Morrison Bros. Company

PO Box 238

Dubuque, IA 52001,

(800)-553-4840, (563) -583-5028 fax

www.morbros.com/AST.htm

Petroleum Equipment Manufacturing Company (PEMCO)

2185 West 76th Street

Hialeah, Florida 33016 USA

(305) 558-9911, (800) 448-3286, (305) 558-8282 fax

www.pemcofl.com/catalog/above_ground.html

Krueger Sentry Gauge

1873 Siesta Rd.

Green Bay, WI 54313

(920) 434-8860

www.ksentry.com

Jackovich Industrial Hardware

PO Box 70407

Fairbanks, Alaska 99707

(907) 456-4414, (907)452-4846 fax

Westeel Petroleum Products

Attn: Ken Mattson, Territory Sales Manager

509-997-13489 phone

509-679-9659 cell

APPURTENANCE  DESCRIPTIONS:

All materials used in fabrication shall be compatible with the base tank, flammable and combustible liquid, and the physical and atmospheric conditions where the device is used.  Polymerics and elastomers shall be evaluated for compatibility with fluids, surface, or atmospheric conditions with which the part comes in contact.  These materials shall comply with the requirements for gaskets and seals, UL 157.  All accessories shall be constructed to minimize the stresses on the base tank.

Coating System:   Sand blast the entire tank to SSPC-SP6 standards.  Apply coatings according to manufacturers recommendations.   Paint shall be equal to Dupont Imron,  Sherwin Williams Dura-Plate, or equal polyurethane epoxy system.  Primer to be high solids primer compatible with finish paint.  Abrasive blasting shall be completed without interruption and coating is applied immediately after.  All welding shall be finished, welds cleaned and weld splatter removed. Threaded openings shall be covered with pipe plugs or thread protectors during coating..  Greasy or oily areas shall be removed from surface with solvent.  Final color shall be Amershield 1046 (desert sand) or approved equal.

Overfill prevention valve (OPV, shutoff device): Morrison 9095A-0200 AV, Emco Wheaton A1100, Guillotine or approved equal with internal floats only.  Valve shall attach firmly to the fill port.  Valve shall be pre-set to stop at 95% full.  Drop tube assembly shall reach within 6" of the tank bottom.  Provide standard quick connect (camlock) or equal for filling.  Overfill valve shall be compatible with and integrate with the overfill containment  basin.  Overfill containment basin lid must be liquid tight.  The OPV shall perform its function for nozzle fill or pressure fill operations.

Anti-siphon devices shall be installed in each external pipe connected to the tank when the pipe extends below the level of the top of the tank.  A check or manual valve shall be provided in the discharge dispensing supply line from the pump with a union between the valve and the same pump discharge.

Clock guage alarm: Morrison 918F or equal. Clock type gage and alarm. Gage shall read in feet and inches with built in high level warning alarm.

Fire Extinguishers: Two - UFC, Article 10, Multi-purpose Dry Chemical, 2-A, 80-B:C, cartridge type, with mounting bracket.  Aviation tank system shall have brackets to hold fire extinguishers.

Mechanical meter: Fill rite 806CL flow meter or equivalent.  FPP fuel meter with resettable Veeder-Root transaction register.

Interstitial leak detection indicator:  Krueger Sentry Gauge model K-2 or approved equal.

Pump:  Heavy duty, UL listed, aviation fuel rated, commercial grade, industry standard pump with explosion-proof motor, sealed bearings and permanent magnet.   Self-priming, automatic bypass valve system that won't let motor overheat. Pump shall be capable of producing 15-20 gpm at the nozzle. The pump will connect to an existing 120 volt wiring in the hangar.  A separate circuit to the hangar wall will need to be provided.  Provide extreme cold weather pump seals.  If extreme cold weather pump seals or other cold weather pump materials (oils, lubricants) are not available, identify those items with proposal.  Provide a minimum two year limited warranty.

Electonic Fuel Management Control:  Jackovich Industrial Hardware,  Gasboy Electonic Keytrol or approved equal.  System shall be capable of the minimum five users.   The fuel meter must be compatable with the Keytrol and a pulser unit is needed to send gallon info from meter to Keytrol.

Floating suction system:  EW Fuel Management Ltd, Eco Tank Systems, Acetank and fueling equipment or equivalent.

Hose:  Goodyear, Durodyne, Elaflex or approved equal.  Hose shall comply with API Bulletin 1529, 1", Class 1, Type C, nonelectrically bonded hose incorporating semiconductive cover compound.  Seventy five (75 feet) of (operability to -40o F, Impervious to damage at -40o F) hose for use in avgas systems.  Couplings shall comply with API 1529.  Hose piping shall have integral grounding strap connections.  Provide a camlock on the hose from end of hose to the pump.

Hose Reel:  Hannay, CoxReel, Reelcraft, or approved equal.  Electric rewind with manual as secondary suitable for 75 feet of 1 inch avgas hose, with hose stop and roller (TR), hose shall be able to be mounted so it can be pulled straight out.

Static Grounding Reel: .  Hannay model #HGR 75, CoxeReel, Reelcraft  or approved equal. Spring rewind, 75 feet 7X19 galvanized cable with clear plastic coating, adjustable guide arm with cable guide

Filters: Velcon (Mdl # VF 61, with differential pressure gauge), Bendix, Facet or approved equal.  Aviation approved conforming to IP 1583, single stage, absorbent monitor rated to allow 20 gpm at the nozzle. All sections of the filtering system shall have electrical continuity with adjoining piping and equipment.  Filter separator sumps and associated piping that may contain water shall be protected to prevent freezing and bursting.  All filters shall match the pumping pressures and flow rate in gallons per minute (gpm) of the pump. Configure filter to be readily accessible.

Sediment pre-filter shall be Goldenrod or equal.

Nozzle:  The overwing refueling nozzle shall be equal to a Morrison 218 Aircraft Refueling Nozzle..  The valve that controls the flow of fuel to an aircraft shall have a deadman control.  Nozzle spout screens shall be 100-mesh or finer and readily accessible for inspection and cleaning.  Nozzles shall have dustcovers.

Fill/Suction tubes:  Provide fill and suction tubes of aluminum material, located at opposite ends of the tank.  The fill pipe shall be provided with a means for making a direct connection to common fuel truck apparatus, so the delivery of fuel is not exposed to the open air during the filling operation.  The fill tube shall extend to within 6" of the tank bottom.

Piping Systems:  Piping, joints, valves, and fittings shall comply with NFPA 30.

Pipe Joints:  Joints shall be made liquid tight and shall be threaded, except that listed flexible connectors may be used when installed in accordance with NFPA 30.

Valves:  Piping systems shall contain a sufficient number of valves to operate and protect the system.  Piping systems in connection with pumps shall contain a sufficient number of valves to control properly the flow of liquid in normal operation and in the event of physical damage.

FUEL DISPENSING MANIFOLD (CLAMSHELL ENCLOSURE):  The fuel-dispensing manifold shall consist of the hose, hose reel, static reel, pumps, and filters.  The manifold shall be housed in an enclosable cabinet with secondary containment sloped to a low point drain. Connect tank system to manifold components by vapor proof braided flexible piping.  The following components are parts of the manifold.

-  Steel Piping (sized to match components and pump flow rate)

-  Flexible connectors (to compensate for shifting)

-  (2) Stainless steel ¼ turn ball valves (used to isolate the filter vessel(s) during filter changes

-  (1) Fuel system pressure gage

-  Pressure relief valves & piping (used to relieve thermal & system pressure build ups)

-  Filter vessel with qualified elements (Institute of Petroleum 1583) the vessel shall be mounted with sufficient clearance (minimum of 8") to allow sumping and cartridge change out.

The filter vessel shall have the following accessories,

--Direct reading differential pressure gage tied to pump cut off switch.

--Pressure relief valve(s)

--Sump Drain

--In line fuel sampling probe (installed in downstream piping) Gammon GTP -7 or equal

-  Fuel dispensing meter ((50 GPM)(Non commercial)

-  Bonding reel with  75 feet cable and clip

- 75 feet X 1- ¼" API 1529 Type C aircraft refueling hose

-  Electric rewind hose reel

-  Over wing aircraft refueling nozzle with bonding wire, screen, and dust cap.

-  Pump on/off switch- designed for flammable liquid storage and transfer systems.

-  Electrical wiring and conduit-designed for flammable liquid storage and transfer systems.

PART 3 - EXECUTION :

Execution Order:

1.	Written approval of  submittals

2.	Manufacture tank according to approved submittals specifications, drawings, and photographs, and modifications

3.	Tank shall be available for inspection before shipment.  Written approval shall be obtained before tank is shipped from manufacturer.

4.	No payments shall be made until written approvals by CO and COR are made

5.	Deliver tank complete to Bettles USFWS Hangar

6.	Provide all operation and maintenance data and all instructions for the tank system.

7.	Final payment (20% minimum) shall be made only after tank arrives on site and has written approval by Station Representative or designated USFWS personnel.

Contacts:

Contracting Officer (CO):

Contracting and General Services

1011 East Tudor Road

Anchorage, Alaska 99503

Dennis Hermannes (907)6786-3412, (907)786-3370 fax

Dennis_hermannes@fws.gov

Station Representative (SR):

Kanuti National Wildlife Refuge

101 12th Avenue,   MS 555

Room 262, Box 11

Fairbanks, Alaska 99701

Primary:  Joanna Fox (907) 456-0329 phone, (907) 456-0428 fax  Joanna_fox@fws.gov

Secondary:  Michael Spindler 456-0329 phone, (907) 456-0428 fax  Mike_Spindler@fws.gov

Contracting Officer Technical Representative (COR):

Division of Engineering

Environmental Section

U.S. Fish and Wildlife Service

1011 E. Tudor Rd.

Anchorage, AK 99503

Charles D. Grant (907)786-3506, (907)786-3370 fax

Charles_grant@fws.gov

SPECIAL REQUIREMENTS:  The availability of equipment in Bettles is unknown.    The government has no equipment to transport new tank system and no government furnished equipment is part of this contract.