Site Survey Report

Dar es Salaam, Tanzania

December 2003

Richard K. Thigpen

Introduction

A site survey of the proposed location for the new GCOS Upper Air Network (GUAN) station at Dar es Salaam, Tanzania was conducted during the period of 9 - 16 December 2003.  The location is at the Dar es Salaam International Airport.

There are two existing buildings probably built in the mid-70's approximately 300 meters from the current forecast office which is across the runway from the airport terminal.  It is a secure area of course and prior approval and an escort are always required.  One of the buildings housed the GIP hydrogen generator (electrolyser) and served as the balloon inflation area while other housed a Mensural wind finding radar itself.

Hydrogen Generator/Inflation Building

Figure 1.  Hydrogen Generator/Inflation Building

The building shown in Figure 1 is in very good condition and is presently being painted.  It is approximately 300 meters from the Forecast office and less than 100 meters from the operations building.  The building is approximately 15.5 meters long by 5 meters wide.  The balloon shed door on the right end of the building in the photo above is 3.2 meters wide.  Adequate electrical power is available and there is an existing water supply.

The old inoperative GIP  hydrogen generator shown in Figure 2 is still inside the building and must be removed.  TMA says this will be done right away and then the floor under the unit can be cleaned and painted.

Figure 2 Old GIP Electrolyser

The new generator will be located in this area and the TMA staff will insure the installation of an electrical service breaker box sufficient to accommodate the 10.7 KVA required by the generator.  Further they will insure that the incoming water is equipped with a convenient connection and shut off valve.  Power is 220 volt 50 HZ.

Figure 3 Balloon inflation area/Storage tank location

The balloon inflation area is shown in figure 3 and this appears to be the logical location for the storage tanks.  It is separated by this wall from the hydrogen generator room.  It is clean, painted and ready to use.

Operations Area

Figure 4 Operations building

The operations building is a two story building and the lower level is currently used by an observer.  The second floor will be used as the upper air operations area.  The antenna will be mounted on the roof.  The building needs more renovation and repair than the hydrogen generator building.  It is a sound building in a good location.

It is not yet clear how this facility will be connected to the communications center in the forecast office.  There are telephones in the lower floor and it is likely that additional pairs of wire will be found in the cable connecting the building to the forecast office.  If useable pairs cannot be found then TMA will arrange to have additional cables installed.  The distance is perhaps 300 meters.  In the forecast office there is a good telecommunications center so the problem is only between the buildings.

Figure 5 Operations room

Figure 5 shows the area that will become the operations area.  These old Mensural wind finding radar equipment racks will be removed and the area refurbished and equipped with tables and chairs as needed to install the new InterMet/Modem upper air equipment.  TMA will also investigate the feasibility of connecting the building to the airport's emergency power grid.  Power is 220 volts 50 Hz.  There are two room mounted air conditioner units that are inoperative and should be replaced.  The general area should be refurbished and there are some areas where the safety railing is dangerous.

Figure 6 Antenna Location

The radiotheodolite antenna will be mounted on this roof top concrete pad after this unit is removed.  The concrete pad is 2.6 meters square and about 10 centimeters thick.  The equipment specification indicates a 2 meter diameter pad is needed so this pad should suffice.

Contact information

The primary contact in the TMA for this project is:

Mohamed Matitu

Manager, International Relations

Tanzania Meteorological Agency

P.O. Box 3056

Dar es Salaam, Tanzania

E-mail:  mrmatitu@meteo.go.tz

Tel: Tel: +255 22 2111645/2126537

Fax: +255 22 2110231/2112471

Mobile: +255 748 400375

The primary contact in the GCOS Secretariat/WMO for this project is:

Richard K. Thigpen

GCOS Secretariat

7 bis, Avenue de la Paix

P.O. Box 2300, CH-1211

Geneva, Switzerland

E-mail:  Rthigpen@wmo.int or

Thigpenr@erols.com

Tel:  (+41 22) 730-8012 or

(1) 301-598-5683

Mobile: (1) 301-452-7669