SPILL PREVENTION, CONTROL, AND COUNTERMEASURES PLAN

NATIONAL WEATHER SERVICE

Marquette Weather Forecast Office

112 Airport Drive South

Negaunee, Michigan  49866

Original Date of Plan	:	March 27, 1995

Date of Last Plan Review	:	February 11, 2002

Date of Last Amendment

and P.E. Certification	:	February 11, 2002

Designated Person Responsible for Spill Prevention:

Bruce Cromell, Environmental Focal Point

Telephone: (906) 475-5782, Ext. 381 or Ext. 0

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of Title 40 of the Code of Federal Regulations Part 112, I attest that this Spill Prevention, Control, and Countermeasures (SPCC) Plan has been prepared in accordance with good engineering practices.

| John McCall |
| --- |
| Printed Name of Registered Engineer |
| Signature of Registered Engineer and Date |
| Registration No. PE-050653-E | State PA |

REVIEW DOCUMENTATION AND MANAGEMENT APPROVAL PAGE

REVIEW DOCUMENTATION

In accordance with Title 40 of the Code of Federal Regulations (CFR) Part 112.5(b), a review and evaluation of this Spill Prevention, Control, and Countermeasures (SPCC) Plan is conducted at least once every 3 years.  As a result of this review and evaluation, the National Weather Service will amend the SPCC Plan within 6 months of the review to include more effective prevention and control technology if:

C	Such technology will significantly reduce the likelihood of a spill event from the facility, and

C	If such technology has been field-proven at the time of review.

Any amendment to the SPCC Plan shall be certified by a Professional Engineer within 6 months after a change in the facility design, construction, operation, or maintenance occurs that materially affects the facility’s potential for the discharge of oil into or upon the navigable waters of the United States or adjoining shorelines.

| Review Date | Signature of Responsible Manager | Amended (Yes or No)? 1 |
| --- | --- | --- |

1	Amendment necessary and certified by a Registered Professional Engineer per Title 40 CFR Part 112.3(d)

MANAGEMENT APPROVAL

The National Weather Service is committed to the prevention of discharges of oil to navigable waters and the environment.  We maintain the highest standards for spill prevention, control, and countermeasures through regular review, updating, and implementation of this SPCC Plan for the Weather Forecast Office.

Edward Fenelon, Meteorologist-in-Charge

Printed Name and Title of Responsible Manager

Signature and Date

CONTENTS

Section	Page

Certification	i

Review Documentation and Management Approval	ii

PART I - GENERAL INFORMATION	1

A.	GENERAL	1

1.	Name	1

2.	Type	1

3.	Date of Initial Operation	1

4.	Location	1

5.	Name and Address of Operator	1

6.	Facility Contacts:	1

B.	SITE DESCRIPTION AND OPERATIONS	2

1.	Facility Location, Layout, and Operations	2

2.	Facility Storage	2

3.	Drainage Pathway and Distance to Navigable Waters	3

4.	Spill History	3

5.	Spill Potential, Volumes, and Rates	3

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL	4

A.	SPILL PREVENTION	4

1.	Bulk Storage Tanks and Facility Transfer Operations	4

2.	Tank Truck Unloading Operations	4

3.	Inspections and Records	5

4.	Site Security	6

    - Training	6

B.	SPILL CONTROL	6

1. 	Secondary Containment Designs, Construction Material, and Volume	6

2. 	Spill Kits Type and Location	7

PART III - SPILL COUNTERMEASURES AND REPORTING	8

A.	SPILL COUNTERMEASURES	8

B.	SPILL REPORTING	9

1.	General Notification Procedures for All Spills	9

2.	Federal Notifications	9

3.	State Notification	10

4.	Cleanup Contractor Notification	11

PART IV - RECOMMENDED IMPROVEMENTS	12

A.	PROCEDURAL CHANGES	12

1.	Inspections and Preventative Maintenance	12

2.	Training	12

Appendix

A	TANK ULLAGE/FUELING LOG AND FUEL UNLOADING PROCEDURE CHECKLIST

B	INSPECTION CHECKLISTS

C	TRAINING OUTLINE AND TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, SECTION 112.1-112.20-OIL POLLUTION PREVENTION

D	SPILL REPORTING FORM

E	CROSS REFERENCE OF THE REQUIREMENTS OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, SECTION 112.7, WITH THIS PLAN

FIGURES

Figure	Page

1	SITE LOCATION	13

2	SITE LAYOUT	14

TABLES

Table	Page

1	DESCRIPTIVE INVENTORY OF FACILITY STORAGE	15

2	POTENTIAL SPILL SOURCES AND VOLUMES	16

PART I - GENERAL INFORMATION

- GENERAL

This section provides general information about the facility.

  - Name

National Weather Service (NWS)

Marquette Weather Forecast Office

  - Type

This facility is an onshore facility (non-production) that operates as a weather forecast center and is staffed 24 hours per day, 7 days per week, and 365 days per year.  This facility also maintains meteorological equipment, containing emergency backup power and radar generators, with three diesel fuel aboveground storage tanks (1,500 gallons).

  - Date of Initial Operation

January 27, 1995

  - Location

112 Airport Drive South

Negaunee, Marquette County, Michigan  49866

  - Name and Address of Operator

National Weather Service

Central Region

601 East 12th Street, Room 1836

Kansas City, Missouri 64106

(816) 426-3226

  - Facility Contacts:

Name	Title	Telephone Number

Bruce Cromell 	Environmental Focal Point	(906) 475-5782 Ext. 381

Jack Rice 	Electronics System Administrator	(906) 475-5782 Ext. 372

Edward Fenelon	Meteorologist In Charge	(906) 475-5782 Ext. 642

(24 hours a day)

- SITE DESCRIPTION AND OPERATIONS

This section describes the site location, its operations that store diesel fuel, site drainage patterns, spill history, and spill potential.

  - Facility Location, Layout, and Operations

The facility is located in Marquette County, Michigan, at the former Marquette International Airport, approximately 8 miles west of Marquette on U.S. Route 41 (Figure 1).  Figure 2 shows the layout of the facility, including the location of one 1,000-gallon and two 250-gallon aboveground storage tanks (AST), which are designed to operate as a single 500-gallon tank system.

Fuel in the 1,000-gallon AST feeds a 175-kilowatt (kW) emergency backup generator that provides backup power to the WFO.  A 25-gallon day tank is located near the 175-kW generator inside the generator enclosure.  Fuel in the two 250-gallon ASTs feeds a 66-kW emergency backup generator that provides backup power to the Radar Data Acquisition (RDA) system.  The 250-gallon tanks and associated generator are located inside the RDA generator building.

Estimated fuel usage is approximately 24 gallons per month for the WFO emergency backup generator (1,000-gallon AST) and approximately 20 gallons per month for the RDA emergency backup generator (250-gallon ASTs).  This estimate is based on a test of each generator once per week for 34 minutes.  Fuel consumption would increase based on the frequency and duration of any power outages.

  - Facility Storage

The WFO generator tank is a 1,000-gallon horizontal diesel fuel AST constructed of single-walled steel enclosed inside a concrete outer shell that provides impervious secondary containment.  The building generator shed contains an emergency backup power generator with a built-in 25-gallon diesel fuel oil day tank that supplies diesel fuel on demand.  A float pump in the day tank allows it to be refilled automatically through aboveground piping from the 1,000-gallon AST.  The tank is built to Underwriter Laboratories specification 142 (UL 142).

The primary and secondary tanks have 2-inch-diameter primary vents and 6-inch-diameter emergency vents (the primary having two emergency vents).  A flame arrester venting the primary tank also is installed on the tank in front of the fill spout.  An aboveground supply pipe connects the 1,000-gallon AST to the day tank via 0.75-inch pipe.  A float pump installed in the day tank automatically controls the volume of oil pumped from the 1,000-gallon AST to the day tank.

The RDA tanks are two 250-gallon horizontal diesel fuel tanks constructed of single-walled steel; they are located inside the RDA generator building.  These two tanks are connected to each other via chemical resistant, flexible, 6-inch diameter piping.  The ASTs have 2-inch-diameter, steel vents connected to an exhaust system located inside the RDA generator building.  The tanks are built to Underwriter Laboratories specification 142 (UL 142).

An automatic shut-off valve on the cam-lock fitting fill spout is set to close at 90 percent of the AST’s capacity (900 gallons).  The AST also has an audible high-level alarm set at 85 percent of capacity (850 gallons) and interstitial monitoring device between the primary tank and the concrete outer shell that is connected to the audible alarm system.  A 10-gallon capacity round spill container surrounds the fill spout.

Table 1 summarizes the pertinent information on the tanks at the facility.

  - Drainage Pathway and Distance to Navigable Waters

Fuel spilled from outside the containment systems of the 1,000-gallon AST, day tank, or the RDA tanks would flow west into an on-site culvert inlet approximately 80 feet west of the WFO generator building.  The culvert directs flow to a drainage ditch along the property’s northern boundary and along Airport Drive South (Figure 2).  Stormwater flow from the site is expected to flow to Midway Creek, located approximately 1 mile northeast of the site.

  - Spill History

Reportable spill events from start of operations (March 1995) to present (date on cover of this plan):   	None.

  - Spill Potential, Volumes, and Rates

The most probable causes of spills from the ASTs are from overfilling, a ruptured hose during fuel unloading, or failure of the fuel supply line to the day tank.  For these tanks, spills caused by loss of structural integrity, vehicle collision, or earthquake are low probability events.  For the day tank, the probable causes of spills are from failure of the pump to shut down or failure of the line from the pump to the day tank.

Table 2 summarizes the potential type of failure, potential spill volume, estimated rate, and direction of spill flow from the tanks.

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES 
FOR SPILL PREVENTION AND CONTROL

This section discusses spill prevention and control measures that shall be implemented at the facility.

- SPILL PREVENTION

This section describes design components and operating procedures that shall be implemented at the facility to prevent oil spills.

  - Bulk Storage Tanks and Facility Transfer Operations

ASTs:  Construction of all ASTs is compatible with the No. 2 diesel fuel stored in the tanks.  The 1,000-gallon WFO tank is encased in concrete, and a float level gauge allows for visual inspection of fuel level (empty to full).  The RDA generator building provides adequate secondary containment for the two 250-gallon RDA tanks.  The secondary containment system consists of a sunken, poured concrete containment basin in the RDA generator building floor that is designed to hold at least 110 percent of the tank system contents (550 gallons).

For all three ASTs, an automatic shut-off valve on the cam-lock fitting fill spout is set to close at 95 percent of tank capacity (950 gallons for the 1,000-gallon AST and 475 gallons for the two 250-gallon ASTs).  The tanks also are equipped with audible high-level alarm systems set at 90 percent of total tank system capacity (900 gallons and 450 gallons, respectively).

On the 1,000-gallon WFO tank, an interstitial monitoring device between the primary and secondary tanks also is connected to the audible alarm system.

Day Tank:  The 25-gallon day tank is enclosed in a weatherproof building that provides sufficient containment for the contents of the tank.  The tank is equipped with an open top spill pan (rupture basin) designed to hold 100 percent of the tank volume.  The day tank also is equipped with a liquid level gauge to indicate the amount of fuel in the tank (empty to full) and a high-level float switch connected to an audible alarm to warn of overfilling.  The day tank rupture basin has a float switch installed that is designed to detect fuel that has spilled or leaked.  The rupture basin float switch is connected to an audible alarm system.  The audible alarm system currently is deactivated.

Piping:  An antisiphoning valve is located between the 1,000-gallon WFO tank and pump to prevent unwanted fuel from being siphoned from the storage tank.  The aboveground piping from the storage tank to the day tank pump is equipped with a polyvinyl chloride pipe sleeve to protect it from corrosion.

  - Tank Truck Unloading Operations

All delivery drivers have received U.S. Department of Transportation hazardous material transportation training, as required by Federal law.

The remainder of this section discusses the procedures that shall be used during unloading of fuel from the tank truck into the storage tank to prevent spills.  This procedure shall be documented every time refueling occurs in the form found in Appendix A.  Copies of this form shall be kept for 3 years.

The following procedure is used prior to fuel unloading:

•	Move spill containment equipment, such as booms or spill barriers, into the unloading area.

•	Ensure that the audible high-level alarm system and the automatic shutoff valve are functioning properly.

•	Determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (see Appendix A).  This ullage is communicated to the fuel supply contractor and marked in the fueling log.

•	Block the tank truck wheels.

•	Place drip pans under all pump hose fittings (if applicable) prior to unloading.

•	Ensure the fill nozzle is placed in the appropriate tank appurtenance.

Both the NWS representative and the delivery driver shall remain with the vehicle at all times during unloading.  Gauges on the tank and the truck shall be continuously monitored to ensure the ullage is not exceeded.  If either the audible or visual alarms engage, the unloading of fuel shall be stopped as soon as possible.

After fuel unloading is completed:

•	Record the amount of fuel transferred to the tank in the log (Appendix A).

•	Drain the fill hose and then ensure that all drain valves are closed (if applicable) prior to removal of the hose from the tank.

•	Pour any fuel in the drip pans, tank truck containment pool, or spill container on the fill pipe into the tank (if it has the capacity), or dispose of it appropriately.

•	Inspect the tank truck prior to removing the blocks to ensure the lines have been disconnected from the tank.

•	Remove the blocks from the truck wheels.

•	Place a copy of the fuel unloading checklist in the SPCC plan.

  - Inspections and Records

Inspection and Maintenance of Tanks:  The ASTs and day tank shall be inspected weekly for any oil outside the tank, especially at seams (including the underside).  The concrete shall be inspected for cracks.  The outside of exposed piping also shall be inspected weekly, especially at the joints such as gasket fittings.  Monthly and annual inspections shall follow the checklists shown in Appendix B.

Record Keeping:  The Environmental Focal Point is responsible for completing the ullage logs and documenting fuel unloading procedures.  These records, as well as records of all inspections, shall be maintained for at least 3 years from the time of inspection.

  - Site Security

The facility is attended and operational 24 hours a day.  The WFO and RDA tanks are adequately lit to detect spills at night.  The WFO AST is not fenced, but the RDA generator ASTs are inside a locked generator building that is located within a security fence with locked gate.  For all ASTs, signage warns of the presence of a combustible liquid, that the combustible liquid is No. 2 diesel fuel, and that smoking is not permitted near the tanks.  Fire extinguishers are kept near each of the ASTs.  None of the tanks are located in the direct line of parking lot traffic; therefore, no guard posts are required.

  - Training

The Environmental Focal Point (person responsible for spill prevention) and an alternate shall be trained in the intent of applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in paragraph 3, above.  Spill control and countermeasures also shall be included in the training.

Training shall be repeated once per year.  All new personnel responsible for implementing this SPCC plan shall be properly trained before beginning the new position.  A record of who was trained, when, and by whom, shall be filed with this SPCC plan and kept for a period of 3 years.

- SPILL CONTROL

This section describes control measures that shall be implemented to prevent any spilled oil from entering navigable waters or adjoining shorelines.

  - Secondary Containment Designs, Construction Material, and Volume

The concrete secondary containment tank on the 1,000-gallon AST completely encloses the primary tank and does not allow precipitation into the containment.  Design includes a monitoring system capable of detecting fuel in the tank interstices.

The generator day tank is contained within a building that provides adequate containment and does not allow precipitation into the building.  The day tank rupture basin is equipped with a float switch designed to detect spilled or leaked fuel.  The float switch is connected to an audible alarm system.

The 250-gallon RDA generator ASTs are located inside the RDA generator building within a poured concrete basin designed to hold at least 110 percent of total tank volume (550 gallons).

  - Spill Kits Type and Location

The facility shall maintain sufficient spill kit materials such as absorbent pads and mats sufficient to prevent a spill from reaching a nearby water body.  The facility has spill kits designed to absorb diesel fuel and includes oil absorbent socks and mats in a polyethylene container that can be used as a disposal container.  These items are stored in the generator building.  In addition, cat litter is stored in the RDA building to supplement the oil absorbent socks and mats stored in the spill kit at that location.

PART III - SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is on prevention.  The spill countermeasures presented do not constitute a contingency plan detailed in Title 40 CFR Part 109, nor is one required.  Such a plan is only required under Title 40 CFR 112.7(d) if it is impracticable to provide containment, diversionary structures, or equipment to prevent the discharge of oil to navigable waters.  In addition, this facility is not required to have a facility response plan under Title 40 CFR Part 112.20 because it does not:

C	Transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons, or

C	Have a total storage capacity over 1 million gallons.

- SPILL COUNTERMEASURES

This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasure activities will be undertaken until conditions are safe for workers.  The SWIMS procedure should be implemented as countermeasures:

S   -	Stop the leak and eliminate ignition sources.

a. 	Attempt to seal or some how stop leak if it can be done safely.

b. 	Attempt to divert flow away from catch basins and waterways with a spill barrier or the contents of the spill kit.

c. 	Eliminate all ignition sources in the immediate area.

W  -	Warn others.

a.  	Yell out “SPILL.”  Inform the person in-charge at your facility.

b. 	Account for all personnel and ensure their safety.

c. 	Notify contacts and emergency response contractor as described in the following section for assistance in control and cleanup.

I    -	Isolate the area.

a. 	Rope off the area.

M  -	Minimize your exposure.  Stay upwind.

S    -	Stand by to assist the emergency response contractor, if necessary.

- SPILL REPORTING

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The individuals and organizations that are notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

A spill report form that requests the information to be reported to all agencies in written form (to the extent known) is included in Appendix D.  Copies of the completed form should be sent to the NWS Environmental Compliance Officer and the NOAA Regional Compliance Officer.

  - General Notification Procedures for All Spills

The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

•	First, call 9-1-1 (or the local emergency agency) if there is an immediate emergency

•	Next, notify the appropriate individuals within the NWS:

•	Mike Jacob, (301) 713-1838 Ext. 165, NWS Environmental Compliance Officer

•	Olga Kebis, (301) 713-1838 Ext. 173, NWS Safety Officer

•	Kirt Grahl, (816) 426-3226 Ext. 470, NWS Midwest Regional Environmental/Safety Coordinator

•	Sherilyn Villegas, (816) 426-3925 Ext. 263, NOAA Central Regional Compliance Officer

  - Federal Notifications

The Federal Clean Water Act as described in Title 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency’s (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  Title 40 CFR Part 110.3 defines “may be harmful” as a discharge that:

•	Violates applicable water quality standards, or

•	Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or causes a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines.

If either of these criteria are met contact:

•	The National Response Center (EPA and USCG):  (800) 424-8802

Under the SPCC regulations, spill information listed in Title 40 CFR Part 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

•	A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shorelines in a single event, or

•	Two spill events that cause visible sheens upon navigable waters or adjoining shorelines within any 12-month period.

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA); therefore, no other notification to the EPA is required for discharges of diesel fuel other than those listed above.

  - State Notification

To satisfy the state reporting requirements, the location and quantity of any spill must be determined.  Under the Michigan Department of Environmental Quality, Part 201, Environmental Remediation, of the Natural Resources and Environmental Protection Act (NREPA), 1994 PA 451, as amended (Act 451), Section 201.14(1)(b), a reportable quantity (RQ) is defined as follows:

•	The requirements of this subdivision shall apply to reportable quantities of hazardous substances established pursuant to 40 CFR 302.4 and 302.6 (1989), unless the department establishes through rules alternate or additional reportable quantities as necessary to protect the public health, safety, or welfare, or the environment

•	Part 31, Environmental Remediation, of the Natural Resources and Environmental Protection Act (NREPA), 1994 PA 451, as amended (Act 451) states: unpermitted release directly or indirectly to public sewer system, surface water or groundwater from an oil storage facility or on-land facility of a “polluting material” (oil, salt, or any material specified in Table 1 in R 324.2009) in excess of its threshold reporting quantity during any 24-hour period

For practical purposes, the facility can use the same criteria used for federal reporting requirements stated above.  If one of the criteria are met, contact the Michigan Department of Environmental Quality Pollution Emergency Alerting System (PEAS) within 24 hours after obtaining knowledge of the release:

•	(800) 292-4706 (24 Hours) (from within Michigan)

•	(517) 373-7660 (outside of Michigan)

  - Cleanup Contractor Notification

An emergency response contractor also should be notified to assist with the clean up, if necessary.  Contact information for at least three emergency response contractors shall be maintained in this plan.  NWS has identified the following contractors that are available for emergency response:

•	Professional Consultants, Inc. 		(906) 228-9821

•	STS Consultants, Ltd.			(906) 228-2333

•	TriMedia Consultants Inc. 		(906) 360-5076 - Spill Response

(906) 228-5125 - Business

•	U.P. Environmental Services		(800) 624-6086 - Spill Response

(906) 466-9900 - Business

•	Superior Hazardous Waste Group	(800) 688-4005 - Spill Response

(800) 932-6216 - Business

PART IV - RECOMMENDED IMPROVEMENTS

In accordance with Title 40 CFR Part 112.7, this section presents physical upgrades or procedural changes that are not yet fully operational but are called for in the plan.

- PROCEDURAL CHANGES

  - Inspections and Preventative Maintenance

The inspection checklists found in Appendix B should be followed.  This requirement is found in Title 40 CFR Part 112.7(e)(8).  Visual inspections include observing for any signs of cracking in the outer concrete containment wall of the 1,000-gallon AST or for signs of corrosion for all of the steel tanks.  Additionally, the interstitial space of the storage tank will be inspected for any signs of leakage.  If a problem is suspected with any tank, tightness testing should be initiated soon after discovery.

  - Training

The Environmental Focal Point (person responsible for spill prevention at the facility) and an alternate should be trained in the intent of the applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in the previous section.  Spill control and countermeasures also should be included in the training.  The alternate should be designated in case the primary person is off the site at the time of a spill.  A recommended outline for the training is found in Appendix C.

Training should be repeated once per year.  All new personnel responsible for implementing the SPCC plan should be properly trained before beginning the new position.  A record of who was trained, when, and by whom should be filed with this SPCC plan and kept for a period of 3 years.  This requirement is found in Title 40 CFR 112.7(e)(10).

Spill prevention briefings for operating personnel should be conducted at frequent intervals to ensure adequate understanding of the SPCC plan and to describe spill events or failures, malfunctioning components, and recently developed precautionary measures.

Figure 1 Site Location

Figure 2 Site Layout

TABLE 1

DESCRIPTIVE INVENTORY OF FACILITY STORAGE

| Tank | Nominal Capacity (Gallons) | Product Stored | Type | Double Walled? |
| --- | --- | --- | --- | --- |
| WFO Generator AST | 1,000 | No. 2 diesel fuel | AST | Yes |
| WFO Generator Day Tank | 25 | No. 2 diesel fuel | AST | No1 |
| Radar Generator AST | 250 | No. 2 diesel fuel | AST | No2 |
| Radar Generator AST | 250 | No. 2 diesel fuel | AST | No2 |
| Total Capacity | 1,525 |  |  |  |

Note:	AST	Aboveground storage tank

1	Tank is situated over a rupture basin that contains 110 percent of its volume and is                          located within the WFO generator building also designed for containment.

2	Tanks are in the RDA generator building designed to contain 110 percent of its volume.

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1,000-gallon AST | Overfilling or a ruptured hose during fueling | >0 to 40a | 80b | Variable, then west | None. |
|  | Failure of fuel supply line to pump | >0 to 1,000 | Variable | Variable, then west | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 1,000 | Variable | Variable, then west | Low probability event that both primary and secondary tank shells would fail. |
|  | Vehicle collision | >0 to 1,000 | Variable | Variable, then west | Low probability event. Vehicle traffic is limited and traffic flow is not directly towards tank. |
|  | Overturn or puncture during natural disaster | >0 to 1,000 | Variable | Variable, then west | Low probability event. Double-walled tank provides extra protection from rupture, but catastrophic event could cause a spill. |
| Generator Day Tank | Failure of the pump to shut down after filling day tank or failure of the line from pump to day tank. | >0 to 1,000 | Variable | Variable, then west | Can be minimized through routine inspections. |
|  | Failure of fuel return line | >0 to 25 | 10c | Variable, then west | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 25 | Variable | None (contained in building) | Low probability event can be minimized through regular inspections and maintenance. |
|  | Overturn or puncture during natural disaster | >0 to 25 | Variable | None (contained in building) | Low probability event. |

Notes:

a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

c	Estimated return line flow rate.

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

(continued)

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| 250-gallon RDA Tanks (2 each) | Overfilling or a ruptured hose during fueling | >0 to 40a | 80b | Variable, then west | None. |
|  | Failure of fuel supply line to pump | >0 to 200 | Variable | Variable, then west | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 200 | Variable | None (contained in building) | Low probability event can be minimized routine inspections and maintenance. |
|  | Overturn or puncture during natural disaster | >0 to 200 | Variable | None (contained in building) | Low probability event. |

Notes:

a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

c	Estimated return line flow rate.

APPENDIX A

TANK ULLAGE/FUELING LOG AND

FUEL UNLOADING PROCEDURE CHECKLIST

(2 Pages)

APPENDIX A-1

TANK ULLAGE AND FUELING LOG

Tank Capacity 			  gallons

| Date | Initials | Gauge Reading | Initial Volume of Fuel in Tanka (Gallons) | Available Capacity or Ullageb (Gallons) | Quantity Added (Gallons) | Comments |
| --- | --- | --- | --- | --- | --- | --- |

Note:

a	From gauge reading

b	Available capacity = tank capacity - initial volume of fuel in tank

APPENDIX A-2

FUEL UNLOADING PROCEDURE CHECKLIST

Date:										Tank:

NWS Representative:								Supplier:

| / | ITEM | DESCRIPTION | COMMENT |
| --- | --- | --- | --- |
| The following six items must be completed prior to fuel unloading: |
|  | 1 | Move spill containment equipment, such as booms or spill barriers, into the unloading area. |  |
|  | 2 | Ensure the audible high-level alarm system and automatic shutoff valve are functioning properly. |  |
|  | 3 | Determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (see Appendix A, Page A-1 in SPCC plan). This ullage should then be marked in the fueling log and communicated to the tank truck-unloading contractor. |  |
|  | 4 | Block the wheels of the tank truck. |  |
|  | 5 | Drip pans should be placed under all pump hose fittings (if applicable) after the hose is hooked up to the tank and prior to unloading. |  |
|  | 6 | Ensure the fill nozzle is placed in th appropriate tank appurtenance. |  |
| During unloading |
|  | 7 | Ensure that the NWS representative and the tank truck operator remain with the vehicle at all times during unloading. |  |
|  | 8 | Monitor the gauges on the tank and the truck continuously to ensure the ullage is not exceeded. If the audible high-level alarm sounds, the unloading of fuel is stopped as soon as possible. |  |
| After fuel unloading is completed |
|  | 9 | Record the amount of fuel unloaded in the log (Appendix A, Page A-1). |  |
|  | 10 | Prior to removing the fill hose from the tank, ensure that it is drained and that all drain valves are closed (if applicable). |  |
|  | 11 | Any fuel in the drip pans or spill container on the fill pipe should be poured into the tank (if it has the capacity) or disposed of appropriately (describe how it was disposed of, if applicable). |  |
|  | 12 | Inspect the tank truck prior to removing the blocks to ensure the lines have been disconnected from the tank. |  |
|  | 13 | Remove the blocks from tank truck wheels. |  |
|  | 14 | Return the catch basin outlet valve in the adjacent parking lot to the “open” position. |  |
|  | 15 | Place a copy of this fuel-unloading checklist in the SPCC plan. |  |

APPENDIX B

INSPECTION CHECKLISTS

(3 Pages)

APPENDIX B

INSPECTION FORMS

| MONTHLY INSPECTION CHECKLIST (Page 1 of 2) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| TANKS | YES | NO | NOTES |
| 1. Are there any oil stains on the outside of the tank, including the underside? |  |  |  |
| 2. Is there any oil on the ground, concrete, or asphalt around the tank? |  |  |  |
| 3. Are there any visible cracks or indications of corrosion on the tank, at fittings, joints, or seals (such as paint peeling or rust spots)? |  |  |  |
| 4. Are there any raised spots, dents, or cracks on the tank? |  |  |  |
| 5. Does it appear that the foundation has shifted or settled? |  |  |  |
| 6. Is the fuel gauge working properly? |  |  |  |
| 7. Are all vents clear so they may properly operate? |  |  |  |
| 8. If rainwater is present in secondary containment area, does sufficient capacity remain for spill control? (If applicable) |  |  |  |

| MONTHLY INSPECTION CHECKLIST (Page 2 of 2) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| B. PIPING | YES | NO | NOTES |
| 1. Is there any oil on the outside of or under any aboveground piping, hoses, fittings, or valves? |  |  |  |
| 2. Are aboveground piping, hoses, fittings, or valves in good working condition? |  |  |  |
| C. SECURITY/SAFETY/SPILL COUNTERMEASURES |  |  |  |
| 1. Are lights working properly to detect a spill at night? |  |  |  |
| 2. Are all locks in the “lock” position? |  |  |  |
| 3. Are all warning signs properly posted and readable? |  |  |  |
| 4. Are vehicle guard posts in place and properly secured (if applicable)? |  |  |  |
| 5. Are spill kits easily accessible, protected from the weather, and complete? |  |  |  |
| Corrective Actions Required: |  |  |  |

| ANNUAL INSPECTION CHECKLIST (Page 1 of 1) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| A. MONTHLY CHECKLIST | YES | NO | NOTES |
| 1. Have monthly inspection checklists been completed? |  |  |  |
| B. TANKS |  |  |  |
| 1. Are all alarms and automatic shutoff devices working properly? |  |  |  |
| 2. Is interstitial monitor functioning properly (if applicable)? |  |  |  |
| C. OTHER |  |  |  |
| 1. |  |  |  |
| Corrective Actions Required: |  |  |  |

APPENDIX C

TRAINING OUTLINE AND TITLE 40 OF THE CODE OF FEDERAL REGULATIONS SECTION 112.1 THROUGH 112.20 - OIL POLLUTION PREVENTION

(29 Pages)

APPENDIX C

OUTLINE FOR SPILL PREVENTION, CONTROL, AND COUNTERMEASURES TRAINING

Training will be provided for facility personnel at the following times:

C	System startup or whenever new equipment is installed

C	Within the first week of employment for new personnel

C	Annually

The training will include complete instruction in the elements of the facility’s Spill Prevention, Control, and Countermeasures Plan and will include the following:

A.	Pollution Control Laws, Rules, and Regulations Including a Summary of Title 40 of the Code of Federal Regulations Part 112, “Oil Pollution Prevention” (see Attachment)

B.	Fuel Storage

1.	Purpose and application of the following system elements:

a.	Tanks

b.	Piping

c.	Pumps

d.	Accessory equipment

e.	Electronic monitors

2.	Operation, maintenance, and inspection of system elements

C.	Spill Prevention

1.	Potential spill sources

2.	Spill flow direction and impact on navigable waters

3.	Procedures to prevent spills, especially during fuel unloading

D.	Spill Control

1.	Secondary containment

2.	Safety valves

3.	Pump and equipment shutoff switches

4.	Use of catch basin inlet covers or other diversionary devices

E.	Spill Countermeasures

1.	Location and use of emergency phone numbers

2.	Location and use of fire extinguishers

3.	Location and use of spill cleanup kit

4.	Stopping the leak

ATTACHMENT

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS SECTION 112.1

THROUGH 112.20 - OIL POLLUTION PREVENTION

APPENDIX D

SPILL REPORTING FORM

(1 Page)

APPENDIX D

SPILL REPORTING FORM

| 1. GENERAL |
| --- |
| Name of Facility: National Weather Service (NWS) Marquette Weather Forecast Office (WFO) | Address: 112 Airport Drive South Negaunee, MI 49866 |
| Completed By: | Organization: National Weather Service |
| Position: | Phone: |
| 2. SPILL INFORMATION |
| Date: | Time: |
| Location at Facility: | Quantity: |
| Substance Spilled: | Other: |
| 3. OUTSIDE NOTIFICATIONS |
| Agencies | Recorder at Outside Agency | Date and Time |
| Call 9-1-1 (or the local emergency agency), if there is an immediate emergency |  |  |
| NWS/NOAA: Mike Jacob: (301) 713-1838, x165 Olga Kebis: (301) 713-1838, x173 Kirt Grahl, (816) 426-3226 x470 Sherilyn Villegas, (816) 426-3925 x 263 |  |  |
| EPA NATIONAL RESPONSE CENTER or U.S. COAST GUARD: (800) 424-8802 |  |  |
| Michigan Department of Environmental Quality (800) 292-4706 (inside Michigan) (517) 373-7660 (outside Michigan) |  |  |
| 4. INFORMATION ON SOURCE AND CAUSE |
| 5. DESCRIPTION OF ENVIRONMENTAL DAMAGE |
| 6. CLEANUP ACTION(S) TAKEN |
| 7. CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |

Note:	All information must be filled in.  If something is unknown, write “unknown.”

Copies must be sent to the NWS/NOAA personnel listed above.

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS,

SECTION 112.7, WITH THIS PLAN

(1 Page)

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF 40 CFR 112.7 WITH THIS PLAN

| CFR Citation | Item | Plan Location |
| --- | --- | --- |
| 112.7(a) | Spill History | Part I.B.4 |
| 112.7(b) | Potential Spill Prediction, Volumes, and Rates | Part I.B.5 and Table 2 |
| 112.7(c) | Containment and Diversionary Structures | Part I.B.2 and Part II.B.2 |
| 112.7(d) | Secondary Containment Impracticability | Not Applicable |
| 112.7(e)(1) | Drainage Control | Part I.B.3 |
| 112.7(e)(2) | Bulk Storage Tanks and Secondary Containment |  |
| 112.7(e)(2)(I) | Tank Compatibility with Its Contents | Part II.A.1 |
| 112.7(e)(2)(ii) | Diked Area Construction and Containment for Storage Tanks | Not Applicable |
| 112.7(e)(2)(iii) | Diked Area Inspection and Drainage of Rainwater | Not Applicable |
| 112.7(e)(2)(iv) | Corrosion Protection of Buried Metallic Storage Tanks | Not Applicable |
| 112.7(e)(2)(v) | Corrosion Protection of Partially Buried Metallic Tanks | Not Applicable |
| 112.7(e)(2)(vi) | Aboveground Tank Periodic Integrity Testing | Part IV.B.1 |
| 112.7(e)(2)(vii) | Control of Leakage through Internal Heating Coils | Not Applicable |
| 112.7(e)(2)(viii) | Tank Installation Fail-safe Engineered | Part II.A.1, B.1 |
| 112.7(e)(2)(ix) | Observation of Disposal Facilities for Effluent Discharge | Not Applicable |
| 112.7(e)(2)(x) | Visible Oil Leak Corrections from Tank Seams and Gaskets | Part II.A.3 & Appendix A |
| 112.7(e)(2)(xi) | Appropriate Position of Mobile or Portable Tanks | Not Applicable |
| 112.7(e)(3) | Facility Transfer Operations |  |
| 112.7(e)(3)(i) | Buried Piping Installation Protection and Examination | Part II.A.1 & Appendix A |
| 112.7(e)(3)(ii) | Not-in-service and Standby Terminal Connections | Not Applicable |
| 112.7(e)(3)(iii) | Pipe Support Designs | Not Applicable |
| 112.7(e)(3)(iv) | Aboveground Valve and Pipeline Examination | Not Applicable |
| 112.7(e)(3)(v) | Aboveground Piping Protection from Vehicular Traffic | Not Applicable |
| 112.7(e)(4) | Facility Truck Unloading Operations | Part II.A.2 |
| 112.7(e)(5-7) | Oil Production Facilities (Onshore) and Oil Drilling, Production, or Work over Facilities (On Shore and Offshore) | Not Applicable |
| 112.7(e)(8) | Inspections and Record Keeping | Part II.A.3 |
| 112.7(e)(9) | Security |  |
| 112.7(e)(9)(i) | Fencing | Part II.A.4 |
| 112.7(e)(9)(ii) | Flow Valves Locked | Not Applicable |
| 112.7(e)(9)(iii) | Starter Controls Locked | Not Applicable |
| 112.7(e)(9)(iv) | Pipeline Loading and Unloading Connections Securely Capped | Not Applicable |
| 112.7(e)(9)(v) | Lighting Adequate to Detect Spills | Part II.A.4 |
| 112.7(e)(10) | Training |  |
| 112.7(e)(10)(i) | Personnel Instructions | Part II.A.5 & Appendix C |
| 112.7(e)(10)(ii) | Designated Person Responsible for Spill Prevention | Page i |
| 112.7(e)(10)(iii) | Spill Prevention Briefings | Part IV.B.2 |

Note:	CFR	Code of Federal Regulations