Volker Sigwarth						Tel.: Skan 	+41 (0)61 485 4444

Skan AG						Tel.: direct	+41 (0)61 485 4470

Binningerstrasse 116					Fax.:		+41 (0)61 485 4445

CH- 4123 Allschwil					E-Mail:		Volker.Sigwarth@skan.ch

Switzerland

Comments on

FDA Draft Guidance:

“ Sterile Drug Products Produced by Aseptic Processing - 
Current Good Manufacturing Practice”

APPENDIX 1: ASEPTIC PROCESSING ISOLATORS

Docket No. 2003D-0382

Global Comment:

The final version of this guidance will represent a leading voice in the application and use of isolator technology for aseptic processing. Therefore the finalization of this guidance should be proceeded with high priority by the FDA, to establish a valuable and useful foundation for the industry to design, implement and use isolator technology in aseptic processing.

Specific Comments:

Line 1544 to 1552

Useful paragraph, the following points could add significant value concerning the integrity of isolator systems:

- A rational of the isolator integrity (e.g. quantified as leakage rate) should be established based on the isolator design and its capability of maintaining the requisite environmental conditions within the isolator.

- A mechanical / physical integrity test of the isolator system should also be performed routinely.

- A significant breach of an isolator could then be defined as “exceeding the defined leakage rate”

- Transfer system should also be considered regarding integrity and should also be part of the maintenance program of an isolator system.

Line 1556 to 1562

Useful and practical paragraph, the following point could add value concerning the glove integrity:

- A rational of the glove integrity (e.g. quantified as leakage rate) should be established.

- Only based on a defined, quantifiable value the result of a mechanical / physical glove integrity test can be useful evaluated and justified.

Line 1573 to 1575

The following point could add value concerning isolator openings:

- The capability of these openings to maintain the requisite environmental conditions within the isolator should be carefully considered.

- The parameters which ensures the proper functionality of such opening should be continuously monitored.

Line 1568

Concerning the design of isolators the following point could add value:

- The zone where aseptic processing takes place and in which the requisite environmental conditions should be maintained and monitored should be clearly defined (by the design of an isolator).

Line 1577 to 1578

Even by using isolator technology it should not be recommended to place an aseptic processing line in a strictly turbulent isolator system. Any aseptic processing will lead at least to the generation of particles. The impact of these particles to the aseptic process is more or less uncontrolled in a turbulent isolator system. This problem can be solved by using unidirectional air flow.

The following change of this lines could add value:

- Turbulent flow is normally acceptable within closed isolators, which are generally compact in size and do not house processing lines, e.g. sterility test- and transfer- isolators.

Line 1581 to 1582

In practice and for economical reasons, with isolator using unidirectional air flow, parts of the air are recirculated from the bottom of the critical zone via a return air system through the terminal filter again into the top of the critical zone. Additionally fresh air is supplied by an intake air unit with dedicated filter system and exhaust air is handled by an additional exhaust air unit with dedicated filter system.

The following point could reduce potential, confusing discussions:

- In most sound designs, air showers over the critical zone once and then is systematically exhausted out of the critical zone.

Line 1582

The following point could add value concerning the chosen air velocity with in the critical zone:

- The air velocity of the unidirectional air flow within the critical zone of an isolator should be based on its capability to protected the individual aseptic process from potential contamination.

- The capability of the chosen air velocity to protected the individual aseptic process from potential contamination should be supported by qualification studies.

Line 1587 to 1589

The following point could add value concerning the selection of construction materials:

- The suitability of any construction material, which is incorporated into to decontamination process of the critical zone of the isolator system, to the intended decontamination method (process) should be carefully considered.

Line 1615 to 1616

Here it would be helpful to point out, if this also includes isolators for sterility testing.

Such isolator could be placed in a room which is unclassified but controlled an of restricted access.

Line 1620 to 1633

To this paragraph the following points could add value:

- The design of transfer systems and any transferring process should not compromise the requisite environmental conditions within the critical zone of the isolator.

- Weak points of transfer systems should be carefully considered and a clear procedure should be established to minimize a potential risk during routing handling of transfer systems.

Line 1642

The following points could add value concerning the decontamination of isolators:

- The decontamination agent should enter the critical zone of the isolator through the terminal intake air filter.

This would ensure, that the terminal intake air filter is decontaminated on both sides at each decontamination cycle.

- The chosen residual concentration of the decontamination agent should not have any impact on the product quality and on any environmental monitoring result.

Often an underestimated issue in using isolator technology.

Line 1657 to 1659

“ The characteristics of these agents generally preclude the reliable use of statistical methods (e. g. fractional negative) to determine the process lethality (Ref. 14).”

This sentences is not clear enough and could be misleading. Here it should be more clear separated between cycle development and final cycle validation.

During cycle development stage the proper use of fractional negative methods can add significant value to evaluate reliable cycle parameters, to justify the suitability of the used biological indicator and finally determine the worst case positions regarding decontamination effect within an isolator system.

The proper use of fractional negative studies during cycle development could help to reach the “…thorough determination of cycle capability.”, required in line 1656 to 1657.

During final cycle validation the use of fractional negative methods should clearly be precluded, (for any inactivation process) because it would never be possible to justify if the fractional results comes from a low killing position, a weak decontamination cycle or an unsuitable biological indicator.

But to develop a decontamination cycle for bottom up and to quantify its inactivation effect over each single process step, including the determination of worst case positions regarding the decontamination effect, the use of fractional negative methods, if proper applied and understood, is a powerful an scientific based tool for process development.

Line 1662 to 1663

“ Normally, a four- to six- log reduction can be justified depending on the application”

Here two point should be considered carefully:

- To define the required process lethality the commonly used term “six- log reduction” should be replaced by “total kill of a six log population” (…of an appropriate test organism using a suitable biological indicator). This term is first from a scientific point of view a clear quantification of a process lethality and second it defines clearly what is expected by using the term “six- log reduction”.
Also this definition goes in line with precluding fractional negative methods for final cycle validation. A “six- log reduction” could be clearly demonstrated using fractional negative methods, the “total kill of a six log population” could never be demonstrated by fractional negative methods.

Remark:

The reliable total kill of a defined initial population requires an inactivation effect of four log steps more than the initial population, e.g. to achieve a reliable total kill of a six log population requires at least an inactivation effect of ten log steps

- For the most aseptic processing applications using isolator technology, especially if processing lines are isolated the required target process lethality on the inner surfaces of the critical zone should be defined as: ”total kill of a six log population of an appropriate test organism using a suitable biological indicator”
In mostly all aseptic processing application / lines some parts has at least secondary contact with the product (e.g. stopper hoppers, stopper lines, conveying systems etc.) and the gloves are used for manipulations or intervention during aseptic processing. Therefore a four log reduction seems to be inadequate for the inner surfaces of the critical zone. This definition goes also in line with line 1692 to 1694 of the draft guidance.
Furthermore to proof a total kill of a six log population is even from an economical point of view possible in state of the art isolator technology.

Line 1664 to 1666

The following point could add value to define the process lethality of a decontamination process used to transferred material into an aseptic isolator.

- The capability of a decontamination process used to transfer material into the critical zone of an aseptic isolator should be able to achieve the same target lethality on the surface of the transferred material than the defined target lethality of the inner surfaces of the isolator, based on the bioload (bioburden) of the transferred material.

- The bioload (bioburden) of those materials has to be carefully considered and monitored routinely.

- Even if the bioload (bioburden) of the transferred material is significant low, the minimum process lethality of the decontamination (transfer) process should be defined as ”total kill of a four log population of an appropriate test organism using a suitable biological indicator”.

Example:

As described above, a proven total kill of a four log population requires a process lethality of at least eight log steps (four log steps more than the initial population to be inactivated).

Based on an estimated material bioload of e.g. one log per square inch, such a process lethality would lead to a “surface quality” on the transferred material which goes in line with the inner surface of the isolator.

Line 1694

In correspondence to line 1662 to 1663 the following definition of the target lethality could add value:

- ”total kill of a six log population of an appropriate test organism using a suitable biological indicator” instead of “six-log reduction”.

Line 1681

The following point could add value concerning an isolator breach.

- A breach of isolator integrity, which may leads to a contamination of the critical zone of the isolator, should lead to a decontamination cycle.

Best regards,

Volker Sigwarth, Skan AG