## 25F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 041
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3344.3693
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3418.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3449.05 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 3432.31 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 3553.12 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3449.05 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 3647.22 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 3527.93 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2975.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3536.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 454.27 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3553.12 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3432.31 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3694.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3536.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3704 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3704 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3647.22 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3077.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 3169.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 525.38 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3077.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3418.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2975.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3527.93 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 618.07 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3694.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 525.38 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3169.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 454.27 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 618.07 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 041
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2656.6433
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3386.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3392.07 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 3409.01 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 3520.76 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 3392.07 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3589.79 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 3486.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2226.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3494.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -602.19 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3520.76 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 3409.01 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3655.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3494.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3396.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3396.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3589.79 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 2324.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2433.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -546.67 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2324.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3386.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2226.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3486.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -483.46 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3655.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -546.67 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2433.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -602.19 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -483.46 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 041
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2414.4513
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3297.31 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3340.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 3325.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 3166.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3340.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 3466.84 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 140 | 3132.75 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 934.01 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3143.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -1953.33 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3166.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3325.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3310.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3143.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3469.69 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3469.69 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
525 | 775 | 3466.84 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 1023.33 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1125.51 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -1801.99 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1023.33 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3297.31 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 934.01 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3132.75 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -1783.39 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3310.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -1801.99 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1125.51 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -1953.33 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -1783.39 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 041
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2931.5733
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2796.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2840.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2832.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2926.15 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2840.13 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 3117.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2883.97 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1688.64 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2894.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -1387.95 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2926.15 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2832.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3080.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2894.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3084.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3084.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3117.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 1795.01 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1927.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -1300.15 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1795.01 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2796.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1688.64 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2883.97 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -1235.32 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3080.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -1300.15 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1927.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -1387.95 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -1235.32 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 041
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3282.498
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2663.05 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2709.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2695.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2792.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2709.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2982.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2770.25 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1808.31 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2792.58 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -1324.5 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2792.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2695.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2965.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2792.58 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2975.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2975.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2982.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 1890.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2008.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -1244.5 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1890.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2663.05 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1808.31 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2770.25 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -1026.8 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2965.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | -1244.5 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2008.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -1324.5 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -1026.8 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
G0 | 3418.41 | 3386.37 | 3297.31 | 2796.86 | 2663.05
G1 | 3432.31 | 3409.01 | 3325.27 | 2832.11 | 2695.06 | Season/Year: | WINTER 2009
G2 | 3449.05 | 3392.07 | 3340.04 | 2840.13 | 2709.51 | Direction: | South-to-North (SN)
G3 | 3527.93 | 3486.32 | 3132.75 | 2883.97 | 2770.25 | Case Loads: | Light Loads
G4 | 3536.39 | 3494.14 | 3143.91 | 2894.86 | 2792.58 | Outage: | 041
G5 | 3553.12 | 3520.76 | 3166.41 | 2926.15 | 2792.91 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3694.04 | 3655.37 | 3310.21 | 3080.53 | 2965.66 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3704 | 3396.33 | 3469.69 | 3084.33 | 2975.2 | Study Person: | JGO7470
G8 | 3647.22 | 3589.79 | 3466.84 | 3117.02 | 2982.49 | Source: | 041WINTER09v1SNL
G9 | 3169.94 | 2433.36 | 1125.51 | 1927.42 | 2008.01
G10 | 3077.58 | 2324.02 | 1023.33 | 1795.01 | 1890.81
G11 | 2975.25 | 2226.84 | 934.01 | 1688.64 | 1808.31
G12 | 618.07 | -483.46 | -1783.39 | -1235.32 | -1026.8
G13 | 525.38 | -546.67 | -1801.99 | -1300.15 | -1244.5
G14 | 454.27 | -602.19 | -1953.33 | -1387.95 | -1324.5
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 041 | Sedro Woolley (PSE) Tap section of Murray - Custer #1 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3344.3693 | 3418.41 | 3432.31 | 3449.05 | 3527.93 | 3536.39 | 3553.12 | 3694.04 | 3704 | 3647.22 | 3169.94 | 3077.58 | 2975.25 | 618.07 | 525.38 | 454.27
35F | 2656.6433 | 3386.37 | 3409.01 | 3392.07 | 3486.32 | 3494.14 | 3520.76 | 3655.37 | 3396.33 | 3589.79 | 2433.36 | 2324.02 | 2226.84 | -483.46 | -546.67 | -602.19
45F | 2414.4513 | 3297.31 | 3325.27 | 3340.04 | 3132.75 | 3143.91 | 3166.41 | 3310.21 | 3469.69 | 3466.84 | 1125.51 | 1023.33 | 934.01 | -1783.39 | -1801.99 | -1953.33
60F | 2931.5733 | 2796.86 | 2832.11 | 2840.13 | 2883.97 | 2894.86 | 2926.15 | 3080.53 | 3084.33 | 3117.02 | 1927.42 | 1795.01 | 1688.64 | -1235.32 | -1300.15 | -1387.95
70F | 3282.498 | 2663.05 | 2695.06 | 2709.51 | 2770.25 | 2792.58 | 2792.91 | 2965.66 | 2975.2 | 2982.49 | 2008.01 | 1890.81 | 1808.31 | -1026.8 | -1244.5 | -1324.5

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3417.67 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2689.28 | -2689.89 | 3415.95 | 3418.41 | -2129.53 | CTG_FAIL_IN_FULL
G1 | 3432.44 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2690.82 | -2690.66 | 3345.72 | 3432.31 | -2120 | CTG_FAIL_IN_FULL
G2 | 3448.87 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2682.98 | -2682.77 | 3358.5 | 3449.05 | -2092.9 | CTG_FAIL_IN_FULL
G3 | 3528.15 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2726.67 | -2728.43 | 3413.94 | 3527.93 | -2134.54 | CTG_FAIL_IN_FULL
G4 | 3536.06 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2699.2 | -2698.87 | 3342.43 | 3536.39 | -2118.02 | CTG_FAIL_IN_FULL
G5 | 3552.76 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2692.81 | -2692.46 | 3355.59 | 3553.12 | -2093.4 | CTG_FAIL_IN_FULL
G6 | 3693.56 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2702.21 | -2701.76 | 3409.66 | 3694.04 | -2124.95 | CTG_FAIL_IN_FULL
G7 | 3703.63 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2689.92 | -2689.53 | 3340.79 | 3704 | -2095.6 | CTG_FAIL_IN_FULL
G8 | 3646.87 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3607.03 | -3604.69 | 3349.97 | 3647.22 | -2037.36 | FULL
G9 | 3170.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -474.53 | -474.48 | 3370.8 | 3169.94 | -1614.82 | FULL
G10 | 3077.74 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -472.13 | -472.03 | 3297.2 | 3077.58 | -1529.58 | FULL
G11 | 2975.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -470.88 | -470.87 | 3306.17 | 2975.25 | -1443.67 | FULL
G12 | 618.39 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -451.62 | -451.61 | 3324.91 | 618.07 | -14.52 | FULL
G13 | 526.08 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -451.88 | -451.89 | 3258.87 | 525.38 | 64.98 | FULL
G14 | 453.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -452.94 | -452.84 | 3275.04 | 454.27 | 133.13 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3386.5 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2628.65 | -2626.96 | 2724.9 | 3386.37 | -2070.76 | CTG_FAIL_IN_FULL
G1 | 3411.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2628.52 | -2627.47 | 2656 | 3409.01 | -2052.64 | CTG_FAIL_IN_FULL
G2 | 3392.23 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.16 | 508.79 | 508.57 | 2667.06 | 3392.07 | -2014.77 | CTG_FAIL_IN_FULL
G3 | 3486.12 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2631.78 | -2631.56 | 2723.28 | 3486.32 | -2069.59 | CTG_FAIL_IN_FULL
G4 | 3494.3 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2622.74 | -2621.65 | 2654.7 | 3494.14 | -2042.86 | CTG_FAIL_IN_FULL
G5 | 3520.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.16 | 510.39 | 510.34 | 2666.76 | 3520.76 | -2030.9 | CTG_FAIL_IN_FULL
G6 | 3655.24 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2625.73 | -2625.53 | 2720.95 | 3655.37 | -2052.75 | CTG_FAIL_IN_FULL
G7 | 3396.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2405.9 | -2403.13 | 2645.43 | 3396.33 | -1872.22 | FULL
G8 | 3589.69 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3551.92 | -3550.7 | 2663.11 | 3589.79 | -1952.05 | FULL
G9 | 2434.78 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -458.32 | -458.23 | 2664.33 | 2433.36 | -1132.22 | FULL
G10 | 2325.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -453.02 | -453.05 | 2592.13 | 2324.02 | -1046.27 | FULL
G11 | 2226.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -454.31 | -454.28 | 2605.32 | 2226.84 | -963.79 | FULL
G12 | -483.58 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -449.05 | -449.01 | 2657.85 | -483.46 | 641.91 | FULL
G13 | -546.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -450.6 | -450.47 | 2594.42 | -546.67 | 705.66 | FULL
G14 | -603.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -452.24 | -452.18 | 2613.41 | -602.19 | 765.21 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3295.48 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2531.27 | -2531.75 | 2475.7 | 3297.31 | -1982.59 | CTG_FAIL_IN_FULL
G1 | 3326.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2542.82 | -2543.06 | 2406.04 | 3325.27 | -1973.99 | CTG_FAIL_IN_FULL
G2 | 3340.47 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.03 | -2539.21 | -2539.38 | 2419.69 | 3340.04 | -1952.55 | CTG_FAIL_IN_FULL
G3 | 3131.48 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2336.43 | -2335.11 | 2467 | 3132.75 | -1833.06 | FULL
G4 | 3142.58 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2327.85 | -2329.27 | 2398.08 | 3143.91 | -1808.42 | FULL
G5 | 3166.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2335.72 | -2336.45 | 2413.4 | 3166.41 | -1788.04 | FULL
G6 | 3308.74 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2328.37 | -2326.35 | 2467.49 | 3310.21 | -1806.3 | FULL
G7 | 3470.2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3434.11 | 3436.07 | 2402.15 | 3469.69 | -1871.71 | FULL
G8 | 3465.37 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3429.53 | 3430.28 | 2414.34 | 3466.84 | -1847.18 | FULL
G9 | 1126.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -407.88 | -407.84 | 2403.18 | 1125.51 | -364.94 | FULL
G10 | 1023.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -407.69 | -407.65 | 2336.14 | 1023.33 | -278.64 | FULL
G11 | 934.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -407.92 | -407.9 | 2351.76 | 934.01 | -200.3 | FULL
G12 | -1783.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -424.9 | -424.76 | 2453.25 | -1783.39 | 1383.15 | FULL
G13 | -1801.98 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -427.93 | -428.04 | 2392.89 | -1801.99 | 1418.1 | FULL
G14 | -1953.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -426.83 | -426.68 | 2415.66 | -1953.33 | 1529.5 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2797.05 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2216.54 | -2217.44 | 2987.64 | 2796.86 | -1734 | FULL
G1 | 2832.32 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2227.76 | -2226.33 | 2918.18 | 2832.11 | -1718.54 | FULL
G2 | 2840.54 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2222.51 | -2220.66 | 2931.77 | 2840.13 | -1697.62 | FULL
G3 | 2884.48 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2267.09 | -2268.1 | 2987.43 | 2883.97 | -1726.5 | FULL
G4 | 2895.42 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2269.49 | -2267.32 | 2917.49 | 2894.86 | -1705.41 | FULL
G5 | 2926.66 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2268.51 | -2269.81 | 2931.75 | 2926.15 | -1693.9 | FULL
G6 | 3082.13 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2225.74 | -2226.12 | 2985.79 | 3080.53 | -1712.67 | FULL
G7 | 3084.32 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2259.49 | -2260.93 | 2919.04 | 3084.33 | -1687.76 | FULL
G8 | 3117.3 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2216.17 | -2217.35 | 2930.55 | 3117.02 | -1680.92 | FULL
G9 | 1927.21 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -419.39 | -419.33 | 2938.93 | 1927.42 | -854.3 | FULL
G10 | 1795.96 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -415.42 | -415.37 | 2868.99 | 1795.01 | -751.33 | FULL
G11 | 1689.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -414.63 | -414.59 | 2881.79 | 1688.64 | -664.54 | FULL
G12 | -1235.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -422.36 | -422.42 | 2959.68 | -1235.32 | 1049.52 | FULL
G13 | -1300.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -423.72 | -423.65 | 2897.02 | -1300.15 | 1104.24 | FULL
G14 | -1388.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -424.15 | -424.29 | 2917.55 | -1387.95 | 1185.58 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2663.13 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2143.85 | -2144.36 | 3337.09 | 2663.05 | -1657.03 | FULL
G1 | 2695.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2159.11 | -2160.8 | 3266.95 | 2695.06 | -1655.08 | FULL
G2 | 2709.59 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2148.7 | -2147.84 | 3279.75 | 2709.51 | -1628 | FULL
G3 | 2770.4 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2146.99 | -2147.79 | 3336.32 | 2770.25 | -1655.61 | FULL
G4 | 2792.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2150.42 | -2148.76 | 3266.9 | 2792.58 | -1641.81 | FULL
G5 | 2793.05 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2147.13 | -2147.99 | 3279.3 | 2792.91 | -1616.7 | FULL
G6 | 2965.81 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2159.39 | -2157.65 | 3335.9 | 2965.66 | -1658.45 | FULL
G7 | 2975.41 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2155.03 | -2153.87 | 3265.9 | 2975.2 | -1631.67 | FULL
G8 | 2982.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.44 | -2152.69 | -2153.57 | 3279.24 | 2982.49 | -1608.61 | FULL
G9 | 2008.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -418.89 | -418.82 | 3296.95 | 2008.01 | -904.41 | FULL
G10 | 1891.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -417.1 | -417.02 | 3226.32 | 1890.81 | -808.03 | FULL
G11 | 1811 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -418.81 | -418.77 | 3238.89 | 1808.31 | -734.54 | FULL
G12 | -1028.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -426.57 | -426.41 | 3310.29 | -1026.8 | 922.1 | FULL
G13 | -1246.08 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -422.01 | -422.11 | 3248.78 | -1244.5 | 1074.24 | FULL
G14 | -1326.07 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | -5.24 | -422.75 | -422.61 | 3268.89 | -1324.5 | 1146.68 | FULL
041WINTER09v1SNL