Docket ID No.EPA-HQ-OPA-2007-0584

Fiberglass Tank & Pipe Institute ~ December 4, 2007 Comments

Environmental Protection Agency

[EPA-HQ-OPA-2007-0584; FRL-8479-7]

RIN 2050-AG16

Oil Pollution Prevention; Spill Prevention, Control, and Countermeasures Rule Requirements – Amendments

Following are comments submitted by the Fiberglass Tank & Pipe Institute, 11150 S. Wilcrest Dr., Suite 101, Houston, Texas 77099-4343 Tel 281 568 4100 Fax 281 568 9998, Executive Director Sullivan D. Curran, on the proposed subject rule published in the Federal Register on October 15, 2007.

The Fiberglass Tank & Pipe Institute (Institute) appreciates the opportunity to comment on the proposed changes to the Spill Prevention, Control and Countermeasure (SPCC) regulations. The Institute was incorporated in 1987 as a non-profit trade association, and it represents the major manufacturers of underground and aboveground fiberglass tanks and vessels in the United States. In addition to aboveground stainless and lined steel tanks, fiberglass tanks and piping are used to store and handle oily water, animal fats and vegetable oils (AFVO). Thus, while not specifically mentioned in the Agency’s 40 CFR Part 112 proposal, such fiberglass tanks and piping are subject to the proposed regulations. This being the case, the Agency needs to include the fiberglass industry aboveground tank integrity standard FTPI 2007-1 Recommended Practice for the In-service Inspections of Aboveground Atmospheric Fiberglass Reinforced Plastic (FRP) Tanks and Vessels© (copy attached).

Following are the Institute’s comments, consistent with EPA’s request for additional information:

V.J. Integrity Testing

The Institute agrees that the owners or operators of all types of facilities subject to either 112.8(c) (6) or 112.12(c)(6) should select particular testing methods to comply with these requirements based on industry inspection standards.  EPA, therefore, should include FTPI 2007-1 for fiberglass above ground storage tanks and vessels in either the rule itself or the preamble to the final rule. The Steel Tank Institute’s recommended practice (STI SP001) for aboveground tank inspections does not cover fiberglass tanks and vessels. Fiberglass tanks and vessels are a growing part of the aboveground storage market.

A summary of FTPI 2007-1 is shown below and does not apply to portable containers, but instead to tanks or vessels greater than 10,000 gallons. Further, the summary describes that fiberglass inspector qualifications limit certification to those who have experience with the inspection of fiberglass tanks or vessels. Of significance, this excludes a PE-certified explanation of environmental equivalence and deviation from an industry standard.

V.K. Animal Fats ad Vegetable Oils

EPA’s proposal essentially would forego integrity testing of bulk storage containers subject to Food and Drug Administration (FDA) regulation and which meet four other criteria by conducting visual inspections will allow for the continuation of visual inspections of tanks:

- evidence of material stress;

- when leaks are occurring;

- when there is a change of service to a dissimilar stored material;

- when a tank or vessel is relocated; and,

- by an untrained or certified person.

The Institute FTPI 2007-1 recommends a certified external tank and vessel inspector every 10 years for tanks/vessels greater than 10,000 gallons capacity when non-hazardous substances are stored. And, annual inspections by a Preventive Maintenance inspector who was shown to be familiar with the equipment and the FTPI 2007-1 content. The EPA proposal is overly lax and should be reconsidered.

K.1. Differentiation Criteria

K.1.i Container Foundations. FDA

No comment other than FTPI 2007-1 includes an inspection of the tank or vessel foundation.

K.1.ii Container Support Structures. FDA

No comment other than FTPI 2007-1 includes an inspection of the tank or vessel support structures.

K.1.iii. Container Itself

Internal Corrosion: While the FDA requires the initial design, construction and use to preclude adulteration of food, there is no assurance that it is “likely to prevent the corrosion of the internal contact surface….” as stated. Thus, FTPI 2007-1 recommends an integrity inspection after 20 years for tanks and vessels greater than 10,000 gallons capacity or when other warning signs appear as described above under K. This requirement is of more significance for carbon steel tanks that are interior lined. Institute experience shows that manufacturing defects, overheating or other processing problems will over time reduce the integrity of tank and vessel interior such that an integrity inspection is required.

External Corrosion:  No comment other than FTPI 2007-1 includes a monthly and annual visual inspection of the tank or vessel exterior.

K.1.c. Containers Made from Austenitic Stainless Steel

The Institute supports limiting consideration of alternative integrity testing to only homogenous Austenitic stainless steel tanks and vessels (see comment above regarding lined carbon steel tanks).

K.1.d. Containers with No External Insulation

The Institute supports limiting consideration of alternative integrity testing no containers with no external insulation. Institute experience is that external insulation is a barrier to effective visual examination and is familiar with insulated tank ruptures occurring within a month of an exterior inspection.

K.1.e. Shop-Fabricated Containers

The Institute does not support the rationale given for an alternative integrity testing option for only shop-fabricated containers. While field-erected tanks are larger than those of shop-fabricated tanks, they are designed and constructed accordingly, meet long standing industry standards and there are no data to support a higher failure rate. Further, both the STI SP001 and the FTPI 2007-1 establish the frequency for visual inspections that is applicable to field-erected tanks and vessels. The Agency should not use this as a valid reason to limit consideration of alternative integrity testing to only shop-fabricated containers.

K.2. Required Recordkeeping

No comment other than FTPI 2007-1 includes monthly preventive maintenance and integrity testing record keeping check lists that meet SPCC Plan requirements.

K. 2. Integrity Testing for containers located indoors vs. outdoors

FTPI 2007-1, like API 653 and STI SP001, does not differentiate inspection requirements for indoor versus outdoor containers. The exterior roof and shell of fiberglass tanks and vessels are inherently corrosion resistant, and whether they are located indoors or outdoors is not a factor when visually or integrity inspected.

Following is background information on the Fiberglass Tank & Pipe Institute and a summary of FTPI 2007-1 Recommended Practice for the In-service Inspections of Aboveground Atmospheric Fiberglass Reinforced Plastic (FRP) Tanks and Vessels©:

Institute Purpose: The Institute provides a forum through which the fiberglass reinforced thermoset plastic (FRP) industry can work together effectively toward the common goal of advancing the use of all fiberglass products in the tank and piping marketplace, i. e., coordinating studies and statistics, combining talents and resources to provide standard-setting organizations with superior technical data, and disseminate information to the government, industry and the public. Published information is available from the Institute web site at www.fiberglasstankandpipe.com.

Member company products: Underground fiberglass tanks are located  in over 50% of the nations gasoline refueling facilities whereas aboveground fiberglass tanks are used to store oily water, animal fats, vegetable oils as well as industrial chemicals such as acids and caustics. In addition, the Institute represents the major manufacturers of small diameter fiberglass gasoline piping systems found underground at most of the nations vehicle refueling facilities and large diameter piping up to 155 inches in diameter for municipal potable and wastewater applications.

FTPI 2007-1 Recommended Practice for the In-service Inspections of Aboveground Atmospheric Fiberglass Reinforced Plastic (FRP) Tanks and Vessels©

The Fiberglass Tank & Pipe Institute published FTPI 2007-1 in October 2007. This Recommended Practice was developed over the past three years in response to requests by aboveground fiberglass tank users, engineering companies and governmental bodies. Members of the Institute and an industry peer review group have shared their fabrication, operation and maintenance expertise on aboveground fiberglass tank in corrosion resistant applications to make this publication possible.

Peer review Group: The Recommended Practice peer review group included the Environmental Protection Agency; US Office of Emergency Management; N. Y. State Dept. of Environmental Conservation Spill Response & Bulk Storage Tank Section; Lyondell Chemical Inc.; two fiberglass Inspection companies; three fiberglass Consultants and Engineering companies; and, both Institute and non-Institute aboveground fiberglass tank manufacturers.

FTPI 2007-1: The Recommended Practice is a 27 page document that includes recommended inspector qualifications, periodic preventive maintenance inspections, certified external inspections, certified integrity inspections, internal inspections and alternate non-intrusive inspection methods. The document also includes report forms for monthly, annual and periodic preventive maintenance and certified inspections and a section on aboveground fiberglass tank fabrication information.

# The purpose of this Recommended Practice is to provide procedures for conducting periodic preventive maintenance (PM) inspections and certified inspections of fiberglass reinforced plastic (FRP) atmospheric tanks and vessels in corrosive industrial and commercial service after a set period of time and when there is a change of service. The procedures are intended to:

- minimize maintenance costs,

- ensure compliance with environmental and safety requirements,

- minimize system failures and

- ensure that proper engineering, construction and maintenance practices are in place.

PM Inspector Qualifications: The Preventive Maintenance (PM) inspector shall be a person familiar with the equipment to be inspected, this FTPI 2007-1 Recommended Practice, and is designated by the equipment owner or operator. Periodic preventive maintenance tank and vessel inspections are the process of ongoing data collection through exterior inspections using investigative tools and methods. The inspection data should be documented in a manner that provides for a long-term trend evaluation.

PM Inspections: Preventive Maintenance inspectors are required to document tank or vessel inspections in written reports using where applicable the minimum information included in FTPI 2007-1 standardized check lists. In addition, the reports shall contain conclusions, recommendations and supplemental sketches with dimensions and/or photographs. The photographs shall have a minimum resolution of 3 mega pixels with the photograph locations identified.

Certified External and Internal Inspector Qualifications:  The certified inspectors shall have education and experience equal to at least one of the following:

- A degree in engineering plus one year of experience in the inspection of FRP tanks or vessels.

- A 2-year certificate in engineering or technology from a technical college, and two years of experience in manufacturing, repair, operation or inspection of FRP tanks or vessels manufactured in accordance with applicable standards or codes.

- The equivalent of a high school education, and three years of experience in manufacturing, repair, operation or inspection of FRP tanks or vessels manufactured in accordance with applicable standards or codes.

Certified External Inspections: Certified external tank and vessel inspections shall be performed by a certified tank or vessel inspector as follows:

- every 5 years for tanks or vessels in Hazardous Substance service, or

- every 10 years for tanks/vessels greater than 10,000 gallons capacity and in other service, or

- if evidence of material stress appears, or

- tank or vessel leaks occur, or

- before there is a change in service to a dissimilar stored material, or

- if a tank or vessel is relocated.

Certified Integrity Inspections: Integrity tank and vessel inspections shall be performed by a certified tank or vessel inspector as follows:

- every 20 years for tanks/vessels in Hazardous Substance service, or

- every 20 years for tanks/vessels greater than 10,000 gallons capacity and in other service, or

- if evidence of material stress appears, or

- tank or vessel leaks occur, or

- before there is a change in service to a dissimilar stored material. or

- if a tank or vessel is relocated.

The report of Certified Inspections shall be delivered to the owner. These reports shall include the inspector’s recommendations, which shall include one or more of the following:

- No remedial action

- Further investigation or analysis

- Repairs

- Changes in tank or vessel operation

- Replacement

* * * * *

The Institute appreciates this opportunity to present its views on the proposed SPCC changes.  Please feel free to contact us for additional information as needed

Sincerely,

Hardcopy signed and mailed to EPA Docket

Sullivan D. Curran P. E.

CC: FTPI 2007-1 Recommended Practice

Submitted in hardcopy format to Docket ID No.EPA-HQ-OPA-2007-0584