HOISTING AND RIGGING

1.0	Objective

The objective of this surveillance is to examine hoisting and rigging operations to ensure that safe equipment and work practices are being used.  The surveillance includes verification that hoisting and rigging work is performed in accordance with DOE requirements and best practices.

2.0	References

2.1	DOE O 440.1A, Worker Protection Management For Doe Federal And Contractor Employees

2.2	DOE-RL-92-36, Hanford Site Hoisting and Rigging Manual

NOTE

The DOE Hoisting and Rigging Manual should be used as the primary reference for this surveillance.

1

3.0	Requirements Implemented

This surveillance is conducted to implement the RL Functions, Responsibilities, and Authorities Manual (FRAM) item No. 2504.

4.0	Surveillance Activities

During this surveillance, the Facility Representative (FR) may evaluate one or more aspects of a facility's hoisting and rigging program.  The surveillance may involve field observations of a lift, field review of equipment, a program evaluation, or a review of hoisting and rigging records.  Choose one or more of the sections identified below to evaluate, as appropriate.  After each question, the Hoisting and Rigging manual reference is included in brackets.  Prior to initiating a surveillance, it is highly recommended that the FR review the complete sections of DOE-RL-92-36, "Hanford Site Hoisting and Rigging Manual," to obtain additional information and review all detailed requirements imposed on the activity or program.  This manual can be found at http://www.hanford.gov/docs/rl9236/rl9236tc.htm.

Surveillance Guideline

HOISTING AND RIGGING

Surveillance No.:

Facility:

Date Completed:

HANFORD SITE HOISTING AND RIGGING MANUAL SECTIONS

Section 2, Responsibilities

Yes  No   N/A

___  ___  ___	1.	Is the crane's rated capacity marked on each side of the crane?

___  ___  ___	2.	Is a supervisor or manager responsible for H&R operations at this facility?        [ 2.2.1]

___  ___  ___	3.	Is a supervisor or manager assigned responsibility for inspection, maintenance, and repair of H&R equipment and components? [2.2.2]

___  ___  ___	4.	Do responsible inspectors, maintenance, and test personnel have access to adequate information?  Such information would include: operating instructions; maintenance and repair information (instructions); manufacturer's recommendations concerning lubrication; wiring diagrams.  [2.2.2.c]

___  ___  ___	5.	Is a Person-In-Charge (PIC) assigned for each critical lift? [2.2.3]

___  ___  ___	6.	Is a designated leader appointed to all H&R activities, including critical and non-critical ordinary lifts, that require more than one person?  [2.2.4]

___  ___  ___	7.	Does a responsible safety organization monitor your H&R operations to ensure that they are performed safely? [2.3.1]

___  ___  ___	8.	Do all personnel involved in a hoisting and rigging activity have a clear understanding of their duties and responsibilities?  [2.2.3 through 2.2.6]

___  ___  ___	9.	Other

Section 3, Critical Lifts

Yes  No   N/A

___  ___  ___	1.	Do critical lift procedures contain adequate and appropriate information? [3.4.1]

___  ___  ___	2.	Are critical lift procedures (and any revision) reviewed and approved by the author, responsible manager, PIC, and the Safety Organization?  [3.4.2/3]

___  ___  ___	3.	Are pre-lift meeting(s) held to review procedures and resolve questions before making critical lifts?  [3.5]

___  ___  ___	4.	Are pre-lift meetings documented?  [3.6(2)]

___  ___  ___	5.	Is appropriate critical lift documentation maintained for one year following the lift? [3.6]

___  ___  ___	6.	Other

Section 4,  Personnel Qualifications And Training Requirements

Yes  No   N/A

___  ___  ___	1.	Does the contractor have a documented training and qualification program for hoisting and rigging activities? [4.3]

___  ___  ___	2.	Does the qualification program include 1) classroom or computer based training, 2) written tests, 3) On-the-job training (OJT), and 4) On-the-job evaluations (OJE).  [4.3]

___  ___  ___	3.	Are personnel requalified on a frequency of 36 months or less?  [4.3.4]

___  ___  ___	4.	Do written, oral, and performance tests have established pass/fail criteria?  [4.6]

___  ___  ___	5. 	Are qualified personnel issued qualification cards with the appropriate information?  [4.7.2]

___  ___  ___	6.	Other.

Section 5, Hooks

Yes  No   N/A

___  ___  ___	1.	Are new and repaired hooks inspected to ensure compliance with applicable provisions of ASME B30.10, Hooks.  [5.4.1.1]

___  ___  ___	2.	Does the operator or other designated person visually inspect the hook daily, before use? [5.4.1.2]

___  ___  ___	3.	Are hooks periodically inspected by a qualified inspector on the proper frequency (depending on service classification)?  Are documented records available to verify periodic hook inspections?  [5.4.3]

___  ___  ___	4.	Do hook inspections look at 1) distortion, 2) wear, 3) cracks, nicks, or gouges, 4) latch engagement, and 5) hook attachment?  [5.4.4]

___  ___  ___	5.	Are hooks with excessive wear or deformation removed from service?  [5.4.5]

___  ___  ___	6.	Do existing crane/hoist hooks rated greater or equal to 10 tons and assigned to heavy or severe service receive an NDT by a qualified inspector at the following intervals:

a.  Heavy service --annually

b.  Severe service--semi-annually (every 6 months)

Note:	Hooks in normal service do not routinely require NDT.  [5.5.2]

___  ___  ___	7.	Other.

Hook Service Classifications service, normal--service that involves operating at less than 85% of rated load except for isolated instances service, heavy--service that involves operating at 85% to 100% of rated load as a regular specified procedure service, severe--heavy service coupled with abnormal operating conditions

Section 6, Forklift Trucks

Yes  No   N/A

___  ___  ___	1.	Does management classify and post hazardous locations before a forklift truck is assigned to work in the area?  [6.2.1.a]

___  ___  ___	2.	Does management ensure forklift operators are properly trained and qualified?  [6.2.1.d]

___  ___  ___	3.	Has management designated an area for battery charging of electric forklifts?  [6.2.1.e]

___  ___  ___	4.	Are personnel assigned and trained to change out LP-gas containers for LP-gas powered forklifts?  [6.2.1.f]

___  ___  ___	5.	For forklift trucks assigned to this facility, are frequent inspection (pre-use) inspection instructions readily available to the operator?  [6.2.2.2.b]

___  ___  ___	6.	Are forklift truck operators at this facility familiar with and do they accomplish frequent (pre-use) inspections? [6.2.3]

___  ___  ___	7.	Examine forklift trucks at this facility to determine if the manufacturer's plates, tags, labels, and decals are in legible condition.  [6.2.2.d and 6.3.1]

___  ___  ___	8.	Do forklift attachments (excluding fork extensions) have nameplates attached with the appropriate information?  [6.3.3]

___  ___  ___	9.	Are front-end attachments used with any forklift truck(s) at this facility?  If so, is the truck(s) marked to identify the attachment(s), the approximate weight of the truck and attachment combination, and the capacity of the truck with the attachment(s)?  [6.4.1]

___  ___  ___	10.	Is prior written approval obtained from the manufacturer prior to making modifications or additions that affect forklift capacity or safe operation?  Are capacity operation and maintenance instruction plates, tags, or decals changed accordingly?  [6.4.2]

___  ___  ___	11.	Do management and forklift operators understand what "free rigging" is?  Do they understand the process that is required to utilize "free rigging"?  [6.4.3]

___  ___  ___	12.	Do forklift operators understand the basis for forklift capacity and the need to "de-rate" a forklift for large or unusually configured loads?  [6.12.c and d]

___  ___  ___	13.	Other

Section 7, Shop Cranes

Yes  No   N/A

___  ___  ___	1.	Are operating instructions readily available for shop cranes?  [7.2]

___  ___  ___	2.	Does each shop crane have the rated capacity for each specified boom and leg position marked in a prominent location?  [7.5.1]

___  ___  ___	3.	Is the manufacturer's warning statement affixed to the shop crane?  [7.5.3]

___  ___  ___	4.	Is maintenance performed for each shop crane in accordance with the manufacturer's instructions?  [7.7]

___  ___  ___	5.	Other

Section 8, Wire Rope

Yes  No   N/A

___  ___  ___	1.	Identify cranes or hoists at this facility that use rotation-resistant wire rope.  Are special installation, inspection, and maintenance procedures readily available for rotation-resistant wire rope? [8.2.2]

___  ___  ___	2.	Confirm that independent wire rope core (IWRC) is used on all mobile cranes and any other hoist or crane that could operate at temperatures in excess of 180F.  [8.2.3]

___  ___  ___	3.	Review wire rope inspection procedures used at the facility.  Do the procedures provide clear instructions/acceptance criteria that are in accordance with DOE-RL-92-36?   [8.3 and 8.4]

___  ___  ___	4.	Are inspection records available for wire ropes on H&R equipment at this facility?  [8.3]

___  ___  ___	5.	If wire rope is stored at this facility, is it adequately protected?  [8.5.2]

___  ___  ___	6.	Other.

Section 9, Slings

Yes  No   N/A

___  ___  ___	1. 	Are alloy steel chain slings properly labeled?  [9.2.2.3]

___  ___  ___	2.	Does the chain sling inspection program at this facility meet the requirements of DOE-RL-92-36?  [9.2.2.6]

___  ___  ___	3.	Are periodic inspections on alloy steel chain slings documented?  [9.2.2.6.2]

___  ___  ___	4.	Have wire rope slings at this facility been proof tested?  [9.2.3.3]

___  ___  ___	5.	Are wire rope slings labeled with a tag or other identification method that provides: manufacturer's name, rated load, load test date, periodic inspection due date?  [9.2.3.4]

___  ___  ___	6.	Is there evidence that personnel who use wire rope slings understand and practice frequent (pre-use) inspection? [9.2.3.8.1]

___  ___  ___	7.	Review the periodic inspection program employed at this facility for wire rope slings.  Is it in accordance with DOE-RL-92-36?  [9.2.3.8.2]

___  ___  ___	8.	Are wire rope slings immediately removed from service if inspections identify adverse conditions?  [9.2.3.8.3]

___  ___  ___	9.	Determine by field inspection if synthetic web slings are labeled to state the following:

a. Manufacturer's name or trademark

b. Manufacturer's code or stock number

c. Rated loads for the types of hitches used

d. Type of synthetic web material

e.	An additional tag, sticker, or other identifier to indicate when the next periodic inspection is required.

f. Synthetic web slings used for critical lifts shall have a tag or other identifier to indicate that a proof test has been performed.

[9.2.5.1.4]

___  ___  ___	10.	Is there evidence that a "before use" inspection is done on synthetic web slings at this facility?  [9.2.5.6.2]

___  ___  ___	11.	Is there evidence of an acceptable periodic inspection program for synthetic web slings at this facility?  (The periodic inspection shall be made at least annually and shall be documented.)  [9.2.5.6.3]

___  ___  ___	12.	Other

Section 10, Rigging Hardware

Yes  No   N/A

___  ___  ___	1.	Do shackles and pins have appropriate manufacturing markings?  [10.2.2]

___  ___  ___	2.	Are shackles and rings properly inspected before each use?  [10.2.3]

___  ___  ___	3.	Are shackles used for critical-lift service proof load tested to two times the safe working load? [10.2.5]

___  ___  ___	4.	Are turnbuckles used for critical-lift service initially proof tested at two times the rated capacity?   Do tested turnbuckles have a tag or other marking to indicate that proof testing has been done?  [10.5.3]

___  ___  ___	5.	Other.

Section 11, Below-The-Hook Lifting Devices

Yes  No   N/A

___  ___  ___	1.	Inspect below-the-hook lifting devices to determine if they are properly tagged/marked. 11.4

___  ___  ___	2.	Are modifications to below-the-hook lifting devices properly analyzed and documented?  [11.5]

___  ___  ___	3.	Is there an established program, including records, for periodic inspection of below-the-hook lifting devices? [11.7.3   and 11.7.4]

___  ___  ___	4.	Have below-the-hook lifting devices at this facility been subjected to a rated load test?  Is documentation available to verify rated load tests?  [11.9.1.4 and/or 11.9.1.5]

___  ___  ___	5.	Are maintenance history files maintained for below-the-hook lifting devices? [11.10]

___  ___  ___	6.	Other.

Section 12, Hoists, Jib Cranes, And Monorail Systems

Yes  No   N/A

___  ___  ___	1.	Is the operation of hoists, jib cranes, and monorail systems at this facility limited to qualified personnel?  [12.2]

___  ___  ___	2.	Are hoists provided with the proper identification markings ?  [12.8.1]

___  ___  ___	3.	Are hoists provided with the proper identification warning labels, if equivalent training has not been conveyed to and understood by the users?   [12.8.2]

___  ___  ___	4.	Are hand signals used for controlling hoists at this facility?  If so, are hand signal charts posted conspicuously at the job site(s)?  [12.8.3]

___  ___  ___	5.	The absence of a hook throat latch is not indiscriminately allowed.  Review operating conditions for any hoist hooks at this facility which operate without a throat latch.  Should throat latches be installed?  [12.8.9]

___  ___  ___	6.	For pendant controls:

a.	Are the pushbutton stations supported so that the electrical conductors are protected from strain?

b.	Do pushbuttons spring return to the off position when pressure is released by the operator?

c.	To the extent possible, is each control clearly marked to indicate the direction of resultant motion?

[12.10.2]

___  ___  ___	7.	Are electrical supplies for permanently installed hoists and monorail systems shall be controlled by a lockable switch or circuit breaker located on a fixed structure, accessible from the floor.   [12.10.3]

___  ___  ___	8.	Is there evidence of a  Frequent/Periodic Inspection Program for hoists at this facility?  [12.12 and Tables 12-1, 12-2, 12-3]

___  ___  ___	9.	Are there hoists, jib cranes, or monorail systems at this facility that are considered standby equipment (idle for 1 month or more)?  If so, are they inspected (equal to Frequent Inspection) before being placed in service?  Does equipment used for standby service receive a Periodic Inspection and operational test no less than annually.  [12.12.6]

___  ___  ___	10.	For hoists, jib cranes and monorail systems at this facility, is there a Preventive Maintenance program? Is this program based on the manufacturer's, or a qualified person's, recommendations?   [12.16.1]

___  ___  ___	11.	Are load tests conducted in accordance with written step-by-step procedures?  [12.17.5]

___  ___  ___	12.	Other

Section 13, Overhead And Gantry Cranes

Yes  No   N/A

___  ___  ___	1.	Is the operation of overhead and gantry cranes at this facility limited to properly qualified personnel?  [13.2.1]

___  ___  ___	2.	Has the facility established an OJE program to verify the qualifications of all personnel (including outside organizations) that are allowed to use a facility crane?  [13.2.1]

___  ___  ___	3.	Inspect marking of overhead and gantry cranes at this facility:

a.	Is the rated load of the crane marked on each side of the crane?

b.	If the crane has more than one hoisting unit, does each hoist have its rated load marked on it or its load block?

c.	Load blocks should be painted to contrast with the bridge and trolley to facilitate quick visual identification.  Do blocks at this facility follow this recommendation?

d.	Are marking on the bridge, trolley, and load block legible from the ground floor?

[13.7.1]

___  ___  ___	4.	Are hand signals used for overhead or gantry cranes at this facility?  If so, are hand signal charts posted conspicuously at the job site(s)?  [13.7.2]

___  ___  ___	5.	Is a means of egress from cab-operated cranes provided to permit departure under emergency conditions? [13.7.3]

___  ___  ___	6.	For cab-operated cranes at this facility, is there a 10BC portable fire extinguisher, minimum, installed in the cab and maintained in a serviceable condition?  [13.7.5]

___  ___  ___	7.	Inspect pendant control stations on overhead and gantry cranes.

a.	Are the pushbutton stations supported so that the electrical conductors are protected from strain?

- To the extent possible, is each control clearly marked to indicate the direction of resultant motion?

c.	Do push buttons spring-return to the "off" position when pressure is released by the operator?

d.	Where possible, are crane controls marked to indicate the direction of resultant motion?

[13.7.11.3]

___  ___  ___	8.	Are appropriate pre-use and daily inspections performed?  [13.9.1.2.1 and 13.9.1.2.2]

___  ___  ___	9.	Are periodic inspections properly documented?  [13.9.1.4.1]

___  ___  ___	10.	Are Periodic Inspection procedures available for each overhead and gantry crane at this facility?  [13.9.1.4.4]

___  ___  ___	11.	For overhead and gantry cranes at this facility is there a Preventive Maintenance program based on the manufacturer's recommendations or  developed by a responsible maintenance organization?  [13.9.2.1]

___  ___  ___	12.	Are new, reinstalled, altered, repaired, or modified cranes load-tested prior to initial use, as determined by a qualified person.  [13.9.3.4]

___  ___  ___	13.	Other

Section 14, Mobile Cranes

Yes  No   N/A

___  ___  ___	1.	Is a system of flagging, barricades, or other safeguards used to isolate pinch point hazards relative to operating mobile cranes?   [14.4.1]

___  ___  ___	2.	Is a portable fire extinguisher in serviceable condition, with a minimum extinguisher rating of 10 BC, installed in the cab or at the machinery housing on each mobile crane?  [14.4.9]

___  ___  ___	3.	Is a durable, legible rating chart(s) from the manufacturer provided in the cab of each mobile crane?  (The crane's serial number should be printed or stamped on the chart by the manufacturer or designee.)   [14.5.1]

___  ___  ___	4.	Is an operating manual for each mobile crane readily available to the operator at all times?  [14.5.2]

___  ___  ___	5.	Does each crane have a boom-angle indicator?  Does each telescoping boom crane have a boom-length indicator? [14.6.5.2 and 14.6.5.3]

___  ___  ___	6.	Are booms, boom sections, and jibs clearly identified as to the crane(s) they are assigned?  [14.6.5.5]

___  ___  ___	7.	Are telescopic boom cranes, lattice boom cranes, or cranes used to lift suspended personnel platforms provided with appropriate anti-two-block devices or two-block warning features?  [14.6.6.1]

___  ___  ___	8.	Do your mobile cranes have a means provided for the operator to visually determine the levelness of the crane? [14.6.6.4]

___  ___  ___	9.	Are durable signs installed on all mobile cranes, at the operator's station, and on the outside of the crane warning that electrocution or serious bodily injury may occur unless adequate clearance is maintained between the crane, or the load line, and energized power lines?  [14.6.6.5.a]

___  ___  ___	10.	Are hand signal charts conspicuously posted at the job site (posting outside the crane cab meets this requirement)? [14.6.6.5.b/c]

___  ___  ___	11.	Is the frequent inspection procedure for each mobile crane available to the operator?  Does each frequent inspection procedure, or an attachment thereto, state how deficiencies found during frequent inspection shall be reported? [14.7.2.1]

___  ___  ___	12. 	Are critical items such as brakes, crane hooks, ropes, hydraulic and pneumatic cylinders, and hydraulic and pneumatic relief pressure valves, inspected  and documented monthly?  [14.7.3]

___  ___  ___	13.	Are operator aids including Anti-Two-Block, Two-Block Warning, and Two-Block Damage Prevention Systems checked and inspected as follows:

a. Before daily operation, by the operator or other designated person, to ensure that the system is functional in accordance with the system manufacturer's written instructions?  (This check is not required to be documented.)

b. Inspected and tested by a qualified person every 12 months, or more frequently, if specified by the manufacturer?  This inspection and testing shall be documented.

[14.7.4]

___  ___  ___	14.	Are records of periodic inspections available?  [14.7.5 to  14.7.9]

___  ___  ___	15.	For each mobile crane, is there a preventive maintenance program based on the crane manufacturer's recommendations?  Are dated PM records available for each crane?  [14.8.1.a]

___  ___  ___	16.	Other.

Section 15.0, Personnel Lifting

Yes  No   N/A

___  ___  ___	1.	Are personnel suspended from cranes in a personnel platform?  Is the crane being used for other purposes while handling personnel?  [15.3]

___  ___  ___	2.	Is personnel lifting performed under the direction of a Personnel Lift Supervisor?  [15.4.b]

___  ___  ___	3.	Are trial lifts performed each shift before hoisting personnel?  [15.4.g]

___  ___  ___	4.	Are personnel in the lift platform wearing appropriate fall protection equipment?  [15.4.o]

___  ___  ___	5.	Are wind and weather restrictions for personnel lifts identified?  [15.4.x]

___  ___  ___	6.	Other.

Section 18.0, Hoisting And Rigging In Hostile Environments

Yes  No   N/A

___  ___  ___	1.	In order to document alternative compliance methods and procedures in hostile environments, are Hostile Environment Plans established where normal usage criteria can not reasonably be met?  [18.2.1]

___  ___  ___	2.	If Hostile Environment Plans are used at this facility, are the plans approved by responsible management and an overview organization (such as Safety or Quality Assurance)?  [18.3.2]

___  ___  ___	3.	Do Hostile Environment Plans contain the appropriate information?  [18.3.3]

___  ___  ___	4.	Does equipment that requires a Hostile Environment Plan properly posted?  [18.4]

___  ___  ___	5.	Are polyester (rope or webbing) slings prohibited from use in radiation areas?  [18.5.2]

___  ___  ___	6.	Are nylon (rope or webbing) slings prohibited from use in radiation areas?  If necessary to use a nylon sling in a radiation area, is the responsible manager ensuring the radiation exposure does not exceed 100,000 rad during the life of the sling?  [18.5.3]

___  ___  ___	7.	Other.

OTHER:

NOTES/COMMENTS:

PERSONNEL CONTACTED:

FINDINGS:

Finding No.:

Description:

OBSERVATIONS:

Observation No.:

Description:

FOLLOW-UP ITEMS:

CONTRACTOR MANAGEMENT DEBRIEFED AND RESULTS:

Signature:  _______________________________		Date: _____/_____/_____

Facility Representative