SPILL PREVENTION, CONTROL, AND COUNTERMEASURES PLAN

NATIONAL WEATHER SERVICE

Weather Forecast Office and Radar Data Acquisition Site

Duluth, Minnesota

Original Date of Plan:		September 20, 2000

Date of Last Plan Review:		September 20, 2000

Date of Last Amendment
and P.E. Certification:		September 20, 2000

Designated Person Responsible for Spill Prevention:

Steve Wannebo, Environmental/Safety Focal Point

Telephone:  (218) 729-0651

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of Title 40 of the Code of Federal Regulations (40 CFR) Part 112, I attest that this Spill Prevention, Control, and Countermeasures (SPCC) plan has been prepared in accordance with good engineering practices.

Timothy E. Denhof

| Printed Name of Registered Engineer |
| --- |
| Signature of Registered Engineer and Date |
| Registration No. 062-047884PE | State IL |

REVIEW DOCUMENTATION AND MANAGEMENT APPROVAL PAGE

REVIEW DOCUMENTATION

In accordance with 40 CFR Part 112.5(b), a review and evaluation of this SPCC plan is conducted at least once every 3 years.  As a result of this review and evaluation, the National Weather Service will amend the SPCC plan within 6 months of the review to include more effective prevention and control technology if the following both apply:

Such technology will significantly reduce the likelihood of a spill event from the facility.

Such technology has been field-proven at the time of review.

Any amendment to the SPCC plan shall be certified by a Professional Engineer within 6 months after a change in the facility design, construction, operation, or maintenance occurs which materially affects the facility’s potential for the discharge of oil into or upon the navigable waters of the United States or adjoining shorelines.

| Review Date | Signature of Responsible Manager | Amended (Yes or No)? a |
| --- | --- | --- |

a	Amendment necessary and certified by a Registered Professional Engineer per 40 CFR Part 112.3(d)

MANAGEMENT APPROVAL

The National Weather Service is committed to the prevention of discharges of oil to navigable waters and the environment.  We maintain the highest standards for SPCC through regular review, updating, and implementation of this SPCC plan for the Weather Forecasting Center and Radar Data Acquisition Site located in Duluth, Minnesota.

Michael Stewart, Meteorologist-In-Charge

Printed Name and Title of Responsible Manager

Signature and Date

CONTENTS

Section	Page

Certification	i

Review Documentation and Management Approval	ii

PART I -	GENERAL INFORMATION	1

A.	GENERAL	1

1.	Name	1

2.	Type	1

3.	Date of Initial Operation	1

4.	Location	1

5.	Name and Address of Operator	1

6.	Facility Contacts:	1

B.	SITE DESCRIPTION AND OPERATIONS	1

1.	Facility Location, Layout, and Operations	1

2.	Facility Storage	2

3.	Drainage Pathway and Distance to Navigable Waters	2

4.	Spill History	2

5.	Spill Potential, Volumes, and Rates	3

PART II -	DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL	4

A.	SPILL PREVENTION	4

1.	Bulk Storage Tanks and Facility Transfer Operations	4

2.	Tank Truck Unloading Operations	4

3.	Inspections and Records	5

4.	Site Security	5

5.	Training	6

B.	SPILL CONTROL	6

1.	Secondary Containment Designs, Construction Material, and Volume	6

2.	Spill Kits Type and Location	6

PART III -	SPILL COUNTERMEASURES AND REPORTING	7

A.	SPILL COUNTERMEASURES	7

B.	SPILL REPORTING	7

1.	General Notification Procedures For All Spills	7

2.	Federal Notifications	8

3.	State Notification	8

4.	Cleanup Contractor Notification	9

PART IV -	RECOMMENDED IMPROVEMENTS	10

A.	PHYSICAL UPGRADES	10

1.	Tanks	10

2.	Spill Kits	10

3.	Containment, Tank Truck Unloading	10

CONTENTS (Continued)

Section	Page

B.	PROCEDURAL CHANGES	11

1.	Tank Truck Unloading Procedure	11

2.	Inspections and Preventative Maintenance	11

3.	Record keeping	11

4.	Training	11

Appendix

A	Tank Ullage/Fueling Log ANd FUeL UNLOADING PROCEDURE CHECKLIST

B	Inspection ChecklistS

C	Training Outline and Title 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.1-112.20-OIL POLLUTION PREVENTION

D	Spill RepoRtING form

E	CROSS REFERENCE OF THE REQUIREMENTS of TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.7, WITH THIS PLAN

FIGURES

Figure	Page

1	SITE LOCATION	12

2	SITE LAYOUT	13

TABLES

Table	Page

1	DESCRIPTIVE INVENTORY OF FACILITY STORAGE	14

2	POTENTIAL SPILL SOURCES AND VOLUMES	15

PART I - GENERAL INFORMATION

This part of the Spill Prevention, Control, and Countermeasures (SPCC) plan presents general information about the facility including a description of the site and its operations.

GENERAL

This section provides general information about the facility.

Name

National Weather Service (NWS), Weather Forecast Office (WFO) and Radar Data Acquisition (RDA) Site

Type

This facility is an onshore facility (non-production) that operates as a weather forecasting center and houses a RADAR dome for collecting atmospheric information. The facility is staffed 24 hours per day, 365 days per year.

Date of Initial Operation

April 1995

Location

5027 Miller Trunk Highway	Latitude:						46		º 50' 12"				 North

Duluth, St. Louis County, MN 55811-1203	Longitude: 								92º 13' 13" West

Name and Address of Operator

National Weather Service

Central Region Headquarters

601 East 12th Street, Room 1836

Kansas City, MO  64106-2897

Facility Contacts:

Name	Title	Telephone Number

Steve Wannebo	Environmental Safety Focal Point	(218) 729-6572

Michael Stewart	Meteorologist-In-Charge	(218) 729-0651

(24 hours a day)

SITE DESCRIPTION AND OPERATIONS

This section describes the site and its operations.

- Facility Location, Layout, and Operations

The facility is located in St Louis County, Minnesota, approximately 7 miles northwest of downtown Duluth, Minnesota (Figure 1).  Figure 2 shows the layout of the facility including the 1,000-gallon aboveground storage tank (AST) and 50-gallon day-tank at the WFO, and the two 250-gallon ASTs for the RDA site.  All the ASTs are used to store number 1 diesel fuel for generators that are used for emergency back-up power to the WFO and RDA site.  The 50-gallon day-tank and the two 250-gallon ASTs are stored inside prefabricated sheds for the respective generators for the WFO and RDA site.

The RDA site is located approximately 250 feet east of the WFO and is in a secured (fenced and locked) area approximately 65 feet by 85 feet square.  This site is comprised of the radar tower, the data acquisition center (DAC), the uninterruptible power supply (UPS), and the emergency back-up power generator.  The generator and the two 250-gallon ASTs are located in an enclosed generator shed.

Fuel usage for the weather station is estimated at 250 gallons per year based on fuel records.  Fuel usage for the RDA is estimated at 500 gallons per year based on fuel records.  Both the WFO and RDA generators are tested once a week.  Fuel consumption would increase based on the frequency and duration of any power outages.

Facility Storage

The WFO storage tank is a 1,000 gallon, LubeCube® AST, rectangular in shape.  The primary steel tank is encased in a secondary tank with a capacity of 110 percent of the primary storage tank.  The tank has a primary and secondary venting system as well as a primary and secondary emergency venting system.

The supply line from the WFO storage tank to the generator is painted-cast iron piping, which is encased in plastic containment piping.  The piping travels overhead to the generator building.  The fuel is transported into the 50-gallon day-tank that directly feeds the generator.

The two 250-gallon single-wall storage tanks at the RDA site are rectangular in shape and inside the generator building.  They are connected to each other in two places via a 2-inch rubber line.  Each tank has a vent pipe out the top that merges together into one pipe that is vented out the side of the generator building.  The generator building is 9 ½ feet wide and 15 ½ feet long and has a 9-inch-high lip on the door.  This building is designed to act as containment for the fuel storage tanks.  Excluding displacement from the equipment, there is approximately 825 gallons of capacity within the sealed concrete floor of the building for secondary containment.  The north tank is connected to the pump that brings fuel to the generator.  The north tank also has a fill line and has a low-level sensor connected to an alarm that is remotely monitored at the WFO.

Table 1 summarizes the pertinent information on the tanks at the facility.

Drainage Pathway and Distance to Navigable Waters

The area is not supplied with a storm water sewer system.  A storm drainage system specific to the property, located in the recessed grass basins, collects storm water runoff from the east side of the building.  The flow from the two basins is directed north to an outlet located approximately 20 feet down the hill on the north side of the facility property.  This outfall flows downhill to neighboring property owned by Duluth International Airport.  The runoff collects in a swamp located near the bottom of the hill or could potentially be transported far enough onto airport property to reach the drainage system for the airport.  Stormwater runoff from the airport is collected in a manmade drainage ditch, which travels approximately 1 mile southeast to an unnamed ditch.  This ditch travels another 1 mile before connecting to Miller Creek which discharges to St. Louis Bay in Duluth and then discharges to Lake Superior.

Spill History

Reportable Spill events from April 1995 to date on cover of this plan:

None

Spill Potential, Volumes, and Rates

The most probable causes for spills from the storage tanks are from overfilling, pump failures, or a ruptured hose during fueling.  For these tanks, spills caused by failure of the fuel supply line, loss of structural integrity, vehicle collisions, or earthquakes are low probability events.

Table 2 summarizes the potential type of failure, potential spill volume, estimated rate, and direction of spill flow from the tanks.

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES 
FOR SPILL PREVENTION AND CONTROL

This section discusses spill prevention and control measures that shall be implemented at the facility.

- SPILL PREVENTION

This section describes design components and operating procedures that shall be implemented at the facility to prevent oil spills.

- Bulk Storage Tanks and Facility Transfer Operations

WFO Storage Tank:  The tank construction shall be compatible with the no. 1 diesel fuel held by the tank.  The tank shall have secondary containment around the primary tank shell.  A float-type level gauge shall indicate the fuel level (from empty to full).

An automatic shut-off valve on the fill spout shall be set to close at 90 percent of the tanks capacity (900 gallons).  The tank also shall have an audible high-level alarm set at 85 percent of capacity (850 gallons) and interstitial monitoring device between the primary and secondary tanks that is connected to the audible alarm system.  A 7-gallon-capacity round spill container shall surround the fill spout.

WFO Generator Day Tank:  This tank shall be compatible with the no. 1 diesel fuel and have an open top spill containment pan with a capacity of not less than 50 gallons.

RDA Storage Tanks:  The tank construction shall be compatible with the no. 1 diesel fuel held by the tank.  The generator building shall be designed to be leak tight for spill containment.  The tank shall be equipped with an audible high level alarm integrated with the current low-level sensor.

Piping:  An antisiphoning valve shall be located between the main storage tanks and the pump to prevent unwanted fuel from being siphoned from the storage tanks.  WFO piping shall be double-walled from the tank to the generator building.

Tank Truck Unloading Operations

All delivery drivers shall have U.S. Department of Transportation hazardous material transportation training as required by Federal law.

The remainder of this section discusses the procedures that shall be used during unloading of fuel from the tank truck into the storage tank to prevent spills.  This procedure shall be documented every time refueling occurs using the form found in Appendix A.  Copies of this form shall be kept for 3 years.

The following procedure shall be used before fuel unloading:

Ensure that the audible high-level alarm system and the automatic shutoff valve function properly.

A NWS representative should determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (See Appendix A). This ullage is communicated to the fuel supply contractor and marked in the fueling log.

Move spill containment equipment such as booms or spill barriers into the unloading area.

Block the tank truck wheels.

Place drip pans under all pump hose fittings (if applicable) before unloading.

The NWS representative and the delivery driver ensure the fill nozzle is placed in the appropriate AST appurtenance.  In the case of the 1,000 gallon AST, the fill nozzle shall be connected to the cam-lock fitting on the 4-inch pipe within the round spill container.  In the case of the two 250-gallon ASTs, the fill nozzle shall be placed into the fill spout marked “fill line” that extends outside of the east wall and shall be equipped with an automatic shutoff valve.

Both the NWS representative and the delivery driver shall remain with the vehicle observing the unloading process at all times.  Gauges on the AST and the truck shall be continuously monitored to ensure the ullage is not exceeded.  If the audible high-level alarm sounds, the unloading of fuel shall be stopped as soon as possible.

The following procedure shall be used after fuel unloading is completed:

Record the amount of fuel transferred to the WFO and RDA ASTs in the log (Appendix A).

Drain the fill hose and then ensure that all drain valves are closed (if applicable) before removal of the hose from the tank

Pour any fuel in the drip pans, or spill container on the fill pipe into the AST (if it has the capacity) or dispose of appropriately.

Inspect the tank truck prior to removing the blocks to ensure the lines have been disconnected from the tank.

Remove the blocks from truck wheels.

Place a copy of the fuel-unloading checklist in the SPCC plan.

Inspections and Records

Inspection and Maintenance of Tanks:  The 1,000 gallon storage tank, WFO generator day tank, and the two 250-gallon storage tanks for the RDA shall be inspected weekly for any oil outside the tanks, especially at seams.  The outside of exposed piping shall also be inspected weekly, especially at the joints such as gasketed fittings.  Monthly and annual inspections shall follow the checklists shown in Appendix B.  These inspections can be performed in conjunction with the weekly generator testing.

Record Keeping:  The Environmental/Safety Focal Point  (person responsible for spill prevention at the facility) shall be responsible for completing the ullage logs and documentation of fuel unloading procedures.  In the absence of the above Focal Point, an appropriate substitute shall record the information.  These records, as well as records of all inspections, shall be maintained for at least 3 years from the time of inspection.

Site Security

The WFO storage tank shall have appropriate lighting to detect spills at night.  Due to the rural location of the site and the lack of readily accessible valves, fencing for security purposes is not warranted around this tank.  The fill cap shall be securely locked at all times except during refueling.  Appropriate signage indicating the tank contents, presence of combustibles and no smoking warnings must be maintained and clearly visible.  A fire extinguisher shall be located in the adjacent generator building.

The two 250 gallon ASTs for the RDA are located inside a locked building surrounded by a locked security fence.

Training

The Environmental/Safety Focal Point and an alternate shall be trained in the intent of applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in paragraph 3, above.  Spill control and countermeasures shall also be included in the training.  An outline for the training is found in Appendix C.

Training shall be repeated once per year.  All new personnel responsible for implementing this SPCC plan shall be properly trained before beginning the new position.  A record of who was trained, when, and by whom, shall be filed with this SPCC plan and kept for a period of 3 years.

- SPILL CONTROL

This section describes control measures that shall be implemented to prevent any spilled oil from entering navigable waters or adjoining shorelines.

- Secondary Containment Designs, Construction Material, and Volume

The secondary containment tank on the WFO storage tank and the sealed floor in the generator building beneath the two RDA storage tanks shall be sized to contain 110 percent of the tank volumes.  Both of these secondary containment features are enclosed to prevent precipitation from entering.  An interstitial monitoring system that can detect fuel of 1 inch or more in the secondary shell of the WFO storage tank shall be included.

Spill Kits Type and Location

The facility shall have spill kits designed to absorb diesel fuel and to divert a spill from navigable waters.  These items shall be stored in each generator building or nearby.  The kit shall include oil absorbent socks and mats in a polyethylene container that doubles as a disposal container.  In addition, urethane spill barriers that can divert or contain a relatively small spill and prevent it from reaching navigable waters should be included with the spill kit.

part iii - SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is on prevention.  The spill countermeasures presented do not constitute a contingency plan detailed in Title 40 of the Code of Federal Regulations (40 CFR) Part 109, nor is one required.  Such a plan is only required under 40 CFR 112.7(d) if it is impracticable to provide containment, diversionary structures, or equipment to prevent the discharge of oil to navigable waters.  In addition, this facility is not required to have a facility response plan under 40 CFR 112.20 since it does not:

Transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons, or

Have a total storage capacity over 1 million gallons.

Should a spill occur, the following measures would be implemented:

- SPILL COUNTERMEASURES

This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasure activities will be undertaken until conditions are safe for workers.  The following general procedures should be implemented as countermeasures:

Account for all personnel and ensure their safety.

Eliminate all ignition sources in the immediate area.

Attempt to divert flow away from the drainage ditch with a spill barrier or the contents of spill kit.

Attempt to seal or somehow stop leak, if it can be done safely.

Notify contacts and emergency response contractor as described in the next section for assistance in control and cleanup.

- SPILL REPORTING

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The people and organizations that are notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

A spill report form that requests the information to be reported to all agencies in written form (to the extent known) is included in Appendix D.  Copies of the completed form should be sent to the NWS Environmental Compliance Officer and the National Oceanic and Atmospheric Administration (NOAA) Central Regional Compliance Officer (see next section).

- General Notification Procedures For All Spills

The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

First, call 9-1-1 (or the local emergency agency) if there is an immediate emergency

Next, notify the appropriate persons within the NWS:

Mike Jacob, (301) 713-1838 Ext. 165, NWS Environmental Compliance Officer.

Olga Kebis, (301) 713-1838 Ext. 173, NWS Safety Officer

Steve Becka, (816) 426-3226 Ext. 473, NWS Central Regional Environmental/Safety Coordinator

Sherilyn Villegas, (816) 426-3925 Ext. 263, NOAA Central Regional Compliance Officer

Federal Notifications

The Federal Clean Water Act as described in Title 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency’s (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  Title 40 CFR Part 110.3 defines “may be harmful” as a discharge that:

Violates applicable water quality standards; or

Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or cause a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines

If either of these criteria are met contact:

The National Response Center (EPA and USCG):  (800) 424-8802.

Under the SPCC regulations, spill information listed in Title 40 CFR Part 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shore lines in a single event

Two spill events that cause visible sheens upon navigable waters or adjoining shore lines within any 12-month period

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA).  Therefore no other notification to the EPA is required for discharges of diesel fuel other than those listed above.

State Notification

Under Minnesota Pollution Control Agency regulations for aboveground storage tanks, Minnesota Rules Chapter 7151, above ground storage tanks that have a capacity of less than 1,100 gallons and are more than 500 feet from class 2 waterways are exempt from this rule.  However, Minnesota Statute 115.061, Duty to Notify and Report Water Pollution does require reporting of all spills, if not recovered, that may cause pollution of the waters of the state.  MPCA interprets this to apply to a 5-gallon release or larger and including releases to outdoor secondary containment areas.  Any release greater than 5 gallons must be reported to the MPCA, Department of Public Health and Safety, Minnesota Duty Officer.

MPCA, Department of Public Health & Safety:  (800) 422-0798 or (651) 649-5451.

Cleanup Contractor Notification

An emergency response contractor should also be notified to assist with the clean up, if necessary.  NWS has identified the following two contractors that are available for an emergency response:

EMR Inc.			(888) 723-8140

Service Response Remediation, Inc.	(800) 401-0121

PART IV - RECOMMENDED IMPROVEMENTS

In accordance with Title 40 CFR Section 112.7, this section presents physical upgrades or procedural changes that are not yet fully operational but are called for in the plan.

- PHYSICAL UPGRADES

- Tanks

An automatic overfill shutoff valve should be installed in the fill spout of the RDA tank.  This valve should be set to stop the flow of fuel into the tank when it reaches 90 percent of capacity.  The fuel supply contractor should be contacted to ensure the valve is compatible with the nozzle used to fill the tank.  A high-level audible alarm should be installed with the existing computer monitored level sensor on the storage tank to sound at 85 percent capacity.

The WFO storage tank should be equipped with a high-level sensor and audible alarm. The sensor should be set to sound the alarm at 85 percent capacity.

Spill Kits

NWS should purchase adequately sized spill kits and store them near the tanks.  NWS should purchase a kit capable of handling up to 60-gallons.  The kit should include oil absorbent socks and mats in a polyethylene container that doubles as a disposal container.  In addition, the facility should have urethane spill barriers available.  These barriers can direct or contain a relatively small spill and prevent it from reaching navigable waters.  This requirement is found in Title 40 CFR Section 112.7(c).

Containment For Tank Truck Unloading Areas

NWS should install containment for tank truck unloading areas for both the WFO and RDA storage tanks.  Containment is required due to the steep grade in the immediate area for fuel transfer.  Any spill occurring during fuel transfer would quickly travel down grade before spill containment devices could be mobilized.

The WFO 1,000 gallon AST unloading area is east of the generator building.  This area is a flat paved section that is away from all traffic and parking areas.  A containment dike should be built around this area on the north, west, and east sides.  The containment dike should be sufficient in height and area to contain 110 percent of the largest compartment of the fuel delivery vehicle.  The vehicle entrance to the transfer containment area should be elevated to the same height of the surrounding dike and have a sloped drive appropriate for delivery vehicle entry and exit.  Structural integrity of the entrance must be sufficient for the gross weight of a filled delivery vehicle.  The asphalt containment area should be coated with an appropriate chemical resistant liner suitable for diesel fuel Nos. 1 and 2.  The diked area will require a manually operated drain valve for precipitation drainage.  The valve is normally closed and locked with a combination or paddle lock.

The RDA unloading area is presently located on a gravel access road.  This area should be paved with asphalt or a concrete containment area could constructed.  An area sufficient in size to contain 110 percent of the largest volume tanker (2,000 gallons based on information supplied by Curtis Oil) should be constructed as an unloading area for fuel delivery.  The area should be diked and drained in a similar manner to the WFO location.  If the oil supplier has sufficient hose to reach both tank locations, a single unloading station could be used.

As an alternate, NWS could require its supplier to provide containment on its tank truck during unloading operations.  NWS would still be responsible for ensuring these containment devices are operated properly during unloading.

- PROCEDURAL CHANGES

- Tank Truck Unloading Procedure

The supplier performs the current tank truck unloading.  Future deliveries will require NWS personnel to be present during the unloading procedure and record the appropriate information on the checklist provided in Appendix A.

Inspections and Preventative Maintenance

The inspection checklists found in Appendix B should be followed.  This requirement is found in Title 40 CFR Section 112.7(e)(8).  The interstitial monitoring device in the storage tank is designed to monitor the integrity of the primary tank.  Visual inspections of the outside of the secondary wall of the storage tank and the primary wall of the day tanks should serve to signal a potential problem with their integrity.  However, if a problem is suspected with any tank, tightness testing should be initiated soon after discovery.

Record keeping

Ullage logs and documentation of fuel unloading procedures should be completed and maintained for 3 years from the time of inspection.

Training

The Environmental/Safety Focal Point (person responsible for spill prevention at the facility) and an alternate should be trained in the intent of the applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in the previous section.  Spill control and countermeasures should also be included in the training.  The alternate should be designated in case the primary person is off-site at the time of a spill.  A recommended outline for the training is found in Appendix C.

Training should be repeated once per year.  All new personnel responsible for implementing the SPCC plan should be properly trained before beginning the new position.  A record of who was trained, when, and by whom, should be filed with this SPCC plan and kept for a period of 3 years.  This requirement is found in Title 40 CFR 112.7(e)(10).

Figure 1 Site Location

Figure 2 Site Layout

TABLE 1

DESCRIPTIVE INVENTORY OF FACILITY STORAGE

| Tank | Nominal Capacity (Gallons) | Product Stored | Type | Double Walled? |
| --- | --- | --- | --- | --- |
| WFO Storage Tank | 1,000 | Diesel fuel no. 1 | AST | Yes |
| WFO Generator Day Tank | 50 | Diesel fuel no. 1 | AST | Yesa |
| RDA Generator Day Tanks | 2 x 250 | Diesel fuel no. 1 | AST | Nob |
| Total Capacity | 1,550 |  |  |  |

Notes:	AST	Aboveground storage tank

WFO	Weather Forecast Office

a	Surrounded by a 190-gallon rupture basin

b	Located in generator building with sealed concrete floor that has a capacity of greater than 500 gallons

TABLE 2

September 20, 2000

Duluth, Minnesota

POTENTIAL SPILL SOURCES AND VOLUMES

15

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| WFO Storage tank | Overfilling or a ruptured hose during fueling. | >0 to 40a | 80b | North | None |
|  | Failure of fuel supply line to pump | >0 to 1,000 | Variable depending on type of failure | North | Can be minimized through routine inspections. |
|  | Structural failure | >0 to 1,000 | Variable depending on type of failure | North | Low probability event that both primary and secondary tank shells would fail. |
|  | Vehicle collision | >0 to 1,000 | Variable depending on type of failure | North | Low probability event. Tank is located behind generator building with no access to vehicles. |
| WFO Generator Day Tank | Failure of pump to shut down or failure of line from pump to day tank | >0 to 1,000 | Variable depending on type of failure | North | Low probability event due to piping double-walled piping located overhead and out of any potential pedestrian traffic. |
|  | Failure of fuel return line | >0 to 1,000 | 10c | North | Low probability event due to piping double-walled piping located overhead and out of any potential pedestrian traffic. |
|  | Structural failure | >0 to 50 | Variable depending on type of failure | East | Low probability event. Would be contained by 190-gallon rupture basin. |
| RDA Storage tanks | Overfilling or a ruptured hose during fueling d | >0 to 40a | 80b | North/East | None |
|  | Failure of fuel supply line to pump d | >0 to 500 | Variable depending on type of failure | North/East | Can be minimized through routine inspections; All lines are within secondary containment. |
|  | Failure of fuel return lined | >0 to 500 | 10c | North/East | Can be minimized through routine inspections; All lines are within secondary containment. |
|  | Structural failure | >0 to 500 | Variable depending on type of failure | North/East | Low probability event. Would be contained by secondary containment. |

Notes:

a			Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump

Duluth, Minnesota

b			Approximate maximum pumping rate of fill truck

c	Estimated return line flow rate

d	North tank only

APPENDIX A

Tank Ullage/Fueling Log ANd

Fuel UNLOADING PROCEDURE CHECKLIST

(2 Pages)

APPENDIX A-1

Tank Ullage anD Fueling Log

A-1

Duluth, Minnesota

Tank Capacity 	 gallons

September 20, 2000

| Date | Initials | Gauge Reading | Initial Volume of Fuel in Tank a (Gallons) | Available Capacity or Ullage b (Gallons) | Quantity Added (Gallons) | Comments |
| --- | --- | --- | --- | --- | --- | --- |

Note:

a	From gauge reading

b	Available capacity (ullage) = tank capacity – initial volume of fuel in tank

APPENDIX A-2

FUEL UNLOADING PrOCEDURE CHECKLIST

Duluth, Minnesota

A-2

Date:										Tank:

NWS Representative:								Supplier

September 20, 2000

| ( | ITEM | DESCRIPTION | COMMENT |
| --- | --- | --- | --- |
| The following six items must be completed before fuel unloading: |
|  | 1 | Ensure the audible high-level alarm system and automatic shutoff valve are functioning properly. |  |
|  | 2 | Determine the available capacity (ullage) of the aboveground storage tank (AST) by converting the reading on the fuel gauge to gallons (See Appendix A, Page A-1). This ullage should then be marked in the fueling log and communicated to the tank truck unloading contractor. |  |
|  | 3 | Move spill containment equipment such as booms or spill barriers into the unloading area. |  |
|  | 4 | Block the wheels of the tank truck. |  |
|  | 5 | Place drip pans under all pump hose fittings (if applicable) after the hose is hooked up to the AST and before unloading. |  |
|  | 6 | Ensure the fill nozzle is placed in the appropriate AST appurtenance. In this case, the fill nozzle is placed in the fill pipe connected to the round spill container. |  |
| During unloading: |
|  | 7 | Ensure that the NWS representative and the tank truck operator remain with the vehicle at all times during unloading. |  |
|  | 8 | Monitor the gauges on the AST and the truck continuously to ensure the ullage is not exceeded. If the audible high-level alarm sounds, stop the unloading of fuel as soon as possible. |  |
| The following six items must be completed after the fuel unloading has been completed: |
|  | 9 | Record the amount of fuel unloaded in the log (Appendix A, page A-1). |  |
|  | 10 | Before removing the fill hose from the AST, ensure that it is drained and that all drain valves are closed (if applicable). |  |
|  | 11 | Pour any fuel in the drip pans, tank truck containment pool, or spill container on the fill pipe into the AST (if it has the capacity) or dispose of appropriately (describe how it was disposed of, if applicable). |  |
|  | 12 | Inspect the tank truck before removing the blocks to ensure the lines have been disconnected from the AST. |  |
|  | 13 | Remove the blocks from tank truck wheels. |  |
|  | 14 | Place a copy of this fuel-unloading checklist in the SPCC plan. |  |

APPENDIX B

INSPECTION CHECKLISTS

(3 Pages)

APPENDIX B

INSPECTIONS FORMS

B-1

September 20, 2000

Duluth, Minnesota

| MONTHLY INSPECTION CHECKLIST (Page 1 of 2) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| A. TANKS | YES | NO | NOTES |
| 1. Are there any oil stains on the outside of the tank, including the underside? |  |  |  |
| 2. Is there any oil on the ground, concrete, or asphalt around the tank? |  |  |  |
| 3. Are there any visible cracks or indications of corrosion on the tank, at fittings, joints, or seals? (such as paint peeling or rust spots) |  |  |  |
| 4. Are there any raised spots, dents, or cracks on the tank? |  |  |  |
| 5. Does it appear that the foundation has shifted or settled? |  |  |  |
| 6. Is the fuel gauge working properly? |  |  |  |
| 7. Are all vents clear so they may properly operate? |  |  |  |
| 8. If rainwater is present in secondary containment area, does sufficient volume remain for spill control? (if applicable) |  |  |  |
| MONTHLY INSPECTION CHECKLIST (Page 2 of 2) |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| B. PIPING | YES | NO | NOTES |
| 1. Is there any oil on the outside of or under any aboveground piping, hoses, fittings, or valves? |  |  |  |
| 2. Are aboveground piping, hoses, fittings, or valves in good working condition? |  |  |  |
| C. SECURITY/SAFETY/SPILL COUNTERMEASURES |  |  |  |
| 1. Are lights working properly to detect a spill at night? |  |  |  |
| 2. Are all locks in the “lock” position? |  |  |  |
| 3. Are all warning signs properly posted and readable? |  |  |  |
| 4. Are vehicle guard posts in place and properly secured? (If applicable) |  |  |  |
| 5. Are spill kits easily accessible, protected from the weather, and complete? |  |  |  |
| Corrective Actions Required: |

B-2

September 20, 2000

Duluth, Minnesota

| ANNUAL INSPECTION CHECKLIST (Page 1 of 1) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
|  | YES | NO | NOTES |
| A. MONTHLY CHECKLIST |  |  |  |
| 1. Has monthly inspection checklist been completed? |  |  |  |
| B. TANKS |  |  |  |
| 1. Are all alarms and automatic shutoff devices working properly? |  |  |  |
| 2. Is interstitial monitor functioning properly? (if applicable) |  |  |  |
| C. OTHER |  |  |  |
| 1. |  |  |  |
| Corrective Actions Required: |  |  |  |

B-3

September 20, 2000

Duluth, Minnesota

APPENDIX C

TRAINING OUTLINE AND COPY OF TITLE 40 OF

THE CODE OF FEDERAL REGULATIONS

Section 112.1-112.20-Oil Pollution Prevention

(1 Page)

APPENDIX C

OUTLINE FOR SPILL PREVENTION, CONTROL, AND COUNTERMEASURE TRAINING

Training will be provided for facility personnel at the following times:

- System startup or whenever new equipment is installed

- Within the first week of employment for new personnel

- Annually

The training will include complete instruction in the elements of the facility’s Spill Prevention, Control, and Countermeasure plan and will include the following:

- Pollution control laws, rules, and regulations including a summary of Title 40 of the Code of Federal Regulations Part 112 "Oil Pollution Prevention" (see Attachment).

B.	Fuel Storage System

1.	Purpose and application of the following system elements:

    - Tanks

    - Piping

    - Pumps

- Accessory equipment

- Electronic monitors

- Operation, maintenance, and inspection of system elements

C.	Spill Prevention

- Potential spill sources

- Spill flow direction and impact on navigable waters

- Procedures to prevent spills, especially during fuel unloading

  - Spill Control

- Secondary containment

- Safety valves

- Pump and equipment shutoff switches

- Use of catch basin inlet covers or other diversionary devices

- Spill Countermeasures

- Location and use of emergency phone numbers

- Location and use of fire extinguishers

- Location and use of spill cleanup kit

- Stopping the leak

APPENDIX D

SPILL REPORTING FORM

(1 Page)

APPENDIX D

SPILL REPORTING FORM

| 1. GENERAL |
| --- |
| Name of Facility: National Weather Service Facility | Address: 5027 Miller Trunk Highway Duluth, Minnesota 55811-1203 |
| Completed By: | Organization: National Weather Service |
| Position: | Phone: (218) 729-0651 |
| 2. SPILL INFORMATION |
| Date: | Time: |
| Location at Facility: | Quantity: |
| Substance Spilled: Diesel Fuel | Other: |
| 3. OUTSIDE NOTIFICATIONS: |
| Agencies | Recorder at Outside Agency | Date and Time |
| Call 9-1-1 (or the local emergency agency), if there is an immediate emergency |  |  |
| NWS/NOAA: Mike Jacob, (301) 713-1838 Ext. 165 Olga Kebis, (301) 713-1838 Ext. 173 Steve Becka, (816) 426-3226 Ext. 473 Sherilyn Villegas, (816) 426-3925 Ext. 263 |  |  |
| EPA National Response Center or U.S. Coast Guard: (800) 424-8802 |  |  |
| Minnesota Pollution Control Agency, Dept. of Public Health & Safety (800) 422-0798 or (651) 649-5451 |  |  |
| 5. INFORMATION ON SOURCE AND CAUSE |
| 6. DESCRIPTION OF ENVIRONMENTAL DAMAGE |
| 7. CLEANUP ACTION(S) TAKEN |
| 8. CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |

Note: 	All information must be filled in.  If something is unknown, write “unknown.”

Copies must be sent to the NWS/NOAA personnel listed previously.

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS of TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.7, WITH THIS DOCUMENT

(1 Page)

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF 40 CFR 112.7 AND THIS PLAN

| CFR Citation | Item | Plan Location |
| --- | --- | --- |
| 112.7 (a) | Spill History | Part I.B.4 |
| 112.7 (b) | Potential Spill Prediction, Volumes, and Rates | Part I.B.5 and Table 2 |
| 112.7 (c) | Containment and Diversionary Structures | Part I.B.2 and Part II.B.2 |
| 112.7 (d) | Secondary Containment Impractability | Not Applicable |
| 112.7 (e)(1) | Drainage Control | Part I.B.3 |
| 112.7 (e)(2) | Bulk Storage Tanks and Secondary Containment. |  |
| 112.7 (e)(2)(i) | Tank compatibility with its contents | Part II.A.1 |
| 112.7 (e)(2)(ii) | Diked area construction and containment for storage tanks | Not Applicable |
| 112.7 (e)(2)(iii) | Diked area inspection and drainage of rainwater | Not Applicable |
| 112.7 (e)(2)(iv) | Corrosion protection of buried metallic storage tanks | Not Applicable |
| 112.7 (e)(2)(v) | Corrosion protection of partially buried metallic tanks | Not Applicable |
| 112.7 (e)(2)(vi) | Aboveground tank periodic integrity testing | Part II.A.3 |
| 112.7 (e)(2)(vii) | Control of leakage through internal heating coils | Not Applicable |
| 112.7 (e)(2)(viii) | Tank installation fail-safe engineered | Part II.A.1, B.1 |
| 112.7 (e)(2)(ix) | Observation of disposal facilities for effluent discharge | Not Applicable |
| 112.7 (e)(2)(x) | Visible oil leak corrections from tank seams and gaskets | Part II.A.3 and Appendix A Inspections |
| 112.7 (e)(2)(xi) | Appropriate position of mobile or portable tanks | Not Applicable |
| 112.7 (e)(3) | Facility Transfer Operations |  |
| 112.7 (e)(3)(i) | Buried piping installation protection and examination | Part II.A.1 & Appendix A |
| 112.7 (e)(3)(ii) | Not in-service and standby terminal connections | Not Applicable |
| 112.7 (e)(3)(iii) | Pipe support designs | Not Applicable |
| 112.7 (e)(3)(iv) | Aboveground valve and pipeline examination | Not Applicable |
| 112.7 (e)(3)(v) | Aboveground piping protection from vehicular traffic | Not Applicable |
| 112.7 (e)(4) | Facility Truck Unloading Operations | Part II.A.2 |
| 112.7 (e)(5)-(7) | Oil Production Facilities (onshore) and Oil Drilling, Production, or Workover Facilities (on shore and offshore) | Not Applicable |
| 112.7 (e)(8) | Inspections And Record Keeping | Part II.A.3 |
| 112.7 (e)(9) | Security |  |
| 112.7 (e)(9)(i) | Fencing | Part II.A.4 |
| 112.7 (e)(9)(ii) | Flow valves locked | Not Applicable |
| 112.7 (e)(9)(iii) | Starter controls locked | Not Applicable |
| 112.7 (e)(9)(iv) | Pipeline loading and unloading connections securely capped | Not Applicable |
| 112.7 (e)(9)(v) | Lighting adequate to detect spills | Part II.A.4 |
| 112.7 (e)(10) | Training |  |
| 112.7 (e)(10)(i) | Personnel instructions | Part II.A.5 |
| 112.7 (e)(10)(ii) | Designated person responsible for spill prevention | Page i |
| 112.7 (e)(10)(iii) | Spill prevention briefings | Part II.A.5 |

Note:	CFR	Code of Federal Regulations