SPILL PREVENTION, CONTROL, AND COUNTERMEASURES PLAN

NATIONAL WEATHER SERVICE

Dodge City Weather Forecast Office

104 Airport Road

Dodge City, KS 67801

Original Date of Plan	:	August 1992

Date of Last Plan Review	:	April 2, 2002

Date of Last Amendment

and P.E. Certification	:	April 2, 2002

Designated Person Responsible for Spill Prevention:

Larry Noller, Environmental Focal Point

Telephone: (620) 225-6514

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of Title 40 of the Code of Federal Regulations Part 112, I attest that this Spill Prevention, Control, and Countermeasures (SPCC) Plan has been prepared in accordance with good engineering practices.

| John McCall |
| --- |
| Printed Name of Registered Engineer |
| Signature of Registered Engineer and Date |
| Registration No. PE-050653-E | State PA |

REVIEW DOCUMENTATION AND MANAGEMENT APPROVAL PAGE

REVIEW DOCUMENTATION

In accordance with Title 40 Code of Federal Regulations (CFR) Part 112.5(b), a review and evaluation of this Spill Prevention, Control, and Countermeasures (SPCC) Plan shall be conducted at least once every 3 years and shall be conducted by the Meteorologist in Charge, NWS Regional Environmental/ Safety Coordinator, or NOAA Regional Environmental Compliance Officer.  After the review and evaluation, the National Weather Service shall amend the SPCC Plan within 6 months to include more effective prevention and control technology if:

C	Such technology will significantly reduce the likelihood of a spill event from the facility, and

C	If such technology has been field-proven at the time of review.

Amendments to the SPCC Plan shall be made when a change in the facility design, construction, operation, or maintenance materially affects the potential for the discharge of oil into or upon the navigable waters of the United States or adjoining shorelines.  These amendments shall be fully implemented as soon as possible, but no later than six months after such a change occurs, and shall be certified by a Professional Engineer.  Other amendments due to facility changes that do not affect the potential for discharge (such as changes in personnel or contact information) can be made at any time, and certification by a Professional Engineer shall not be required.

| Review Date1 | Signature of Responsible Manager | Amended (Yes or No)? | PE Certification Required (Yes/No)? |
| --- | --- | --- | --- |

MANAGEMENT APPROVAL

The National Weather Service is committed to the prevention of discharges of oil to navigable waters and the environment.  We maintain the highest standards for spill prevention, control, and countermeasures through regular review, updating, and implementation of this SPCC Plan for the Weather Forecast Office.

LarryRuthie, Meteorologist in Charge

Printed Name and Title of Responsible Manager

Signature and Date

CONTENTS

Section	Page

Certification	i

Review Documentation and Management Approval	ii

PART I - GENERAL INFORMATION	1

A.	GENERAL	1

1.	Name	1

2.	Type	1

3.	Date of Initial Operation	1

4.	Location	1

5.	Name and Address of Operator	1

6.	Facility Contacts	1

B.	SITE DESCRIPTION AND OPERATIONS	1

1.	Facility Location, Layout, and Operations	1

2.	Facility Storage	2

3.	Drainage Pathway and Distance to Navigable Waters	2

4.	Spill History	3

5.	Spill Potential, Volumes, and Rates	3

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL	4

A.	SPILL PREVENTION	4

1.	Bulk Storage Tanks and Facility Transfer Operations	4

2.	Tank Truck Unloading Operations	4

3.	Inspections And Records	5

4.	Site Security	6

5.	Training	6

B.	SPILL CONTROL	6

1.	Secondary Containment Designs, Construction Material, and Volume	6

2.	Spill Kits Type and Location	7

PART III - SPILL COUNTERMEASURES AND REPORTING	8

A.	SPILL COUNTERMEASURES	8

B.	SPILL REPORTING	9

1.	General Notification Procedures for All Spills	9

2.          Federal Notification	9

3.          State Notification	10

4.          Cleanup Contractor Notification	10

PART IV - RECOMMENDED IMPROVEMENTS	11

A.	PHYSICAL UPGRADES	11

1.	Secondary Containment	11

B.	PROCEDURAL CHANGES	11

1.	Inspections and Preventative Maintenance	11

2.	Training	11

Appendix

A	TANK RECORDS

B	TANK ULLAGE/FUELING LOG AND FUEL UNLOADING PROCEDURE CHECKLIST

C	INSPECTION CHECKLISTS

D	TRAINING OUTLINE AND TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, PARTS 112.1-112.20-OIL POLLUTION PREVENTION

E	SPILL REPORTING FORM

F	CROSS REFERENCE OF THE REQUIREMENTS OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, PART 112.7, WITH THIS PLAN

FIGURES

Figure	Page

1	SITE LOCATION	12

2	SITE LAYOUT	13

TABLES

Table	Page

1	DESCRIPTIVE INVENTORY OF FACILITY STORAGE	14

2	POTENTIAL SPILL SOURCES AND VOLUMES	15

PART I - GENERAL INFORMATION

- GENERAL

This section provides general information about the facility.

  - Name

National Weather Service (NWS)

Dodge City Weather Forecast Office (WFO)

  - Type

This facility is an onshore facility (non-production) that operates as a river and weather forecasting center and is staffed 24 hours per day, 7 days per week, and 365 days per year.

  - Date of Initial Operation

October 1989

  - Location

104 Airport Road

Dodge City, Ford County, Kansas  67801

  - Name and Address of Operator

National Weather Service

104 Airport Road

Dodge City, Kansas  67801

  - Facility Contacts

Name	Title				Telephone Number

Larry Noller	Environmental Focal Point		(620) 225-6514

Larry Ruthie	Meteorologist in Charge		(620) 225-6514

- SITE DESCRIPTION AND OPERATIONS

This section describes the site location, its operations that store diesel fuel, site drainage patterns, spill history, and spill potential.

  - Facility Location, Layout, and Operations

The facility is located in Ford County, Kansas, approximately 2.5 miles east of Dodge City and adjacent to the Dodge City Regional Airport (Figure 1).  Figure 2 shows the layout of the facility, including the location of the 750-gallon aboveground storage tank (AST), 25-gallon day tank, and two 200-gallon Radar Data Acquisition (RDA) tanks.

The 750-gallon AST and 25-gallon day tank are used to store fuel that is used to power the WFO emergency generator.  The WFO generator and the day tank are located in the WFO generator room in the northeast corner of the WFO building and are not exposed to precipitation.  The 750-gallon AST is located outside the WFO generator building to the east.

The two 200-gallon RDA tanks are used to fuel the RDA emergency generator that supplies power to the RDA systems.  The two RDA tanks and RDA generator are located inside the RDA generator building approximately 50 feet northeast of the WFO and are not exposed to precipitation.

The estimated fuel usage is approximately 80 gallons per month.  This estimate is based on a test of the generators once per week for at least 30 minutes.  Fuel consumption would increase based on the frequency and duration of any power outages.

  - Facility Storage

The 750-gallon AST is a welded steel tank situated within a sufficiently impervious concrete containment basin and designed to hold the entire contents of the tank plus sufficient capacity to account for potential precipitation.  The 750-gallon AST is equipped with a 2-inch-diameter primary vent.

The 750-gallon AST is connected to a pump on top of the day tank via a pipe that travels through the outer wall of the WFO building and into the WFO generator room.  This pump moves fuel from the 750-gallon AST into the day tank.  The day tank is a 25-gallon single-walled rectangular steel tank and is situated over a rupture basin.  The day tank is connected to the generator by flexible rubber supply and return lines.

The two 200-gallon RDA tanks are constructed of steel and located within the RDA generator building that is designed and constructed to contain potential spills.  The RDA tanks supply fuel to the RDA generator, that is also located within the RDA generator building.

Table 1 summarizes the pertinent information on the tanks at the facility.  A copy of all tank registrations and other tank records, such as notifications to the Local Emergency Planning Committee or tank testing documentation, is included in Appendix A.

  - Drainage Pathway and Distance to Navigable Waters

Any fuel spilled from outside the secondary containment area of the 750-gallon AST would flow northwest along a slope approximately 300 feet and into a grassy pasture area.  A potential spill from a fuel unloading truck could flow to the parking lot and into the surrounding grassy areas.  Any fuel spilled outside the secondary containment of the two 200-gallon RDA tanks likely would flow northwest.  All stormwater runoff from the site eventually flows to an unnamed intermittent stream located west of the site.  The intermittent stream flows south.

  - Spill History

Reportable spill events from October 1989 to present (date on cover of this plan):

None.

  - Spill Potential, Volumes, and Rates

The most probable causes of spills from the 750-gallon AST and RDA tanks are overfilling, a ruptured hose during fuel unloading, or from failure of the fuel supply lines.  For the day tank, the probable causes of spills are from a failure of the pump to shut down or failure of the pipe that directs fuel from the pump to the day tank.  Low probability spill events for any of the tanks could include loss of structural integrity because of vandalism or a natural disaster.  It is possible that a vehicle collision could cause a spill from the 750-gallon AST, but the probability of such an event is low because the 750-gallon AST is not located in the direct line of traffic.

Table 2 summarizes the potential type of failure, potential spill volume, estimated rate, and direction of spill flow from the tanks.

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES 
FOR SPILL PREVENTION AND CONTROL

This section discusses spill prevention and control measures that shall be implemented at the facility.

- SPILL PREVENTION

This section describes design components and operating procedures that shall be implemented at the facility to prevent oil spills.

  - Bulk Storage Tanks and Facility Transfer Operations

750-gallon AST:  The tank construction is compatible with the diesel fuel stored in the tank.  Secondary containment is provided for the AST that will provide for the entire capacity of the tank plus sufficient freeboard to allow for the accumulation of precipitation.  A float-type level gauge indicates the fuel level (from empty to full).  A round spill container with 5-gallon capacity surrounds the fill spout to capture potential overflow during fuel transfer.  The AST is equipped with an audible high-level alarm set to engage at 85 percent of capacity (638 gallons) and an automatic shutoff valve on the cam-lock fitting fill spouts that is set to close at 90 percent of the AST capacity (675 gallons).  A monitoring system that can detect 1 inch or more of fluid in the interstitial space of the storage tank is also present.

Day Tank:  The day tank is located inside the WFO generator room and provides containment for the contents of the tank.  The day tank is equipped with a gauge to indicate the amount of fuel in the tank (empty to full)and a high-level float switch connected to an audible alarm to warn of overfilling.  The day tank is situated over an open top spill pan (rupture basin) that can hold 100 percent of the tank volume.  The rupture basin has a float switch designed to detect fuel that has spilled or leaked; the float switch is designed to activate an audible alarm.

Piping:  An antisiphoning valve is located between the 750-gallon AST and the pump to prevent unwanted fuel from being siphoned from the 750-gallon AST to the day tank.  The piping from the 750-gallon AST to the day tank is equipped with a polyvinyl chloride pipe sleeve to protect from corrosion.

Two 200-gallon RDA Tanks:  The tanks are located inside the RDA generator building that provides sufficient containment for the contents of the tank.  The tanks are constructed of steel and are compatible with the diesel fuel stored.  The tanks are equipped with a high level audible alarm that sounds when the fuel level is high to warn of overfilling.

  - Tank Truck Unloading Operations

All delivery drivers shall have U.S. Department of Transportation hazardous material transportation training as required by Federal law.

The remainder of this section discusses the procedures that shall be used during unloading of fuel from the tank truck into the storage tank to prevent spills.  Using the form in Appendix B, this procedure shall be documented every time refueling occurs.  Copies of this form shall be kept for 3 years.

The following procedure shall be used prior to fuel unloading:

    - Move spill containment equipment, such as booms or spill barriers, into the unloading area.

    - Ensure that the audible high-level alarm system and the automatic shutoff valve are functioning properly.

    - Determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (See Appendix B).  This ullage is communicated to the fuel supply contractor and marked in the fueling log.

    - Block the tank truck wheels.

    - Place drip pans under all pump hose fittings (if applicable) prior to unloading.

    - Ensure the fill nozzle is place in the appropriate tank appurtenance.

Both the NWS representative and the delivery driver shall remain with the vehicle at all times during unloading.  Gauges on the tank and the truck shall be continuously monitored to ensure the ullage is not exceeded.  If an alarm engages, the unloading of fuel shall be stopped as soon as possible.

After fuel unloading is completed:

    - Record the amount of fuel transferred to the tank in the log (Appendix B).

    - Drain the fill hose and then ensure that all drain valves are closed (if applicable) prior to removal of the hose from the tank.

    - Pour any fuel in the drip pans, tank truck containment pool, or spill container on the fill pipe into the tank (if it has the capacity) or disposed of appropriately.

    - Inspect the tank truck before removing the blocks to ensure the lines have been disconnected from the tank.

    - Remove the blocks from the truck wheels

    - Place a copy of the fuel unloading checklist in the SPCC plan.

  - Inspections And Records

Inspection and Maintenance of Tanks:  The 750-gallon AST, day tank, and two 200-gallon RDA tanks shall be inspected weekly for any fuel outside the tank, especially at seams (including the underside).  The concrete is inspected for cracks.  The outside of exposed piping also is inspected weekly, especially at the joints such as gasket fittings.  Monthly and annual inspections shall follow the checklists shown in Appendix C.

Record Keeping:  The Environmental Focal Point or designated alternate is responsible for completing the ullage logs and documentation of fuel unloading procedures.  These records, as well as records of all inspections, shall be maintained for at least 3 years from the time of inspection.

  - Site Security

The facility is operational 24 hours a day and well lit.  Security cameras also are strategically placed around the outside of the facility.  Adequate lighting is provided for all storage tanks to detect spills that may occur at night and to deter vandalism.

The WFO generator and day tank are located in the WFO generator room that can be locked to restrict access.  Signage around the day tank and 750-gallon AST warns of the presence of a combustible liquid, that the combustible liquid is diesel fuel number 2, and that smoking is not permitted near the tank.  A fire extinguisher is located in the adjacent generator enclosure.  The 750-gallon AST is situated such that is not in the direct line of vehicular traffic.

The two 200-gallon RDA tanks are located within the RDA generator building and within a fenced area.  The RDA generator building can be locked to restrict access.  Signage around the of the tanks warns of the presence of a combustible liquid, that the combustible liquid is diesel fuel number 2, and that smoking is not permitted near the tank.  A fire extinguisher is located in the RDA generator building.

  - Training

The Environmental Focal Point (person responsible for spill prevention) and an alternate shall be trained in the intent of applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in paragraph 3, above.  Spill control and countermeasures also shall be included in the training.

Training shall be repeated once per year.  All new personnel responsible for implementing this SPCC plan shall be properly trained before beginning the new position.  A record of who was trained, when, and by whom, shall be filed with this SPCC plan and kept for a period of 3 years.

- SPILL CONTROL

This section describes control measures that shall be implemented to prevent any spilled oil from entering navigable waters or adjoining shorelines.

  - Secondary Containment Designs, Construction Material, and Volume

The 750-gallon AST is situated within a concrete secondary containment basin.  The basin is equipped with a manual drainage valve that is normally kept closed.  Should precipitation accumulate in the basin and require draining, the valve is manually opened only after it is verified that no sheen or other evidence of fuel is present to ensure that the water will not cause a harmful discharge per 40 CFR 110 prior to discharge.  A round spill container with 5-gallon capacity surrounds the fill spout to capture potential overflow during fuel transfer.  The AST is equipped with an audible high-level alarm set to engage at 85 percent of capacity (638 gallons) and an automatic shutoff valve on the cam-lock fitting fill spout that is set to close at 90 percent of the AST capacity (675 gallons).  A monitoring system that can detect one inch or more of fluid in the interstitial space of the storage tank is also present.

The WFO generator day tank is contained within the WFO generator room that provides containment and is not exposed to precipitation.  The day tank is situated over a rupture basin that is equipped with a float switch designed to detect fuel that has spilled or leaked.  This float switch automatically shuts off the pump if engaged.

Secondary containment for the two 200-gallon RDA tanks is provided for in the RDA generator building design and construction.  The RDA generator building is designed with “tub flooring” that is approximately 6-to 8-inches deep, with a raised door frame to keep fuel from spilling out of the doorway.

  - Spill Kits Type and Location

The facility shall have kits designed to absorb diesel fuel and which can prevent discharged oil from reaching nearby water bodies or storm sewers.  The kits include oil absorbent socks and mats in a polyethylene container that serves also as a disposal container.  One spill kit is stored in each of the WFO generator room and RDA generator building.

PART III - SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is on prevention.  The spill countermeasures presented do not constitute a contingency plan detailed in Title 40 CFR Part 109, nor is one required.  Such a plan is only required under Title 40 CFR 112.7(d) if it is impracticable to provide containment, diversionary structures, or equipment to prevent the discharge of oil to navigable waters.  In addition, this facility is not required to have a facility response plan under Title 40 CFR Part 112.20 because it does not:

    - Transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons, or

    - Have a total storage capacity over 1 million gallons.

- SPILL COUNTERMEASURES

This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasure activities will be undertaken until conditions are safe for workers.  The “SWIMS” procedures should be implemented as countermeasures:

S   -	Stop the leak and eliminate ignition sources.

a. 	Attempt to seal or some how stop leak if it can be done safely.

b. 	Attempt to divert flow away from catch basins with a spill barrier or the contents of the spill kit.

c. 	Eliminate all ignition sources in the immediate area.

W  -	Warn others.

a.  	Yell out “SPILL.”  Inform the person in-charge at your facility.

b. 	Account for all personnel and ensure their safety.

c. 	Notify contacts and emergency response contractor as described in the following section for assistance in control and cleanup.

I    -	Isolate the area.

a. 	Rope off the area.

M  -	Minimize your exposure.  Stay upwind.

S    -	Stand by to assist the emergency response contractor, if necessary.

- SPILL REPORTING

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The individuals and organizations that are notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

A spill report form that requests the information to be reported to all agencies in written form (to the extent known) is included in Appendix E.  Copies of the completed form should be submitted, preferably by e-mail, to the NWS Environmental Compliance Officer and the NOAA Regional Environmental Compliance Officer.

  - General Notification Procedures for All Spills

The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

- First, call 9-1-1 if there is an immediate emergency

- Next, notify the appropriate individuals within the NWS such that the individuals can keep internal records regarding the spill event.  If necessary, the individuals can provide technical assistance regarding the procurement of cleanup contractors, the potential need for follow-up assessments, regulatory reporting, waste disposal, or other issues.

1.		Mike Jacob, (301) 713-1838 Ext. 165, JMichael.Jacob@noaa.gov, NWS Environmental Compliance Officer

2.		Olga Kebis, (301) 713-1838 Ext. 173, Olga.Kebis@noaa.gov, NWS Safety Officer

3.		Kirt Grahl, (816) 426-3226, Ext. 470, Kirt.Grahl@noaa.gov, NWS Central Regional Environmental/Safety Coordinator

4.		Sherilyn Villegas, (816) 426-3925, Ext. 263, Sherilyn.S.Villegas@noaa.gov, NOAA Central Regional Environmental Compliance Officer

2.          Federal Notification

The Federal Clean Water Act as described in Title 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency’s (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  Title 40 CFR Part 110.3 defines “may be harmful” as a discharge that:

    - Violates applicable water quality standards, or

    - Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or causes a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines.

If either of these criterion are met contact:

    - The National Response Center (EPA and USCG):  (800) 424-8802

Under the SPCC regulations, spill information listed in Title 40 CFR Part 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

    - A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shorelines in a single event, or

    - Two spill events that cause visible sheens upon navigable waters or adjoining shorelines within any 12-month period.

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA); therefore, no other notification to the EPA is required for discharges of diesel fuel other than those listed above.

3.          State Notification

To satisfy the state reporting requirements, the location and quantity of the spill must be determined.  Under the Kansas Administrative Regulations, Part 28-44-24, a reportable quantity (RQ) is defined as follows:

    - Any spill over 25 gallons, or

    - Any spill which creates a sheen upon navigable waters of the State.

If one or both of these criteria are met, contact the Kansas Emergency Spill Hotline within 24 hours of obtaining knowledge of the release:

    - (785) 296-1679 (During business hours)

    - (785) 296-0614 (After business hours)

4.          Cleanup Contractor Notification

An emergency response contractor also should be notified to assist with the clean up of a spill, if necessary.  Contact information for at least three emergency response vendors shall be maintained in this plan.  NWS has identified the following contractors that are available for emergency response:

    - Haz-Mat Response, Inc.		(800) 229-5252

    - Integrated Solutions		(620) 264-7050

    - Safety Kleen			(620) 225-5016

    - 3E Company			(800) 468-1760

PART IV - RECOMMENDED IMPROVEMENTS

In accordance with Title 40 CFR Section 112.7, this section presents physical upgrades or procedural changes that are not yet fully operational but are called for in the plan.

- PHYSICAL UPGRADES

  - Secondary Containment

The facility should install a locking valve onto the drainage valve of the 750-gallon AST containment basin.  This upgrade should be implemented within 6 months of the date of this plan.

- PROCEDURAL CHANGES

  - Inspections and Preventative Maintenance

The inspection checklists found in Appendix C should be followed.  This requirement is found in Title 40 CFR Part 112.7(e)(8).  The area within and around all tanks shall be inspected for signs of leakage regularly.  Visual inspections of the outside each of the tank’s walls shall be inspected for potential problems with tank integrity such as leaks or evidence of cracking or breaching.  Also, the interstitial monitoring device in the 750-gallon AST is designed to monitor the integrity of its primary tank.  If a problem is suspected with any tank, tightness testing should be initiated soon after discovery.

  - Training

The Environmental Focal Point (person responsible for spill prevention at the facility) and an alternate should be trained in the intent of the applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in the previous section.  Spill control and countermeasures also should be included in the training.  The alternate should be designated in case the primary person is off the site at the time of a spill.  A recommended outline for the training is found in Appendix D.

Training should be repeated once per year.  All new personnel responsible for implementing the SPCC plan should be properly trained before beginning the new position.  A record of who was trained, when, and by whom, should be filed with this SPCC plan and kept for a period of three years.  This requirement is found in Title 40 CFR 112.7(e)(10).

Spill prevention briefings for operating personnel should be conducted at frequent intervals to ensure adequate understanding of the SPCC plan and to describe spill events or failures, malfunctioning components, and recently developed precautionary measures.

Figure 1 Site Location

Figure 2 Site Layout

TABLE 1

DESCRIPTIVE INVENTORY OF FACILITY STORAGE

| Tank | Nominal Capacity (Gallons) | Product Stored | Type | Double Walled? |
| --- | --- | --- | --- | --- |
| 750-Gallon AST | 750 | Diesel fuel number 1 | AST | No1 |
| RDA Tank | 200 | Diesel fuel number 1 | AST | No2 |
| RDA Tank | 200 | Diesel fuel number 1 | AST | No2 |
| 25-Gallon Day Tank | 25 | Diesel fuel number 1 | AST | Yes3 |
| Total Capacity | 1,175 |  |  |  |

Notes:

AST	Aboveground storage tank

1		Tank is situated within a sufficiently impervious concrete containment basin.

2		The RDA tank is located within a building that is designed and constructed to provide sufficient secondary containment.

3		The day tank is situated over a rupture basin that is capable of containing 110 percent the tank volume and is located within a building.

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| 750-Gallon AST | Overfilling or a ruptured hose during fueling | >0 to 40a | 80b | Northwest or South | Operational procedures are in place to prevent overfilling. |
|  | Failure of fuel supply line to pump | >0 to 750 | Variable | Northwest or South | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 750 | Variable | Northwest or South | Low probability event that both primary and secondary tank shells would fail. |
|  | Vehicle collision | >0 to 750 | Variable | Northwest or South | Tank is not in the direct line of traffic. |
|  | Overturn or puncture during natural disaster | >0 to 750 | Variable | Northwest or South | Low probability event. |
| 25-Gallon Day Tank | Failure of the pump to shut down after filling day tank or failure of the line from pump to day tank. | >0 to 750 | Variable | Northwest | Can be minimized through routine inspections. |
|  | Failure of fuel return line | >0 | 10c | Northwest | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 25 | Variable | Northwest | Low probability event can be minimized through regular inspections and maintenance. |
|  | Overturn or puncture during natural disaster | >0 to 25 | Variable | Northwest | Low probability event. |

Notes:

a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

c	Estimated return line flow rate.

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| Each of two 250-Gallon RDA Tanks | Overfilling or a ruptured hose during fueling | >0 to 40a | 80b | Northwest | Operational procedures are in place to prevent overfilling. |
|  | Failure of fuel supply line to pump | >0 to 200 | Variable | Northwest | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 200 | Variable | Northwest | Low probability event that both primary and secondary tank shells would fail. The RDA generator building is within a fenced area, can be kept locked, and designed and constructed to contain spills. |
|  | Overturn or puncture during natural disaster | >0 to 200 | Variable | Northwest | Low probability event. Double-walled tank gives extra protection from rupture, but a large tornado could cause a spill. |

Notes:

a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

c	Estimated return line flow rate.

APPENDIX A

TANK RECORDS

APPENDIX B

TANK ULLAGE/FUELING LOG AND

FUEL UNLOADING PROCEDURE CHECKLIST

(2 Pages)

APPENDIX B-1

TANK ULLAGE AND FUELING LOG

Tank Capacity 			  gallons

| Date | Initials | Gauge Reading | Initial Volume of Fuel in Tanka (Gallons) | Available Capacity or Ullageb (Gallons) | Quantity Added (Gallons) | Comments |
| --- | --- | --- | --- | --- | --- | --- |

Notes:

a	From gauge reading

b	Available capacity = tank capacity - initial volume of fuel in tank

APPENDIX B-2

FUEL UNLOADING PROCEDURE CHECKLIST

Date:										Tank:

NWS Representative:								Supplier:

| / | ITEM | DESCRIPTION | COMMENT |
| --- | --- | --- | --- |
| The following six items must be completed prior to fuel unloading: |
|  | 1 | Move spill containment equipment, such as booms or spill barriers, into the unloading area. |  |
|  | 2 | Ensure the audible high-level alarm system and automatic shutoff valve are functioning properly. |  |
|  | 3 | Determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (see Appendix B, page B-1 in SPCC plan). This ullage should then be marked in the fueling log and communicated to the tank truck unloading contractor. |  |
|  | 4 | Block the wheels of the tank truck. |  |
|  | 5 | Place drip pans under all pump hose fittings (if applicable) after the hose is hooked up to the tank and prior to unloading. |  |
|  | 6 | Ensure the fill nozzle is placed in the appropriate tank appurtenance. |  |
| During unloading |
|  | 7 | Ensure that the NWS representative and the tank truck operator remain with the vehicle at all times during unloading. |  |
|  | 8 | Monitor the gauges on the tank and the truck continuously to ensure the ullage is not exceeded. If the audible high-level alarm sounds, the unloading of fuel is stopped as soon as possible. |  |
| After fuel unloading is completed |
|  | 9 | Record the amount of fuel unloaded in the log (Appendix B, page B-1). |  |
|  | 10 | Prior to removing the fill hose from the tank, ensure that it is drained and that all drain valves are closed (if applicable). |  |
|  | 11 | Any fuel accumulated in the drip pans or spill container on the fill pipe should be poured into the tank (if it has the capacity) or disposed of appropriately (describe how it was disposed of, if applicable). |  |
|  | 12 | Inspect the tank truck prior to removing the blocks to ensure the lines have been disconnected from the tank. |  |
|  | 13 | Remove the blocks from tank truck wheels. |  |
|  | 14 | Place a copy of this fuel-unloading checklist in the SPCC plan. |  |

APPENDIX C

INSPECTION CHECKLISTS

(2 Pages)

| MONTHLY INSPECTION CHECKLIST |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: Signature: |
| A. TANKS | YES | NO | NOTES |
| 1. Are tanks marked properly? |  |  |  |
| 2. Is area atop and around tank and within berm free of combustible materials, debris, and stains? |  |  |  |
| 3. Is there any oil on the ground, concrete, or asphalt around the tank? |  |  |  |
| 4. Are there any visible cracks or indications of corrosion on the tank, at fittings, joints, or seals (such as paint peeling or rust spots)? |  |  |  |
| 5. Are there any raised spots, dents, or cracks on the tank? |  |  |  |
| 6. Does it appear that the foundation has shifted or settled? |  |  |  |
| 7. Is the fuel gauge working properly? |  |  |  |
| 8. Are all vents clear so they may properly operate? |  |  |  |
| 9. If rainwater is present within containment, does capacity remain for spill control (if applicable)? |  |  |  |
| B. PIPING |  |  |  |
| 1. Is there any oil on the outside of or under any aboveground piping, hoses, fittings, or valves? |  |  |  |
| 2. Are aboveground piping, hoses, fittings, or valves in good working condition? |  |  |  |
| C. SECURITY/SAFETY/SPILL COUNTERMEASURES |  |  |  |
| 1. Are lights working properly to detect a spill at night? |  |  |  |
| 2. Are all locks in the “lock” position? |  |  |  |
| 3. Are all warning signs properly posted and readable? |  |  |  |
| 4. Are vehicle guard posts in place and properly secured (if applicable)? |  |  |  |
| 5. Are spill kits easily accessible, protected from the weather, complete, and replenished if necessary? |  |  |  |
| Corrective Actions Required: |  |  |  |

| ANNUAL INSPECTION CHECKLIST |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: Signature: |
| A. MONTHLY CHECKLIST | YES | NO | NOTES |
| 1. Have monthly inspection checklists been completed? |  |  |  |
| B. TANKS |  |  |  |
| 1. Are all alarms and automatic shutoff devices working properly? |  |  |  |
| 2. Is interstitial monitor functioning properly (if applicable)? |  |  |  |
| C. OTHER |  |  |  |
| 1. |  |  |  |
| Corrective Actions Required: |  |  |  |

APPENDIX D

TRAINING OUTLINE AND

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS

PARTS 112.1 THROUGH 112.20 - OIL POLLUTION PREVENTION

(29 Pages)

APPENDIX D

OUTLINE FOR SPILL PREVENTION, CONTROL, AND COUNTERMEASURES TRAINING

Training will be provided for facility personnel at the following times:

C	System startup or whenever new equipment is installed

C	Within the first week of employment for new personnel

C	Annually

The training will include complete instruction in the elements of the facility’s Spill Prevention, Control, and Countermeasures plan and will include the following:

A.	Pollution Control Laws, Rules, and Regulations Including a Summary of Title 40 of the Code of Federal Regulations Part 112, “Oil Pollution Prevention” (see Attachment)

B.	Fuel Storage

1.	Purpose and application of the following system elements:

a.	Tanks

b.	Piping

c.	Pumps

d.	Accessory equipment

e.	Electronic monitors

2.	Operation, maintenance, and inspection of system elements

C.	Spill Prevention

1.	Potential spill sources

2.	Spill flow direction and impact on navigable waters

3.	Procedures to prevent spills, especially during fuel unloading

D.	Spill Control

1.	Secondary containment

2.	Safety valves

3.	Pump and equipment shutoff switches

4.	Use of catch basin inlet covers or other diversionary devices

E.	Spill Countermeasures

1.	Location and use of emergency phone numbers

2.	Location and use of fire extinguishers

3.	Location and use of spill cleanup kit

4.	Stopping the leak

ATTACHMENT

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS

PARTS 112.1 THROUGH 112.20 - OIL POLLUTION PREVENTION

APPENDIX E

SPILL REPORTING FORM

(1 Page)

APPENDIX E

SPILL REPORTING FORM

| GENERAL |
| --- |
| Name of Facility: National Weather Service Dodge City Weather Forecast Office | Address: 104 Airport Road Dodge City, KS 67801 |
| Completed By: | Organization: National Weather Service |
| Position: | Phone: |
| SPILL INFORMATION |
| Date: | Time: |
| Location at Facility: | Quantity: |
| Substance Spilled: | Other: |
| OUTSIDE NOTIFICATIONS |
| Agencies | Recorder at Outside Agency | Date and Time |
| Call 9-1-1 if there is an immediate emergency |  |  |
| NWS/NOAA: Mike Jacob: (301) 713-1838, Ext. 165 Olga Kebis: (301) 713-1838, Ext. 173 Kirt Grahl: (816) 426-3226, Ext. 470 Sherilyn Villegas: (816) 426-3925, Ext. 263 |  |  |
| EPA NATIONAL RESPONSE CENTER or U.S. COAST GUARD: (800) 424-8802 |  |  |
| Kansas Emergency Spill Hotline: During Business Hours: (785) 296-1679 After Business Hours: (785) 296-0614 |  |  |
| INFORMATION ON SOURCE AND CAUSE |
| 5. DESCRIPTION OF ENVIRONMENTAL DAMAGE |
| 6. CLEANUP ACTION(S) TAKEN |
| 7. CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |

Note:	All information must be filled in.  If something is unknown, write “unknown.”

Copies must be submitted to the NWS/NOAA personnel listed above.

APPENDIX F

CROSS REFERENCE OF THE REQUIREMENTS OF

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS,

PART 112.7, WITH THIS PLAN

(1 Page)

APPENDIX F

CROSS REFERENCE OF THE REQUIREMENTS OF 40 CFR 112.7 WITH THIS PLAN

| CFR Citation | Item | Plan Location |
| --- | --- | --- |
| 112.7(a) | Spill History | Part I.B.4 |
| 112.7(b) | Potential Spill Prediction, Volumes, and Rates | Part I.B.5 and Table 2 |
| 112.7(c) | Containment and Diversionary Structures | Part I.B.2 and Part II.B.2 |
| 112.7(d) | Secondary Containment Impracticability | Not Applicable |
| 112.7(e)(1) | Drainage Control | Part I.B.3 |
| 112.7(e)(2) | Bulk Storage Tanks and Secondary Containment | See Subparts |
| 112.7(e)(2)(I) | Tank Compatibility with Its Contents | Part II.A.1 |
| 112.7(e)(2)(ii) | Diked Area Construction and Containment for Storage Tanks | Not Applicable |
| 112.7(e)(2)(iii) | Diked Area Inspection and Drainage of Rainwater | Not Applicable |
| 112.7(e)(2)(iv) | Corrosion Protection of Buried Metallic Storage Tanks | Not Applicable |
| 112.7(e)(2)(v) | Corrosion Protection of Partially Buried Metallic Tanks | Not Applicable |
| 112.7(e)(2)(vi) | Aboveground Tank Periodic Integrity Testing | Part IV.B.1 |
| 112.7(e)(2)(vii) | Control of Leakage through Internal Heating Coils | Not Applicable |
| 112.7(e)(2)(viii) | Tank Installation Fail-safe Engineered | Part II.A.1, B.1 |
| 112.7(e)(2)(ix) | Observation of Disposal Facilities for Effluent Discharge | Not Applicable |
| 112.7(e)(2)(x) | Visible Oil Leak Corrections from Tank Seams and Gaskets | Part II.A.3 & Appendix C |
| 112.7(e)(2)(xi) | Appropriate Position of Mobile or Portable Tanks | Not Applicable |
| 112.7(e)(3) | Facility Transfer Operations | See Subparts |
| 112.7(e)(3)(i) | Buried Piping Installation Protection and Examination | Part II.A.1 & Appendix C |
| 112.7(e)(3)(ii) | Not-in-service and Standby Terminal Connections | Not Applicable |
| 112.7(e)(3)(iii) | Pipe Support Designs | Not Applicable |
| 112.7(e)(3)(iv) | Aboveground Valve and Pipeline Examination | Not Applicable |
| 112.7(e)(3)(v) | Aboveground Piping Protection from Vehicular Traffic | Not Applicable |
| 112.7(e)(4) | Facility Truck Unloading Operations | Part II.A.2 |
| 112.7(e)(5-7) | Oil Production Facilities (Onshore) and Oil Drilling, Production, or Work over Facilities (On Shore and Offshore) | Not Applicable |
| 112.7(e)(8) | Inspections and Record Keeping | Part II.A.3 |
| 112.7(e)(9) | Security | See Subparts |
| 112.7(e)(9)(i) | Fencing | Part II.A.4 |
| 112.7(e)(9)(ii) | Flow Valves Locked | Not Applicable |
| 112.7(e)(9)(iii) | Starter Controls Locked | Not Applicable |
| 112.7(e)(9)(iv) | Pipeline Loading and Unloading Connections Securely Capped | Not Applicable |
| 112.7(e)(9)(v) | Lighting Adequate to Detect Spills | Part II.A.4 |
| 112.7(e)(10) | Training | See Subparts |
| 112.7(e)(10)(i) | Personnel Instructions | Part II.A.5 & Appendix D |
| 112.7(e)(10)(ii) | Designated Person Responsible for Spill Prevention | Page i |
| 112.7(e)(10)(iii) | Spill Prevention Briefings | Part IV.B.2 |

Note:	CFR	Code of Federal Regulations