# GCC Tape Library Room Impact

# General

Room lighting and other working environment power.

# Library

The table below lists the approximate Physical dimensions of the libraries being considered.  Space for at least 4 tape libraries should be provided. In FY06 and FY07  2 tape libraries will be acquired: a general purpose library and a CMS library. Minimum footprint to consider for this acquisition should be the two largest of these, the (boxed) AML-2 (768 sq ft) and a Storage Tek SL8500 10000 slot robot (198 sq ft).

| Vendor | Library | H (ft) | W (ft) | L (ft) | FP (sq ft) | slots |
| --- | --- | --- | --- | --- | --- | --- |
| ADIC | AML2-2Q-1R | ? | 24 | 32 | 768 | 9600 |
| ADIC | 3 x I2000 | 6.45 | 9.58 | 15.8 | 151.3 | 9900 |
| Storage Tek | SL8500 | 7.5 | 5.6 | 18.5 | 103.6 | 6640 |
| Storage Tek | SL8500 | 7.5 | 5.6 | 30 | 198 | 10000 |
| IBM | 3584-L52 | 5.9 | 4 | 41.4 | 164.4 | 6887 |
| Spectralogic | T950 | 6.56 | 3.6 | 12.76 | 45.9 | 6000 |

Library power consumption is expected to be less than 2 kVA for each library, so a total of  8 kVA should be available for libraries.

# Peripheral Equipment (movers, servers and drives)

Up to 100 drives and movers will be required. The movers run at about 2.5 Amps in a 2u form factor so about 15 can be accommodated in a rack with 2 20 Amp feeds. This requires about 8 racks for a total occupation.  Also a rack of server machines, up to 8, may be required. This should also be able to be accommodated by two 20 Amp feeds.

| Equipment | Count | Power/Unit | Total Power |
| --- | --- | --- | --- |
| Movers | 100 | 300VA (2.5A) | 30 kVA |
| Servers | 8 | 420VA (3.5A) | 3.4 kVA |
| Racks | 9 | - | - |
| Tape drives | 100 | 100VA | 10 kVA |
| Total peripheral power |  |  | 43 kVA |

# Networking Equipment and other connectivity

The above equipment each requires a single GB NIC.  Network switching supporting 120 GB connections to the FNAL core network and 25 connections to the enstore network is required. In addition the private sub-net used by enstore may need to extend from FCC to GCC.

Tape drives attached to the library will communicate with the racked mover nodes via Fiber Channel connectivity (up to 100 fibers).

All connectivity listed above is to be routed via overhead cable trays.

# Environment

Temperature and relative humidity ( non condensing ) need to be maintained at 72 degrees Fahrenheit (dry bulb), 50% RH for the media. The relative humidity should always be maintained within the range of [40,60] % and the temperature [65,79] degrees Fahrenheit.

Tape drive operating environment requirements fall within the range of the media requirements.

The room should provide a relatively dust free computer room environment.

# Service across power outages

Tape library service needs to be maintained across unplanned power outages. It is expected that a combination of UPS and some fashion (permanent or rolling) of backup generator will provide this capability. In the case of a an unplanned power disruption, enough UPS needs to be supplied to keep the tape library, its supporting peripherals (tape drives, servers, movers) and all supporting networking, and the AC (to maintain required temperature and RH for the tape media)  powered up until contingency generators are moved into place and providing power.

# Footnotes

These requirements meet  Storage Tek’s  and Imation’s media archival requirements