## 25F nomo
Murray-Custer #1 230kV Line (S>N @ 100MW)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 031
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6648.3886
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -85.86 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 105.23 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | -2.69 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1470.62 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 105.23 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3137.18 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1280.2 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 3015.35 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1361.42 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2512.13 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1470.62 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | -2.69 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3028.64 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1361.42 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3136.63 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3136.63 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3137.18 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3012.59 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 3001.74 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2855.64 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 3012.59 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -85.86 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 3015.35 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1280.2 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2855.32 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3028.64 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2855.64 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 3001.74 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2512.13 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2855.32 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Murray-Custer #1 230kV Line (S>N @ 100MW)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 031
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6321.2946
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 408.64 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 624.29 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 517.95 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1804.13 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 624.29 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2937.74 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1589.41 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2694.63 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1672.27 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2607.16 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1804.13 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 517.95 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3086.81 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1672.27 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2928.33 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2928.33 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2937.74 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2687.04 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2680.28 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2600.06 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2687.04 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 408.64 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2694.63 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1589.41 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2596.5 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3086.81 | N-2: Monroe - Custer #1&2 500kV | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2600.06 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2680.28 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2607.16 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2596.5 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Murray-Custer #1 230kV Line (S>N @ 100MW)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 031
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5957.5992
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 10.99 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 219.77 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 117.04 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1497.34 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 219.77 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2898.39 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1303.13 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2654.48 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1392 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2565.95 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1497.34 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 117.04 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3017.81 | BFR: A1238 Cust-Intalco #1 & Belling-Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1392 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2891.86 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2891.86 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2898.39 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2651.57 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2648.3 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2561.7 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2651.57 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 10.99 | BFR: Bellingham 230kV Bus | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2654.48 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1303.13 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2553.83 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3017.81 | BFR: A1238 Cust-Intalco #1 & Belling-Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2561.7 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2648.3 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2565.95 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2553.83 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Murray-Custer #1 230kV Line (S>N @ 100MW)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 031
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4916.2238
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1723.27 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1944.81 | BFR: A1238 Cust-Intalco #1 & Belling-Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1832.77 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2762.75 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1944.81 | BFR: A1238 Cust-Intalco #1 & Belling-Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2794.63 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2526.04 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2556.48 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2643.08 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2423.42 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2762.75 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1832.77 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2780.19 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2643.08 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2786.3 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2786.3 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2794.63 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2546.54 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2540.46 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2416.88 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2546.54 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1723.27 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2556.48 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2526.04 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2411.29 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2780.19 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2416.88 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2540.46 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2423.42 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2411.29 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Murray-Custer #1 230kV Line (S>N @ 100MW)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 031
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4641.8867
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1964.95 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2165.05 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2069.44 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2956.19 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 2165.05 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2760.53 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2761.54 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2169.95 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2851.25 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1624.92 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2956.19 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2069.44 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2751.25 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2851.25 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2754.68 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2754.68 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2760.53 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2458.84 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2452.07 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2254.41 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2458.84 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1964.95 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2169.95 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2761.54 | N-1: Bellingham - Custer W #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2211.83 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2751.25 | N-2: Monroe - Custer #1&2 500kV | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2254.41 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2452.07 | N-2: Monroe - Custer #1&2 500kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1624.92 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2211.83 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Murray-Custer #1 230kV Line (S>N @ 100MW)
G0 | -85.86 | 408.64 | 10.99 | 1723.27 | 1964.95
G1 | -2.69 | 517.95 | 117.04 | 1832.77 | 2069.44 | Season/Year: | WINTER 2009
G2 | 105.23 | 624.29 | 219.77 | 1944.81 | 2165.05 | Direction: | North-to-South (NS)
G3 | 1280.2 | 1589.41 | 1303.13 | 2526.04 | 2761.54 | Case Loads: | Heavy Loads
G4 | 1361.42 | 1672.27 | 1392 | 2643.08 | 2851.25 | Outage: | 031
G5 | 1470.62 | 1804.13 | 1497.34 | 2762.75 | 2956.19 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3028.64 | 3086.81 | 3017.81 | 2780.19 | 2751.25 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3136.63 | 2928.33 | 2891.86 | 2786.3 | 2754.68 | Study Person: | JGO7470
G8 | 3137.18 | 2937.74 | 2898.39 | 2794.63 | 2760.53 | Source: | 031WINTER09v2NSH(SN@100MW)
G9 | 3001.74 | 2680.28 | 2648.3 | 2540.46 | 2452.07
G10 | 3012.59 | 2687.04 | 2651.57 | 2546.54 | 2458.84
G11 | 3015.35 | 2694.63 | 2654.48 | 2556.48 | 2169.95
G12 | 2855.32 | 2596.5 | 2553.83 | 2411.29 | 2211.83
G13 | 2855.64 | 2600.06 | 2561.7 | 2416.88 | 2254.41
G14 | 2512.13 | 2607.16 | 2565.95 | 2423.42 | 1624.92
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 031 | Murray-Custer #1 230kV Line (S>N @ 100MW)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6648.3886 | -85.19 | -1.95 | 106.08 | 1278.69 | 1359.24 | 1468.01 | 3014.13 | 3121.61 | 3120.65 | 2988.07 | 2997.68 | 3001.82 | 2843.28 | 2843.05 | 2503.83
35F | 6321.2946 | 410.22 | 517.71 | 624.18 | 1586.23 | 1668.82 | 1800.29 | 3071.25 | 2913.2 | 2922.07 | 2668.15 | 2674.58 | 2682.68 | 2585.58 | 2589.37 | 2597.56
45F | 5957.5992 | 11.74 | 118.4 | 220.73 | 1301.13 | 1391.1 | 1494.28 | 3004.13 | 2878.01 | 2884.32 | 2636.21 | 2640.55 | 2642.57 | 2541.5 | 2550.92 | 2555.31
60F | 4916.2238 | 1718.51 | 1828.44 | 1938.12 | 2516.15 | 2632.77 | 2751.46 | 2767.22 | 2773.06 | 2781.4 | 2530.66 | 2536.97 | 2546.53 | 2402.32 | 2407.75 | 2413.28
70F | 4641.8867 | 1957.69 | 2063.1 | 2156.87 | 2749.88 | 2838.85 | 2942.8 | 2739.21 | 2742.02 | 2748.83 | 2442.81 | 2449.27 | 2162.37 | 2204.27 | 2246.18 | 1926.32

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -85.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 478.08 | 478 | 6659.72 | -85.19 | -229.47 | FULL
G1 | -2.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 477.42 | 477.32 | 6589.17 | -1.95 | -152.48 | FULL
G2 | 105.23 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 477.67 | 477.58 | 6598.75 | 106.08 | -59.46 | FULL
G3 | 1280.2 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 485.38 | 485.34 | 6652.43 | 1278.69 | 660.3 | FULL
G4 | 1361.42 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 484.3 | 484.17 | 6584.08 | 1359.24 | 736.02 | FULL
G5 | 1470.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 485 | 484.84 | 6597.43 | 1468.01 | 828.6 | FULL
G6 | 3028.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 492.33 | 492.36 | 6694.95 | 3014.13 | 1803.31 | FULL
G7 | 3136.63 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 81.05 | 836.42 | 835.29 | 6631.73 | 3121.61 | 1908.79 | FULL
G8 | 3137.18 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 81.05 | 834.64 | 833.62 | 6648.41 | 3120.65 | 1916.5 | FULL
G9 | 3001.74 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -780.98 | -781.89 | 6718.18 | 2988.07 | 1995.94 | FULL
G10 | 3012.59 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -782.8 | -783.57 | 6650.9 | 2997.68 | 2027.39 | FULL
G11 | 3015.35 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -782.53 | -783.47 | 6663.03 | 3001.82 | 2060.85 | FULL
G12 | 2855.32 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -786.27 | -786.74 | 6727.7 | 2843.28 | 2065.53 | FULL
G13 | 2855.64 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -786.85 | -789.37 | 6662.42 | 2843.05 | 2083.49 | FULL
G14 | 2512.13 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.82 | 458.91 | 458.97 | 6658.26 | 2503.83 | 1944.18 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 408.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 472.02 | 471.96 | 6322.05 | 410.22 | 110.28 | FULL
G1 | 517.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 472.2 | 472.14 | 6251.85 | 517.71 | 203.13 | FULL
G2 | 624.29 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 472.31 | 472.25 | 6263.58 | 624.18 | 295.53 | FULL
G3 | 1589.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 478.59 | 478.53 | 6322.98 | 1586.23 | 884.54 | FULL
G4 | 1672.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 478.16 | 477.96 | 6255.55 | 1668.82 | 954.97 | FULL
G5 | 1804.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 479.14 | 479.39 | 6271.19 | 1800.29 | 1065.63 | FULL
G6 | 3086.81 | Branch CUST BEL (95007) TO BELLNGHM (40095) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 81.05 | 814.22 | 813.13 | 6370.63 | 3071.25 | 1870.12 | FULL
G7 | 2928.33 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 822.89 | 821.75 | 6300.89 | 2913.2 | 1805.05 | FULL
G8 | 2937.74 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 825.89 | 824.69 | 6315.67 | 2922.07 | 1854.79 | FULL
G9 | 2680.28 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 831.06 | 829.96 | 6378.78 | 2668.15 | 1836.97 | FULL
G10 | 2687.04 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 831.82 | 828.94 | 6312.5 | 2674.58 | 1869.11 | FULL
G11 | 2694.63 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 819.36 | 817.6 | 6328.46 | 2682.68 | 1912.83 | FULL
G12 | 2596.5 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 820.26 | 817.4 | 6391.52 | 2585.58 | 1957.71 | FULL
G13 | 2600.06 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 815.19 | 813.18 | 6325.64 | 2589.37 | 1986.79 | FULL
G14 | 2607.16 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 818.28 | 816.2 | 6339.44 | 2597.56 | 2019.62 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 10.99 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 438.28 | 438.24 | 6040.4 | 11.74 | -118.17 | FULL
G1 | 117.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 438.42 | 438.39 | 5969.43 | 118.4 | -24.45 | FULL
G2 | 219.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: Bellingham 230kV Bus | 6.16 | 438.5 | 438.46 | 5980.58 | 220.73 | 65.95 | FULL
G3 | 1303.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 442.91 | 442.99 | 6036.16 | 1301.13 | 722.49 | FULL
G4 | 1392 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 442.2 | 441.98 | 5968.59 | 1391.1 | 804.84 | FULL
G5 | 1497.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 442.39 | 442.57 | 5983.19 | 1494.28 | 894.09 | FULL
G6 | 3017.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: A1238 Cust-Intalco #1 & Belling-Cust #1 230kV | 8.72 | 446.98 | 446.98 | 6081.7 | 3004.13 | 1843.93 | FULL
G7 | 2891.86 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 816.86 | 814.97 | 6015.27 | 2878.01 | 1801.03 | FULL
G8 | 2898.39 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 817.89 | 815.04 | 6031.67 | 2884.32 | 1831.59 | FULL
G9 | 2648.3 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 810.43 | 809.31 | 6094.17 | 2636.21 | 1832.44 | FULL
G10 | 2651.57 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 809.5 | 808.58 | 6027.88 | 2640.55 | 1884.78 | FULL
G11 | 2654.48 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 804.98 | 802.79 | 6043.44 | 2642.57 | 1903.02 | FULL
G12 | 2553.83 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 800.87 | 799.51 | 6105.71 | 2541.5 | 1960.48 | FULL
G13 | 2561.7 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 808.13 | 806.69 | 6041.29 | 2550.92 | 1995.51 | FULL
G14 | 2565.95 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 805.14 | 803.74 | 6057.26 | 2555.31 | 2007.86 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1723.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 443.48 | 443.6 | 4962.46 | 1718.51 | 1014.85 | FULL
G1 | 1832.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 443.75 | 443.85 | 4898.08 | 1828.44 | 1107.61 | FULL
G2 | 1944.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: A1238 Cust-Intalco #1 & Belling-Cust #1 230kV | 8.72 | 444.52 | 444.9 | 4915.95 | 1938.12 | 1203.54 | FULL
G3 | 2526.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 446.82 | 446.91 | 4983.14 | 2516.15 | 1550.12 | FULL
G4 | 2643.08 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 447.14 | 447.2 | 4921.77 | 2632.77 | 1630.84 | FULL
G5 | 2762.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 447.29 | 446.94 | 4941.82 | 2751.46 | 1747.35 | FULL
G6 | 2780.19 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 763.47 | 763.6 | 5008.21 | 2767.22 | 1801.6 | FULL
G7 | 2786.3 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 763.21 | 764.14 | 4943.22 | 2773.06 | 1833.7 | FULL
G8 | 2794.63 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 761.5 | 762.55 | 4960.7 | 2781.4 | 1868.96 | FULL
G9 | 2540.46 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -727.83 | -734.69 | 5018.14 | 2530.66 | 1877.24 | FULL
G10 | 2546.54 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -728.86 | -736.17 | 4953.28 | 2536.97 | 1914.39 | FULL
G11 | 2556.48 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 767.42 | 765.96 | 4970.92 | 2546.53 | 1947.69 | FULL
G12 | 2411.29 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -733.37 | -734.61 | 5033.18 | 2402.32 | 1958.74 | FULL
G13 | 2416.88 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -731.52 | -732.79 | 4969.14 | 2407.75 | 1989.92 | FULL
G14 | 2423.42 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -89.84 | -734.3 | -735.5 | 4986.94 | 2413.28 | 2024.21 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1964.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 445.21 | 445.23 | 4633.63 | 1957.69 | 1174.1 | FULL
G1 | 2069.44 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 444.87 | 445.03 | 4569.96 | 2063.1 | 1264.59 | FULL
G2 | 2165.05 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 444.64 | 444.8 | 4588.95 | 2156.87 | 1358.83 | FULL
G3 | 2761.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 447.53 | 447.59 | 4657.85 | 2749.88 | 1709.28 | FULL
G4 | 2851.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 447.5 | 447.37 | 4596.45 | 2838.85 | 1788.41 | FULL
G5 | 2956.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-1: Bellingham - Custer W #1 230kV | 8.72 | 447.8 | 447.86 | 4617.64 | 2942.8 | 1874.46 | FULL
G6 | 2751.25 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 755.13 | 753.24 | 4673.14 | 2739.21 | 1820.34 | FULL
G7 | 2754.68 | Branch BELLNGHM (40095) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | 100 | 751.84 | 750.68 | 4608.94 | 2742.02 | 1850.08 | FULL
G8 | 2760.53 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.38 | -173.67 | -173.61 | 4623.31 | 2748.83 | 1879.39 | FULL
G9 | 2452.07 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -88.94 | -706.35 | -704.77 | 4682.73 | 2442.81 | 1857.39 | FULL
G10 | 2458.84 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -88.94 | -706.24 | -704.62 | 4618.85 | 2449.27 | 1889.44 | FULL
G11 | 2169.95 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.38 | -174.18 | -174.18 | 4624.55 | 2162.37 | 1752.44 | FULL
G12 | 2211.83 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -21.23 | -686.33 | -686.86 | 4694.71 | 2204.27 | 1875.29 | FULL
G13 | 2254.41 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -21.23 | -685.19 | -685.16 | 4633.11 | 2246.18 | 1926.32 | FULL
G14 | 1624.92 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.38 | -173.97 | -173.97 | 4626.58 | 1620.62 | 1589.02 | FULL
031WINTER09v2NSH(SN@100MW)