SPILL PREVENTION, CONTROL, AND COUNTERMEASURES PLAN

NATIONAL WEATHER SERVICE

National Weather Forecast Office

8400 Remount Road

North Little Rock, Arkansas  72118

Original Date of Plan	:	October 13, 2000

Date of Last Plan Review	:	October 13, 2000

Date of Last Amendment

and P.E. Certification	:	October 13, 2000

Designated Person Responsible for Spill Prevention:

Edward J. Pasierb, Environmental/Safety Focal Point

Telephone: (501) 834-9102

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of Title 40 of the Code of Federal Regulations (40 CFR) Part 112, I attest that this spill prevention, control, and countermeasures (SPCC) plan has been prepared in accordance with good engineering practices.

| William A. Clattenburg |
| --- |
| Printed Name of Registered Engineer |
| Signature of Registered Engineer and Date |
| Registration No. 7970 | State AR |

REVIEW DOCUMENTATION AND MANAGEMENT APPROVAL PAGE

REVIEW DOCUMENTATION

In accordance with 40 CFR Part 112.5(b), a review and evaluation of this SPCC plan is conducted at least once every 3 years.  As a result of this review and evaluation, the National Weather Service will amend the SPCC plan within 6 months of the review to include more effective prevention and control technology if the following both apply:

- Such technology will significantly reduce the likelihood of a spill event from the facility.

- Such technology has been field-proven at the time of review.

Any amendment to the SPCC plan shall be certified by a Professional Engineer within 6 months after a change in the facility design, construction, operation, or maintenance occurs that materially affects the facility’s potential for the discharge of oil into or upon the navigable waters of the United States or adjoining shorelines.

| Review Date | Signature of Responsible Manager | Amended (Yes or No)? a |
| --- | --- | --- |

a	Amendment necessary and certified by a Registered Professional Engineer per 40 CFR Part 112.3(d)

MANAGEMENT APPROVAL

The National Weather Service is committed to the prevention of discharges of oil to navigable waters and the environment.  We maintain the highest standards for SPCC through regular review, updating, and implementation of this SPCC plan for the Weather Forecast Office located in North Little Rock, Arkansas.

Renee Fair, Meteorologist-In-Charge

Printed Name and Title of Responsible Manager

Signature and Date

CONTENTS

Section	Page

Certification	i

Review Documentation and Management Approval	ii

PART I -	GENERAL INFORMATION	1

A.	GENERAL	1

1.	Name	1

2.	Type	1

3.	Date of Initial Operation	1

4.	Location	1

5.	Name and Address of Operator	1

6.	Facility Contacts	1

B.	SITE DESCRIPTION AND OPERATIONS	1

1.	Facility Location, Layout, and Operations	1

2.	Facility Storage	2

3.	Drainage Pathway and Distance to Navigable Waters	2

4.	Spill History	2

5.	Spill Potential, Volumes, and Rates	2

PART II -	DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL	3

A.	SPILL PREVENTION	3

1.	Bulk Storage Tanks and Facility Transfer Operations	3

2.	Tanker Truck Unloading Operations	3

3.	Inspections and Records	4

4.	Site Security	4

5.	Training	4

B.	SPILL CONTROL	5

1.	Secondary Containment Designs, Construction Material, and Volume	5

2.	Spill Kits Type and Location	5

PART III -	SPILL COUNTERMEASURES AND REPORTING	6

A.	SPILL COUNTERMEASURES	6

B.	 SPILL REPORTING	6

1.	General Notification Procedures For All Spills	6

2.	Federal Notifications	7

3.	State Notification	7

4.	Cleanup Contractor Notification	8

PART IV -	RECOMMENDED IMPROVEMENTS	9

A.	PHYSICAL UPGRADES	9

1.	Tanks	9

2.	Secondary Containment Bin Valve	9

CONTENTS (Continued)

Section	Page

B.	PROCEDURAL CHANGES	9

1.	Inspections and Preventative Maintenance	9

2.	Training	9

Appendix

A	Tank Ullage/Fueling Log ANd FUeL UNLOADING PROCEDURE CHECKLIST

B	Inspection ChecklistS

C	Training Outline and Title 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.1-112.20-OIL POLLUTION PREVENTION

D	Spill RepoRtING form

E	CROSS REFERENCE OF THE REQUIREMENTS of TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.7, WITH THIS PLAN

FIGURES

Figure	Page

1	SITE LOCATION	10

2	FACILITY LAYOUT AND SPILL PATH	11

TABLES

Table	Page

1	DESCRIPTIVE INVENTORY OF FACILITY STORAGE	12

2	POTENTIAL SPILL SOURCES AND VOLUMES	13

- GENERAL INFORMATION

This part of the spill prevention, control, and countermeasures (SPCC) plan presents general information about the facility and a description of the site and its operations.

A.	GENERAL

This section of the SPCC plan provides general information about the facility.

- Name

National Weather Service (NWS) Weather Forecast Office (WFO).

- Type

This is an onshore (nonproduction) facility that operates as a weather forecasting office and is staffed 24 hours per day, 365 days per year.

- Date of Initial Operation

1974

- Location

8400 Remount Road

North Little Rock, Pulaski County, Arkansas  72118

- Name and Address of Operator

National Weather Service

Southern Region

819 Taylor Street

Fort Worth, Texas  76102

- Facility Contacts

Name	Title					Telephone Number

Ed Pasierb 	Environmental/Safety Focal Point	(501) 834-9102

Renee Fair 	Meteorologist-In-Charge		(501) 834-9102

(24 hours)

b.	SITE DESCRIPTION AND OPERATIONS

This section describes the site and its operations.

- Facility Location, Layout, and Operations

The facility is located in Pulaski County, Arkansas, just northwest of the North Little Rock Municipal Airport (Figure 1).  Figure 2 shows the layout of the facility, including the location of a 1,000-gallon aboveground storage tank (AST) and a 19-gallon aboveground day tank.  The fuel in the AST is pumped to the 19-gallon aboveground day tank, which is connected to a emergency backup power (electric) generator.  The day tank and generator are located in the enclosed generator building.

The estimated fuel usage is approximately 360 gallons per month.  This estimate is based on an average of the fuel purchased during the last 8 months of operation.  Fuel consumption increases based on the frequency and duration of any power outages.

- Facility Storage

The single-walled, welded steel plate AST is cylindrical in shape and horizontally situated.  The AST is located in an open-top steel rectangular secondary containment bin. The secondary containment bin is equipped with a drain valve and has a total containment capacity of 1,300 gallons.  This bin, when properly operated, should contain any overfills during refueling and, therefore, an automatic shut-off valve is not required.

The AST is connected to a pump on top of the day tank via a single supply line.  The supply line is constructed of steel pipe and is equipped with a shut-off valve and backflow preventer.  The supply line is not equipped with any type of secondary containment system.  This pump moves fuel from the AST into the day tank.  The day tank is a single-walled rectangular steel tank set in an open top spill pan (rupture basin).  The day tank is connected to the generator by flexible rubber supply and return lines.  Table 1 summarizes the pertinent information on the tanks at the facility.

- Drainage Pathway and Distance to Navigable Waters

Any fuel oil spilled from the AST or the day tank would flow northeast to the airport parking area (Figure 2).  Drainage from the airport parking area flows north to an unnamed tributary of the Arkansas River.

- Spill History

Reportable Spill events from 1974 to the date on the cover of this plan:

None

- Spill Potential, Volumes, and Rates

The most probable causes of spills from the AST are from either overfilling, a ruptured hose during fuel unloading, or from failure of the fuel supply line to the day tank.  For the AST, spills caused by loss of structural integrity, vehicle collisions, or earthquakes are low-probability events.  The probable causes of spills for the day tank are from a failure of the pump to shut down or failure of the line from the pump to the day tank.

Table 2 summarizes the potential type of failure, potential spill volume, estimated rate, and direction of spill flow from the tanks.

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL

This section discusses spill prevention and control measures that shall be implemented at the facility.

- SPILL PREVENTION

This section describes design components and operating procedures that shall be implemented at the facility to prevent oil spills.

- Bulk Storage Tanks and Facility Transfer Operations

AST:  The AST construction shall be compatible with the diesel fuel held by the AST.  The AST shall be located in a secondary containment bin with a capacity to store at least 110 percent of the volume of the AST.

The AST shall not be filled to more than 90 percent of capacity.  The filling of the AST shall be monitored full time by the fuel supply contractor and a NWS representative.

Day Tank:  This tank shall have an open top spill pan (rupture basin) designed to hold 110 percent of the tank volume.  It shall have a liquid level gauge to indicate the amount of fuel in the tank (empty to full) and a high-level float switch connected to the audible alarm to warn of overfilling.  The rupture basin shall have a float switch designed to detect fuel that has spilled or leaked.  The float switch shall be connected to the audible alarm system.

Piping:  The portion of piping located underground shall be wrapped or coated to prevent corrosion.  An antisiphoning valve shall be located between the AST and the pump to prevent unwanted fuel from being siphoned from the AST.

- Tanker Truck Unloading Operations

All delivery drivers shall have U.S. Department of Transportation hazardous material transportation training as required by Federal law.

The remainder of this section discusses the procedures that shall be used during unloading of fuel from the tanker truck into the AST to prevent spills.  This procedure shall be documented every time refueling occurs using the form found in Appendix A.  Copies of this form shall be kept for 3 years.

The following procedure shall be used before fuel unloading:

- Ensure that the high-level alarm system is functioning properly.

- A NWS representative should determine the available capacity (ullage) of the AST by measuring the depth of the fuel in the AST and converting the reading to gallons (See Appendix A).  This ullage is communicated to the fuel supply contractor and marked in the fueling log.

- Move spill containment equipment such as booms or spill barriers into the unloading area.

- Block the tanker truck wheels.

- Place drip pans under all pump hose fittings (if applicable) before unloading.

- The NWS representative and the delivery driver ensure the fill nozzle is placed in the appropriate AST appurtenance.

Both the NWS representative and the delivery driver shall remain with the vehicle at all times during unloading.  Gauges on the truck shall be continuously monitored to ensure the ullage is not exceeded.

The following procedure shall be used after fuel unloading is completed:

- Record the amount of fuel transferred to the AST in the log (Appendix A).

- Drain the fill hose and then ensure that all drain valves are closed (if applicable) before removal of the hose from the AST.

- Pour any fuel in the drip pans, tanker truck containment pool, or secondary containment bin into the AST (if it has the capacity) or dispose of appropriately.

- Inspect the tanker truck before removing the blocks to ensure the lines have been disconnected from the AST.

- Remove the blocks from truck wheels.

- Place a copy of the fuel-unloading checklist in the SPCC plan.

3.	Inspections and Records

Inspection and Maintenance of Tanks:  The AST and generator day tank shall be inspected weekly for any oil outside the tank, especially at seams (including the underside).  The outside of exposed piping shall also be inspected weekly, especially at the joints such as gasketed fittings.  Monthly and annual inspections shall follow the checklists shown in Appendix B.

Record Keeping:  The Environmental/Safety Focal Point (person responsible for spill prevention at the facility) shall be responsible for completing the ullage logs and documentation of fuel unloading procedures.  These records as well as records of all inspections shall be maintained for at least 3 years from the time of inspection.

4.	Site Security

The AST shall have adequate lighting to detect spills at night and a security fence with a locked gate to prevent tank damage or spills caused by vandalism.  The generator building shall be kept locked.  Signage around the AST shall warn of the presence of a combustible liquid, that the combustible liquid is diesel fuel, and that smoking is not permitted near the AST.  A fire extinguisher shall be located in the adjacent generator enclosure.  The AST is not located in the direct line of parking lot traffic; therefore, no guard posts are required.

5.	Training

The Environmental/Safety Focal Point and an alternate shall be trained in the intent of applicable oil spill regulations and methods for implementing the inspection and maintenance procedures outlined in the previous paragraph.  Spill control and countermeasure shall also be included in the training.  An outline for the training is found in Appendix C.

Training shall be repeated once per year.  All new personnel responsible for implementing this SPCC plan shall be properly trained before beginning the new position.  A record of who was trained, when, and by whom, shall be filed with this SPCC plan and kept for a period of 3 years.

B.	sPILL CONTROL

This section describes control measures that shall be implemented to prevent any spilled oil from entering navigable waters or adjoining shorelines.

- Secondary Containment Designs, Construction Material, and Volume

The secondary containment structures for the AST and the generator day tank shall be sized to contain a minimum of 110 percent of the tank volumes.  The AST secondary containment shall have a drain valve that is normally closed for the drainage of storm water from the containment area.  The day tank rupture basin shall have a float switch designed to detect fuel that has spilled or leaked.  The float switch shall be connected to the audible alarm system.

- Spill Kits Type and Location

The facility shall have spill kits designed absorb diesel fuel and to divert a spill from navigable waters.  These items shall be stored in the generator shed or nearby.  The kit shall include oil absorbent socks and mats in a polyethylene container that doubles as a disposal container.  In addition, urethane spill barriers that can divert or contain a relatively small spill and prevent it from reaching navigable waters should be included with the spill kit.

PART III - SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is prevention.  The spill countermeasures presented do not constitute a contingency plan detailed in Title 40 of the Code of Federal Regulations (40 CFR) Part 109, nor is one required.  Such a plan is only required under 40 CFR Part 112.7(d) if it is impracticable to provide containment, diversionary structures, or equipment to prevent the discharge of oil to navigable waters.  In addition, this facility is not required to have a facility response plan under 40 CFR Part 112.20 since at least one of the following statements is true:

- The facility does not transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons

- The facility does not have a total storage capacity over 1 million gallons.

Should a spill occur, the following measures would be implemented:

- SPILL COUNTERMEASURES

This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.

A spill containment and cleanup activity will never take precedence over the safety of personnel. No countermeasure activities will be undertaken until conditions are safe for workers.  The following general procedures should be implemented as countermeasures:

- Account for all personnel and ensure their safety.

- Eliminate all ignition sources in the immediate area.

- Attempt to divert flow from leaving the facility with a spill barrier or the contents of spill kit.

- Attempt to seal or somehow stop leak if it can be done safely.

- Notify contacts and emergency response contractor as described in the following section for assistance in control and cleanup.

B.		SPILL REPORTING

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The people and organizations notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

A spill reporting form that requests the information to be reported to all agencies (to the extent known) is included in Appendix D.  Copies of the completed form should be sent to the NWS Environmental Compliance Officer and the National Oceanic and Atmospheric Administration (NOAA) Southern Regional Compliance Officer (see following section).

- General Notification Procedures For All Spills

The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

- First, call 9-1-1 (or the local emergency agency) if there is an immediate emergency

- Next, notify the appropriate persons within the NWS:

- Mike Jacob, (301) 713-1838 Ext. 165, NWS Environmental Compliance Officer.

- Olga Kebis, (301) 713-1838 Ext. 173, NWS Safety Officer

- Terry Brisbin, (817) 978-2367 Ext. 139, NWS Southern Regional Environmental/Safety Coordinator

- Sherilyn Villegas, (816) 426-3925 Ext. 263, NOAA Central Regional Compliance Officer

2.	Federal Notifications

The Federal Clean Water Act, as described in 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  40 CFR Part 110.3 defines “may be harmful” as a discharge for which one of the following applies:

- Violates applicable water quality standards

- Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or cause a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines

If either of these criteria is met, contact the following:

- The National Response Center (EPA and USCG):  (800) 424-8802.

Under the SPCC regulations, spill information listed in 40 CFR Part 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

- A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shorelines in a single event

- Two spill events that cause visible sheens upon navigable waters or adjoining shorelines within any 12-month period

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act; therefore, no other notification to the EPA is required for discharges of diesel fuel other than those listed previously.

3.	State Notification

As required by the Arkansas Pollution Control and Ecology Commission any spill of refined petroleum product (gasoline, diesel, oil, etc.) be reported to the Arkansas Department of Emergency Management at (800) 322-4012.

4.	Cleanup Contractor Notification

An emergency response contractor should also be notified to assist with the cleanup if necessary.  NWS has identified the following contractors that are available for an emergency response:

- {To be provided by facility}

PART IV - RECOMMENDED IMPROVEMENTS

In accordance with 40 CFR Part 112.7, this section presents physical upgrades or procedural changes not yet fully operational but called for in the plan.

- PHYSICAL UPGRADES

- Tanks

An audible high-level alarm shall be installed set to sound at 90 percent capacity (900 gallons) to help prevent overfills.

- Secondary Containment Bin Valve

The valve used to drain rainwater from the concrete secondary containment bin shall be sealed in the closed position at all times except to release clean rain water.  Once the rain water is released, the valve should be closed again.

B.	PROCEDURAL CHANGES

- Inspections and Preventative Maintenance

The inspection checklists in Appendix B should be followed.  This requirement is found in 40 CFR Part 112.7(e)(8).  Visual inspections of the outside of the AST and the day tank should serve to signal a potential problem with their integrity.

- Training

The Environmental/Safety Focal Point and an alternate should be trained in the intent of the applicable oil spill regulations and methods for implementing the inspection and maintenance procedures outlined in the previous section.  Spill control and countermeasures should also be included in the training.  The alternate should be designated in case the primary person is off site at the time of a spill.  A recommended outline for the training is found in Appendix C.

Training should be repeated once per year.  All new personnel responsible for implementing the SPCC plan should be properly trained before beginning the new positions.  A record of who was trained, when, and by whom should be filed with the SPCC plan and kept for a period of 3 years.  This requirement is found in 40 CFR Part 112.7(e)(10).

Figure 1 Site Location

Figure 2 Site Layout

TABLE 1

DESCRIPTIVE INVENTORY OF FACILITY STORAGE

| Tank | Nominal Capacity (Gallons) | Product Stored | Type | Double Walled? |
| --- | --- | --- | --- | --- |
| Aboveground Storage Tank | 1,000 | Diesel fuel number 2 | AST | Noa |
| Generator Day Tank | 19 | Diesel fuel number 2 | AST | Noa |
| Total Capacity | 1,019 |  |  |  |

Notes:	AST	Aboveground storage tank

a	Tank is in a secondary containment bin that contains at least 110 percent of its volume.

13

October 13, 2000

North Little Rock, Arkansas

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| Aboveground Storage Tank | Overfilling or a ruptured hose during fueling | 0 to 40a | 80b | Northeast | None |
|  | Failure of fuel supply line to pump | 0 to 1,000 | Variable depending on size of hole | Northeast | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | 0 to 1,000 | Variable depending on size of hole | Northeast | Low-probability event that both AST and secondary containment bin would fail. |
|  | Vehicle collision | 0 to 1,000 | Variable depending on size of hole | Northeast | Low-probability event. Vehicle traffic is limited, and traffic flow is not directly towards tanks. |
|  | Overturn or puncture in an earthquake | 0 to 1,000 | Variable depending on size of hole | Northeast | Low-probability event. Secondary containment bin tank gives extra protection from rupture, but a large earthquake could cause a spill. |
| Generator Day Tank | Failure of the pump to shut down after filling day tank or failure of the line from pump to day tank. | 0 to 1,000 | Variable depending on size of hole | Northeast | Can be minimized through routine inspections. |
|  | Failure of fuel return line | >0 | 10c | Northeast | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | 0 to 19 | Variable depending on size of hole | Northeast | Low-probability event can be minimized through regular inspections and maintenance. |
|  | Vehicle collision | 0 to 19 | Variable depending on size of hole | Northeast | Low-probability event. Vehicle traffic is limited, and traffic flow is not directly towards tanks. |
|  | Overturn or puncture in an earthquake | 0 to 19 | Variable depending on size of hole | Northeast | Low-probability event. |

Notes:

a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

c	Estimated return line flow rate.

APPENDIX A

Tank Ullage/Fueling Log ANd Fuel UNLOADING PROCEDURE CHECKLIST

(2 Pages)

APPENDIX A-1

Tank Ullage anD Fueling Log

A-1

North Little Rock, Arkansas

Tank Capacity 	 gallons

October 13, 2000

| Date | Initials | Gauge Reading | Initial Volume of Fuel in Tank a (Gallons) | Available Capacity or Ullage b (Gallons) | Quantity Added (Gallons) | Comments |
| --- | --- | --- | --- | --- | --- | --- |

Note:

a	From gauge reading

b	Available capacity (ullage) = tank capacity – initial volume of fuel in tank

APPENDIX A-2

FUEL UNLOADING PrOCEDURE CHECKLIST

North Little Rock, Arkansas

A-2

Date:										Tank:

NWS Representative:								Supplier

October 13, 2000

| ( | ITEM | DESCRIPTION | COMMENT |
| --- | --- | --- | --- |
| The following six items must be completed before fuel unloading: |
|  | 1 | Ensure the audible high-level alarm system is functioning properly. |  |
|  | 2 | Determine the available capacity (ullage) of the aboveground storage tank (AST) by converting the reading on the fuel gauge to gallons (See Appendix A, Page A-1). This ullage should then be marked in the fueling log and communicated to the tank truck unloading contractor. |  |
|  | 3 | Move spill containment equipment such as booms or spill barriers into the unloading area. |  |
|  | 4 | Block the wheels of the tank truck. |  |
|  | 5 | Place drip pans under all pump hose fittings (if applicable) after the hose is hooked up to the AST and before unloading. |  |
|  | 6 | Ensure the fill nozzle is placed in the appropriate AST appurtenance. In this case, the fill nozzle is placed in the fill pipe connected to the round spill container. |  |
| During unloading: |
|  | 7 | Ensure that the NWS representative and the tank truck operator remain with the vehicle at all times during unloading. |  |
|  | 8 | Monitor the gauges on the AST and the truck continuously to ensure the ullage is not exceeded. If the audible high-level alarm sounds, stop the unloading of fuel as soon as possible. |  |
| The following six items must be completed after the fuel unloading has been completed: |
|  | 9 | Record the amount of fuel unloaded in the log (Appendix A, page A-1). |  |
|  | 10 | Before removing the fill hose from the AST, ensure that it is drained and that all drain valves are closed (if applicable). |  |
|  | 11 | Pour any fuel in the drip pans or spill container on the fill pipe into the AST (if it has the capacity) or dispose of appropriately (describe how it was disposed of, if applicable). |  |
|  | 12 | Inspect the tank truck before removing the blocks to ensure the lines have been disconnected from the AST. |  |
|  | 13 | Remove the blocks from tank truck wheels. |  |
|  | 14 | Place a copy of this fuel-unloading checklist in the SPCC plan. |  |

APPENDIX B

INSPECTION CHECKLISTS

(3 Pages)

APPENDIX B

INSPECTION FORMS

B-1

October 13, 2000

North Little Rock, Arkansas

| MONTHLY INSPECTION CHECKLIST (Page 1 of 2) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| A. TANKS | YES | NO | NOTES |
| 1. Are there any oil stains on the outside of the tank, including the underside? |  |  |  |
| 2. Is there any oil on the ground, concrete, or asphalt around the tank? |  |  |  |
| 3. Are there any visible cracks or indications of corrosion on the tank, at fittings, joints, or seals? (such as paint peeling or rust spots) |  |  |  |
| 4. Are there any raised spots, dents, or cracks on the tank? |  |  |  |
| 5. Does it appear that the foundation has shifted or settled? |  |  |  |
| 6. Is the fuel gauge working properly? |  |  |  |
| 7. Are all vents clear so they may properly operate? |  |  |  |
| 8. If rainwater is present in secondary containment area, does sufficient volume remain for spill control? (if applicable) |  |  |  |
| MONTHLY INSPECTION CHECKLIST (Page 2 of 2) |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| B. PIPING | YES | NO | NOTES |
| 1. Is there any oil on the outside of or under any aboveground piping, hoses, fittings, or valves? |  |  |  |
| 2. Are aboveground piping, hoses, fittings, or valves in good working condition? |  |  |  |
| C. SECURITY/SAFETY/SPILL COUNTERMEASURES |  |  |  |
| 1. Are lights working properly to detect a spill at night? |  |  |  |
| 2. Are all locks in the “lock” position? |  |  |  |
| 3. Are all warning signs properly posted and readable? |  |  |  |
| 4. Are vehicle guard posts in place and properly secured? (If applicable) |  |  |  |
| 5. Are spill kits easily accessible, protected from the weather, and complete? |  |  |  |
| Corrective Actions Required: |

B-2

October 13, 2000

North Little Rock, Arkansas

| ANNUAL INSPECTION CHECKLIST (Page 1 of 1) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
|  | YES | NO | NOTES |
| A. MONTHLY CHECKLIST |  |  |  |
| 1. Has monthly inspection checklist been completed? |  |  |  |
| B. TANKS |  |  |  |
| 1. Are all alarms and automatic shutoff devices working properly? |  |  |  |
| C. OTHER |  |  |  |
| 1. |  |  |  |
| 2. |  |  |  |
| Corrective Actions Required: |  |  |  |

B-3

October 13, 2000

North Little Rock, Arkansas

APPENDIX C

TRAINING OUTLINE AND COPY OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS PARTS 112.1 THROUGH 112.20, Oil Pollution Prevention

(15 Pages)

APPENDIX C

OUTLINE FOR SPILL PREVENTION, CONTROL, AND COUNTERMEASURE TRAINING

Training will be provided for facility personnel at the following times:

- System start up or whenever new equipment is installed

- Within the first week of employment for new personnel

- Annually

The training will include complete instruction in the elements of the facility’s Spill Prevention, Control, and Countermeasure plan and will include the following:

- Pollution control laws, rules, and regulations including a summary of Title 40 of the Code of Federal Regulations Part 112 "Oil Pollution Prevention" (see Attachment).

B.	Fuel Storage System

1.	Purpose and application of the following system elements:

a.	Tanks

b.	Piping

c.	Pumps

d.	Accessory equipment

- Electronic monitors

- Operation, maintenance, and inspection of system elements

C.	Spill Prevention

  - Potential spill sources

  - Spill flow direction and impact on navigable waters

  - Procedures to prevent spills, especially during fuel unloading

D.	Spill Control

- Secondary containment

- Safety valves

- Pump and equipment shutoff switches

- Use of catch basin inlet covers or other diversionary devices

E.	Spill Countermeasures

1.		Location and use of emergency phone numbers

2.	Location and use of fire extinguishers

3	Location and use of spill cleanup kit

4.	Stopping the leak

ATTACHMENT

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS Section 112.1 - 112.20

Oil Pollution Prevention

APPENDIX D

SPILL REPORTING FORM

(1 Page)

APPENDIX D

SPILL REPORTING FORM

| 1. GENERAL |
| --- |
| Name of Facility: National Weather Forecast Office | Address: 8400 Remount Road North Little Rock, Arkansas 72118 |
| Completed By: | Organization: National Weather Service |
| Position: | Phone: |
| 2. SPILL INFORMATION |
| Date: | Time: |
| Location at Facility: | Quantity: |
| Substance Spilled: Diesel Fuel | Other: |
| 3. OUTSIDE NOTIFICATIONS: |
| Agencies | Recorder at Outside Agency | Date and Time |
| Call 9-1-1 (or the local emergency agency), if there is an immediate emergency |  |  |
| NWS/NOAA: Mike Jacob, (301) 713-1838 Ext. 165 Olga Kebis, (301) 713-1838 Ext. 173 Terry Brisbin, (817) 978-2644 Ext. 139 Sherilyn Villegas, (816) 426-3925 Ext. 263 |  |  |
| EPA National Response Center or U.S. Coast Guard : ( 800) 424-8802 |  |  |
| Arkansas Department of Emergency Management (800) 322-4012 |  |  |
| 5. INFORMATION ON SOURCE AND CAUSE |
| 6. DESCRIPTION OF ENVIRONMENTAL DAMAGE |
| 7. CLEANUP ACTION(S) TAKEN |
| 8. CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |

Note: 	All information must be filled in.  If something is unknown, write “unknown”.

Copies must be sent to the NWS/NOAA personnel listed above.

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS of TITLE 40 OF THE 
CODE OF FEDERAL REGULATIONS part 112.7 WITH THIS DOCUMENT

(1 Page)

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF 40 CFR 112.7 AND THIS PLAN

| CFR Citation | Item | Plan Location |
| --- | --- | --- |
| 112.7 (a) | Spill History | Part I.B.4 |
| 112.7 (b) | Potential Spill Prediction, Volumes, and Rates | Part I.B.5 and Table 2 |
| 112.7 (c) | Containment and Diversionary Structures | Part I.B.2 and Part II.B.1 |
| 112.7 (d) | Secondary Containment Impractability | Not Applicable |
| 112.7 (e)(1) | Drainage Control | Part I.B.3 |
| 112.7 (e)(2) | Bulk Storage Tanks and Secondary Containment. |  |
| 112.7 (e)(2)(i) | Tank compatibility with its contents | Part II.A.1 |
| 112.7 (e)(2)(ii) | Diked area construction and containment for storage tanks | Part IV.B.3 |
| 112.7 (e)(2)(iii) | Diked area inspection and drainage of rainwater | Part IV.B.3 and Appendix F |
| 112.7 (e)(2)(iv) | Corrosion protection of buried metallic storage tanks | Not Applicable |
| 112.7 (e)(2)(v) | Corrosion protection of partially buried metallic tanks | Not Applicable |
| 112.7 (e)(2)(vi) | Aboveground tank periodic integrity testing | Part II.A.3 |
| 112.7 (e)(2)(vii) | Control of leakage through internal heating coils | Not Applicable |
| 112.7 (e)(2)(viii) | Tank installation fail-safe engineered | Part II.A.1, B.1 |
| 112.7 (e)(2)(ix) | Observation of disposal facilities for effluent discharge | Not Applicable |
| 112.7 (e)(2)(x) | Visible oil leak corrections from tank seams and gaskets | Part II.A.3 and Appendix B Inspections |
| 112.7 (e)(2)(xi) | Appropriate position of mobile or portable tanks | Not Applicable |
| 112.7 (e)(3) | Facility Transfer Operations |  |
| 112.7 (e)(3)(i) | Buried piping installation protection and examination | Not Applicable |
| 112.7 (e)(3)(ii) | Not in-service and standby terminal connections | Not Applicable |
| 112.7 (e)(3)(iii) | Pipe support designs | Not Applicable |
| 112.7 (e)(3)(iv) | Aboveground valve and pipeline examination | Part II.A.3 and Appendix B |
| 112.7 (e)(3)(v) | Aboveground piping protection from vehicular traffic | Part II.A.4 |
| 112.7 (e)(4) | Facility Truck Unloading Operations | Part II.A.2 |
| 112.7 (e)(5)-(7) | Oil Production Facilities (onshore) and Oil Drilling, Production, or Workover Facilities (on shore and offshore) | Not Applicable |
| 112.7 (e)(8) | Inspections And Record Keeping | Part II.A.3 |
| 112.7 (e)(9) | Security |  |
| 112.7 (e)(9)(i) | Fencing | Part II.A.4 |
| 112.7 (e)(9)(ii) | Flow valves locked | Not Applicable |
| 112.7 (e)(9)(iii) | Starter controls locked | Not Applicable |
| 112.7 (e)(9)(iv) | Pipeline loading and unloading connections securely capped | Not Applicable |
| 112.7 (e)(9)(v) | Lighting adequate to detect spills | Part II.A.4 |
| 112.7 (e)(10) | Training |  |
| 112.7 (e)(10)(i) | Personnel instructions | Part II.A.5 |
| 112.7 (e)(10)(ii) | Designated person responsible for spill prevention | Page i |
| 112.7 (e)(10)(iii) | Spill prevention briefings | Part II.A.5 |

Note:	CFR	Code of Federal Regulations