SPILL  PREVENTION,  CONTROL,  AND  COUNTERMEASURES

BEST  MANAGEMENT  PLAN

N O A A

NATIONAL WEATHER SERVICE

Eastern Weather Forecast Office

1200 Airport Drive

Burlington International Airport

South Burlington, Vermont  05403

Designated Person Responsible for Spill Prevention (DRO):

Printed Name:			John Ferguson

Signature:

Date:

Telephone:			(802) 862-8711

The Regional Environmental Compliance Officer (RECO)  has reviewed the facility and determined that an SPCC Plan is not required per 40 CFR 112.  This Plan is developed strictly as a Best Management Plan.  The determination is based on:

The facility does not exceed capacity.

X   	The facility meets capacity requirements but, a discharge will not reach navigable waterways.

RECO Printed Name:		Lynnette Ansell

RECO Signature:

Date:

PART I - GENERAL INFORMATION

A.	GENERAL

This section of the Best Management Plan provides general information about the facility.

  - Name:

National Weather Service (NWS) Eastern Weather Forecast Office (WFO)

  - Date of Initial Operation:

1996

  - Location:

Street: 			Airport Corporate Center, 1200 Airport Drive

Burlington International Airport

City: 			South Burlington

State/Zip Code: 	Vermont 05403

4.	Name and phone number of owner (Point of Contact)

John Ferguson, Environmental Focal Point (802) 862-8711

5. 	Facility Contacts

Name             		Title/Role    				Telephone Number

John Ferguson		Environmental Focal Point		(802) 862-8711

B. 	SITE DESCRIPTION AND OPERATIONS

The facility is located in South Burlington, Vermont, and within the Burlington International Airport terminal.  A 1,000-gallon aboveground storage tank (AST) contains a mixture of diesel fuel (60 percent) and kerosene (40 percent).  The fuel mixture is used to power an adjacent 175-kilowatt emergency backup power (electric) generator.  The emergency generator and a 75-gallon day tank are located within an enclosed steel building.  Both the AST and the generator building rest on a concrete slab foundation.  The fuel in the AST is pumped as needed to a day tank inside the building that feeds the generator.

The emergency generator is operated approximately 4 to 5 hours per month and is typically used during weather-related power outages.  The generator also is operated once per week for maintenance purposes.  Approximately 18 gallons per month of fuel are used on average.

Appendix A includes a Tank Ullage and Fueling Log (Appendix A-1) that should be used when fuel is delivered and a Fuel Unloading Procedure Checklist (Appendix A-2) that includes a list of procedures that should be implemented when fuel is delivered.

Drainage from the area of the AST flows to the north and along a small drainage ditch to a sewer inlet within a grassy area.  This inlet and other nearby inlets - in the adjacent parking area to the west and airport runways to the east - direct flows to the South Burlington Wastewater Treatment Plant.

The facility maintains a spill kit in the generator building that includes absorbent pads and socks that can be used to divert a small spill.  The kit also includes a small container that can be used as a disposal container.

PART II - SPILL COUNTERMEASURES AND REPORTING

- SPILL COUNTERMEASURES

This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasures will be undertaken until conditions are safe for workers.  The SWIMS procedure should be implemented as countermeasures as follows:

S   -	Stop the leak and eliminate ignition sources.

a. 	Attempt to seal or some how stop leak if it can be done safely.

b. 	Attempt to divert flow away from the drainage ditch with a spill barrier or the contents of spill kit. The spill kit is located in the generator building.

c. 	Eliminate all ignition sources in the immediate area.

W  -	Warn others.

a.  	Yell out “SPILL.”  Inform the person in-charge at your facility.

b. 	Account for all personnel and ensure their safety.

c. 	Notify contacts and emergency response contractor as described in the following section for assistance in control and cleanup.

I    -	Isolate the area.

a. 	Rope off the area.

M  -	Minimize your exposure.  Stay upwind.

S    -	Stand by to assist the emergency response contractor, if necessary.

B. 	SPILL REPORTING

1.  General Notification Procedures for All Spills

Within 24 hours, the responsible person or designee (DRO on this plan title page) is directly charged with reporting all oil spills that result from facility operations as follows

    - In the event of an emergency (for example, fire or injury), call 9-1-1 (if “9" is required to obtain an outside telephone line, it may be necessary to dial 9-9-1-1).

b.	Notify the appropriate persons within your region and line office.

National Weather Service:

Mike Jacob, NWS Environmental Compliance Officer

Phone number: (301) 713-1838 Ext. 165, Jmichael.Jacob@NOAA.GOV

Olga Kebis, NWS Safety Officer

Phone number: (301) 713-1838 Ext. 173, Olga.Kebis@NOAA.GOV

Kevin Murray, NWS Eastern Regional Environmental/Safety Coordinator

Phone number: (631) 244-0146, Kevin.Murray@NOAA.GOV

c.	Notify the appropriate Regional Environmental Compliance Officer (RECO) at the NOAA Environmental Compliance and Safety Office Program.

Lynnette Ansell, Eastern Regional Environmental Compliance Officer

Phone number: (757) 441-6298, Lynnette.J.Ansell@NOAA.GOV

- RECO must determine if Federal or State notification is required and follow up accordingly.

2.  Cleanup Contractor Notification

An emergency response contractor should also be notified to assist with the clean up, if necessary.  NWS has identified and contacted the following contractors that are available for an emergency response:

Contractor					Phone Number

Environmental Products and Services, Inc.	(802) 862-1212

Flynn Avenue, Burlington, VT

3.  Spill Report

The form in Appendix B should be used to complete a spill report.  This form should be sent, preferably by e-mail, to the NOAA representatives listed above.

C.  Training

The Environmental Focal Point and an alternate should be trained in spill countermeasures.  The alternate should be designated in case the primary person is off site at the time of a spill.

# Comments

Bottom of Form