SPECIAL SPECIFICATION

SECTION 02201

EARTHWORK

Page

PART 1 - GENERAL

1.01  	Description Of Work	2

1.02  	Quality Assurance	2

1.03  	Job Conditions	3

1.04  	Soil Investigation Report	3

1.05  	Digging Permit	4

PART 2 - PRODUCTS

2.01  	Soils Materials	4

2.02 	Miscellaneous Materials	6

PART 3 - EXECUTION

3.01  	Excavation	6

3.02  	Compaction	9

3.03  	Backfill And Fill	11

3.04  	Grading	12

3.05  	Building Slab Drainage Course	13

3.06  	Maintenance	14

3.07  	Disposal Of Excess And Waste Materials	14

SPECIAL SPECIFICATION

SECTION 02201

EARTHWORK

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

A.	Earthwork includes, but is not limited to, clearing, grading, excavating, filling, backfilling and compacting of soils as necessary to accomplish finished construction as indicated on the drawings.

B.	Excavation for Mechanical/Electrical Work.  Excavation and backfill required in conjunction with underground mechanical and electrical utilities, and buried mechanical and electrical appurtenances is included as work of this section.

1.02	QUALITY ASSURANCE

A.	Testing and Inspection Service

Sandia will engage a soil testing and inspection service, for quality control testing during earthwork operations.  Should initial tests indicate noncompliance with this specification, the Contractor shall make corrections as directed.  All subsequent testing required to determine compliance with this specification shall be performed by an approved testing laboratory at the Contractor's expense.

1.03	JOB CONDITIONS

A.	Existing Utilities.  Locate existing underground utilities in areas of work.  If utilities are to remain in place, provide adequate means of support and protection during earthwork operations.

Should uncharted, or incorrectly charted, piping or other utilities be encountered during excavation, report it in writing to the Sandia Contracting Representative (SCR).

Do not interrupt existing utilities without following the standard Plant Engineering procedures for utility outages.  Provide a minimum of two weeks' notice to the Sandia Delegated Representative (SDR) and await notice to proceed before interrupting any utility.

B.	Use of Explosives.  The use of explosives is not permitted.

C.	Protection of Persons and Property.  Barricade open excavations occurring as part of this work and post with warning lights.  Protect structures, utilities, sidewalks, pavements, and other facilities from damages caused by settlement, lateral movement, undermining, washout, and other hazards created by earthwork operations.

D.	Street Crossings.  Excavations shall be conducted in a manner to cause the least interruption to traffic.  Steel plates (1/2" x 4' x 10') will be supplied by Sandia upon request to place over an open trench for a traffic crossing. Maintain half the width of the street open at all times unless prior approval from the SCR has been given to close the street.  Requests to close a street must be presented in writing to the SCR at least two weeks prior to the requested closing date.

1.04	SOIL INVESTIGATION REPORT

A.	To assist the Contractor, copies of the Soil Investigation Report and all amendments will be provided with the specifications.

1.05	DIGGING PERMIT

A.	Before any ground excavation takes place, the Contractor shall have obtained a "Digging Permit" from Sandia.  Contractor shall contact the Sandia Delegated Representative for permit procedures.

PART 2 - PRODUCTS

2.01	SOILS MATERIALS

A.	General.  Unless otherwise noted on the contract documents, the existing site soils shall be used for fill and backfill materials.  If the on-site soils are found by laboratory test to be unsuitable for fill and backfill material, this will constitute a differing site condition and will be handled in accordance with the differing site conditions provisions given in Section II of the contract. Any additional fill material used must conform with paragraph 2.01B.

B.	Structural Fill

1.	General.  Structural fill shall consist of a controlled fill constructed in areas indicated on the drawings.

2.	Materials.  Structural fill material shall consist of soils that conform to the following physical characteristics:

Sieve Size				Percent Passing

(Square Openings)			   by Weight

6 inch					    100

No. 4					50-100

No. 200					10-35

The plasticity index of the material, as determined in accordance with ASTM D 423 and D 424, shall not exceed 15.

The fill material shall be free from roots, grass, other vegetable matter, clay lumps, rocks larger than 6", or other deleterious materials

C.	Retaining Wall Backfill

1.	Retaining wall backfill material shall be free-draining and conform to fill quality requirements as follows:

Sieve Size				Percent Passing

(Square Openings)			 by Dry Weight

3/4 inch					   100

No. 4					30-80

No. 200					 0-5

2.	The material should have a plasticity index of less than 5 when tested in accordance with ASTM D 423 and D 424.

D.	Granular Base

1.	Granular base shall meet the following grading requirements as determined in accordance with ASTM C 136.

Sieve Size				Percent Passing

(Square Openings)			 by Dry Weight

1 inch					    100

3/4 inch					80-100

No. 4					30-60

No. 200					 3-10

2.	The granular base shall have a plasticity index of no greater than 3 when tested in accordance with ASTM D 423 and D424.  The coarse aggregate shall have a percent of wear, when subject to the Los Angeles abrasion test (ASTM C 131), or no greater than 50.

2.02	MISCELLANEOUS MATERIALS

A.	Utility Identification Tape.  Polyethylene plastic sheet, nominally 6" wide, in bright contrasting colors with 1"-minimum black lettering as indicated.

1.	Color Codes:

Electric		- Yellow

Gas			- Orange

Water		- Blue

Steam		- Yellow

Sewer		- Red

Telephone	- Green

2.	Text:  The lettering shall be repeated continuously for the full length of the tape as follows see standard specification.

B.	Shoring.  Sheet Piling or Bracing as required to protect embankments, paving, structures, or utilities.

PART 3 - EXECUTION

3.01	EXCAVATION

A.	Unauthorized excavation consists of removal of materials beyond indicated sub-grade elevations or dimensions without specific direction of the SCR. Unauthorized excavation, as well as remedial work directed by the SCR, shall be Contractor's expense.

1.	Under footings, foundation bases, or retaining walls, fill unauthorized excavation by extending indicated bottom elevation of footing or base to excavation bottom, without altering required top elevation.  Concrete fill (2000 psi min.) may be used to bring elevations to proper position, when acceptable to the SCR.

2.	Elsewhere, backfill and compact authorized excavations as specified for authorized excavations of same classifications, unless otherwise directed by the SCR.

B.	Additional Excavation.  When excavation has reached required sub-grade elevations, notify the SDR who will make an inspection of conditions.

1.	If unsuitable bearing materials are encountered at required sub-grade elevations, the situation will be considered and handled in accordance with the differing site conditions provisions given in Section II of the contract.

2.	Removal of unsuitable material and its replacement as directed will be paid on basis of contract conditions relative to changes in work.

C.	Stability of Excavation.  Slope sides of excavations where possible.  Shore and brace where sloping is not possible because of space restrictions or stability of material excavated.  Maintain sides and slopes of excavations in safe condition until completion of backfilling.

1.	Shore all vertical cuts greater than five (5) feet in depth.

2.	Shore all trenches across streets that continue to carry traffic over steel plates.

D.	Dewatering.  Prevent surface water and subsurface or ground water from flowing into excavations and from flooding project site and surrounding area. Remove water to prevent softening of foundation bottoms, undercutting footings, and soil changes detrimental to stability of sub-grades and foundations.

E.	Material Storage.  Stockpile satisfactory excavated materials where directed, until required for backfill or fill.  Place, grade, and shape stockpiles for proper drainage.  Locate and retain soil materials a minimum of 2 feet away from edge of excavations.  Dispose of excess soil material and waste materials as herein specified.

F.	Excavation of Structures

1.	Conform to elevations and dimensions shown within a tolerance of plus or minus 0.10', and extending a sufficient distance from footings and foundations to permit placing and removal of concrete formwork, installation of service, other construction, and for inspection.

2.	In excavating for footings and foundations, take care not to disturb bottom of excavation.  Excavate by hand to final grade just before concrete reinforcement is placed.  Trim bottoms to required lines and grades to leave solid base to receive other work.

G.	Excavation for Pavements.  Cut surface under pavements to comply with cross-sections, elevations and grades as shown.

H.	Excavation for Trenches

1.	Dig trenches to the uniform width required for particular item to be installed, sufficiently wide to provide ample working room.  Provide 6" to 9" clearance on both sides of pipe or conduit.

2.	Excavate trenches to depth indicated or required.  Carry depth of trenches for piping to establish indicated flow lines and invert elevations.

3.	Where rock is encountered, carry excavation 6" below specified elevation and backfill with a 6" layer of crushed stone or gravel prior to pipe installation.

4.	Grade bottoms of trenches as indicated, notching under pipe bells to provide solid bearing for entire body of pipe.

5.	Backfill trenches with concrete where trench excavations pass within 18" of column or wall footings and which are carried below bottom of such footings, or which pass under wall footings.  Place concrete to level of bottom of adjacent footing.

6.	Do not backfill trenches until tests and inspections have been made and backfilling authorized by the SDR.  Use care in backfilling to avoid damage or displacement of pipe systems.

I.	Excavation for Trenches Near Buildings 858 and 897.

1.	Scrapers cannot be used for excavation of the soils near Buildings 858 and 897..

2.	Excavations can be carried out using a front-end-loader equal to the Michigan Model 140 or a backhoe equal to the Ford Model 550.  This equipment may be used closer than 150 ft. from Buildings 858 and 897.

3.	Excavations at closer distances shall involve manual digging with shovels.

4.	Small rubber-tired bulldozers may be used for miscellaneous excavation and cleanup at distances not closer than 200 ft. from Buildings 858 and 897.

5.	Throughout the excavation process, the vibration conditions in Buildings 858 and 897 will be monitored.  If these measurements show that the restriction on excavation procedures can be relaxed from the above, the contractor will be notified.

6.	Excavation shall be performed per PART 3.01.H.

J.	Cold Weather Protection.  Protect excavation bottoms against freezing when atmosphere temperature is less than 35 degrees F. (1 degree C).  Do not place any construction on frozen ground.

3.02	COMPACTION

A.	General.  Control soil compaction during construction, providing minimum percentage of density specified for each area classification indicated below.

B.	Percentage of Maximum Density Requirements.  Compact soil to not less than the following percentages of maximum density for soils which exhibit a well-defined moisture-density relationship (cohesive soils) determined in accordance with ASTM D 1557; and not less than the following percentages of relative density, determined in accordance with ASTM D 2049, for soils which will not exhibit a well-defined moisture-density relationship (cohesionless soils).

1.	Structures, Building Slabs and Steps, Pavements:  Compact top 12" of sub-grade and each layer of backfill or fill material at 95% relative density.  (Exception:  Utility trenches under pavements may be compacted as indicated on Standard Drawing 90426).

2.	Lawn or Unpaved Areas:  Compact top 6" of sub-grade and each layer of backfill or fill material at 85% maximum density for clayey soils (more than 35% passing No. 200 sieve) and 90% relative density for all other soils.

3.	Walkways:  Compact top 6" of sub-grade and each layer of backfill or fill material at 90% maximum density for clayey material or 95% relative density for all other material.

C.	Compaction Near Buildings 858 and 897

1.	Static (non-vibratory) roller compactors may be used without restrictions.

2.	Small hand-held "page" compactors may be used at distances no closer than 100 ft. from Buildings 858 and 897.

3.	A Ray Go Model 22A vibratory compactor may be used no closer than 400 ft. from Buildings 858 and 897.

4.	A hand-guided Rammex vibratory compactor may be used no closer than 250 ft. from Buildings 858 and 897.

5.	An Ingersol Rand Model DA30 vibratory compactor may be used no closer than 150 ft. from Buildings 858 and 897.

D.	Moisture Control.  Where sub-grade or layer of soil material must be moisture conditioned before compaction, uniformly apply water to surface of sub-grade, or layer of soil material, to prevent free water appearing on surface during or subsequent to compaction operations.  Remove and replace, or scarify and air dry, soil material that is too wet to permit compaction to specified density.

3.03	BACKFILL AND FILL

A.	General.  Place acceptable soil material in layers to required sub-grade elevations, for each area classification listed below:

1.	In excavations, use satisfactory excavated or borrow material.

2.	Under building slabs, use granular base material.

3.	Behind retaining walls, use retaining wall backfill material.

B.	Backfill excavation as promptly as work permits, but not until completion of the following:

1.	 Acceptance of construction below finish grade including, where applicable, dampproofing, waterproofing, and perimeter insulation.

2.	Inspection, testing, approval, and recording locations of underground utilities.

3.	Removal of concrete formwork.

4.	Removal of shoring and bracing, and backfilling of voids with satisfactory materials.

5.	Removal of trash and debris.

C.	Ground Surface Preparation.  Remove vegetation, debris, unsatisfactory soil materials, obstructions, and deleterious materials from ground surface prior to placement of fills.  Plow, strips, or break-up sloped surfaces steeper than 1 vertical to 4 horizontal so that fill material will bond with existing surface.

D.	Placement and Compaction.

1.	Place backfill and fill materials in layers not more than 8" in loose depth for material compacted by heavy compaction equipment, and not more than 6" loose depth for material compacted by hand-operated tampers.

2.	Before compaction, moisten or aerate each layer as necessary to provide optimum moisture content.  Compact each layer to required percentage of maximum dry density or relative dry density for each area classification.  Do not place backfill or fill material on surfaces that are muddy, frozen, or contain frost or ice.

3.	Place backfill and fill material evenly adjacent to structures, piping or conduit to required elevations.  Take care to prevent wedging action of backfill against structures or displacement of piping or conduit by carrying material uniformly around structure, piping or conduit to approximately same elevation in each lift.

E.	Backfill at Utility Trenches.  Install continuous utility identification tape at all utility trenches as they are backfilled.  Locate the tape approximately three feet above the utility line, but not less than one foot below grade. Install it directly above and parallel to the utility line with the printed side up.  Take necessary precautions to avoid distorting or misplacing the tape as backfill continues.

3.04	GRADING

A.	General.  Uniformly grade areas within limits of grading under this section, including adjacent transition areas.  Smooth finished surfaces within specified tolerances, compact with uniform levels or slopes between points where elevations are indicated, or between such points and existing grades.

B.	Grading Outside Building Lines

1.	Grade areas adjacent to building lines to drain away from structures and to prevent ponding.

2.	Finish surfaces free from irregular surface changes and as follows:

Lawn or Unpaved Areas:  Finish areas to receive topsoil to within not more than 0.10' above or below required sub-grade elevations.

Walks:  Shape surface of areas under walks to line, grade and cross-section, with finish surface not more than 1/2" above or below required sub-grade elevation.

Pavements:  Shape surface of areas under pavement to line, grade and cross-section, with finish surface not more than 1/2" above or below required sub-grade elevation.

C.	Grading Surface of Fill Under Building Slabs.  Grade smooth and even, free of voids, compacted as specified, and to required elevation.  Provide final grades within a tolerance of 1/2" when tested with a 10' straightedge.

D.	Compaction.  After grading, compact sub-grade surfaces to the depth and indicated percentage of maximum or relative density for each area classification.

3.05	BUILDING SLAB DRAINAGE COURSE

General:  Drainage course consists of placement of 6" thickness of granular base material over sub-grade surface to support concrete building slabs.

3.05	MAINTENANCE

A.	Protection of Graded Areas.  Protect newly graded areas from traffic and erosion.  Keep free of trash and debris.  Repair and re-establish grades in settled, eroded, and rutted areas to specified tolerances.

B.	Reconditioning Compacted Areas.  Where completed compacted areas are disturbed by subsequent construction operations or adverse weather, scarify surface, re-shape, and compact to required density prior to further construction.

C.	Settling.  Where settling is measurable or observable at excavated areas during general project warranty period, remove surface (pavement, lawn or other finish), add backfill material, compact, and replace surface treatment. Restore appearance, quality, and condition of surface or finish to match adjacent work, and eliminate evidence of restoration to greatest extent possible.

3.07	DISPOSAL OF EXCESS AND WASTE MATERIALS

A.	Removal of Excess Materials.  Transport excess excavated material to designated soil storage areas on Kirtland Air Force Base.  Waste areas will generally be within one mile of project site.  Stockpile soil or spread as directed by the SDR.

END OF SECTION