SPILL PREVENTION, CONTROL, AND COUNTERMEASURES PLAN

NATIONAL WEATHER SERVICE

Wichita Weather Forecast Office

2142 South Tyler Road

Wichita, Kansas  67209

Original Date of Plan	:	February 19, 1993

Date of Last Plan Review	:	March 19, 2002

Date of Last Amendment

and P.E. Certification	:	March 19, 2002

Designated Person Responsible for Spill Prevention:

Joe Rosner, Environmental Focal Point

Telephone: (316) 942-8483

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of Title 40 of the Code of Federal Regulations Part 112, I attest that this Spill Prevention, Control, and Countermeasures (SPCC) Plan has been prepared in accordance with good engineering practices.

| John McCall |
| --- |
| Printed Name of Registered Engineer |
| Signature of Registered Engineer and Date |
| Registration No. PE-050653-E | State PA |

REVIEW DOCUMENTATION AND MANAGEMENT APPROVAL PAGE

REVIEW DOCUMENTATION

In accordance with Title 40 Code of Federal Regulations (CFR) Part 112.5(b), a review and evaluation of this Spill Prevention, Control, and Countermeasures (SPCC) Plan is conducted at least once every 3 years.  As a result of this review and evaluation, the National Weather Service will amend the SPCC Plan within 6 months of the review to include more effective prevention and control technology if:

C	Such technology will significantly reduce the likelihood of a spill event from the facility, and

C	If such technology has been field-proven at the time of review.

Any amendment to the SPCC Plan shall be certified by a Professional Engineer within 6 months after a change in the facility design, construction, operation, or maintenance occurs that materially affects the facility’s potential for the discharge of oil into or upon the navigable waters of the United States or adjoining shorelines.

| Review Date | Signature of Responsible Manager | Amended (Yes or No)? 1 |
| --- | --- | --- |

1	Amendment necessary and certified by a Registered Professional Engineer per Title 40 CFR Part 112.3(d)

MANAGEMENT APPROVAL

The National Weather Service is committed to the prevention of discharges of oil to navigable waters and the environment.  We maintain the highest standards for spill prevention, control, and countermeasures through regular review, updating, and implementation of this SPCC Plan for the Weather Forecast Office.

Richard Elder, Meteorologist in Charge

Printed Name and Title of Responsible Manager

Signature and Date

CONTENTS

Section	Page

Certification	i

Review Documentation and Management Approval	ii

PART I - GENERAL INFORMATION	1

A.	GENERAL	1

1.	Name	1

2.	Type	1

3.	Date of Initial Operation	1

4.	Location	1

5.	Name and Address of Operator	1

6.	Facility Contacts	1

B.	SITE DESCRIPTION AND OPERATIONS	1

1.	Facility Location, Layout, and Operations	1

2.	Facility Storage	2

3.	Drainage Pathway and Distance to Navigable Waters	2

4.	Spill History	3

5.	Spill Potential, Volumes, and Rates	3

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL	4

A.	SPILL PREVENTION	4

1.	Bulk Storage Tanks and Facility Transfer Operations	4

2.	Tank Truck Unloading Operations	4

3.	Inspections and Records	5

4.	Site Security	6

5.	Training	6

B.	SPILL CONTROL	6

1.	Secondary Containment Designs, Construction Material, and Volume	6

2.	Spill Kits Type and Location	7

PART III - SPILL COUNTERMEASURES AND REPORTING	8

A.	SPILL COUNTERMEASURES	8

B.	SPILL REPORTING	9

1.	General Notification Procedures for All Spills	9

2.	Federal Notifications	9

3.	State Notification	10

4.	Cleanup Contractor Notification	10

PART IV - RECOMMENDED IMPROVEMENTS	11

A.	PHYSICAL UPGRADES	11

B.	PROCEDURAL CHANGES	11

1.	Inspections and Preventative Maintenance	11

2.	Training	11

Appendix

A	TANK ULLAGE/FUELING LOG AND FUEL UNLOADING PROCEDURE CHECKLIST

B	INSPECTION CHECKLISTS

C	TRAINING OUTLINE AND TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, SECTION 112.1-112.20-OIL POLLUTION PREVENTION

D	SPILL REPORTING FORM

E	CROSS REFERENCE OF THE REQUIREMENTS OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, SECTION 112.7, WITH THIS PLAN

FIGURES

Figure	Page

1	SITE LOCATION	12

2	SITE LAYOUT	13

TABLES

Table	Page

1	DESCRIPTIVE INVENTORY OF FACILITY STORAGE	14

2	POTENTIAL SPILL SOURCES AND VOLUMES	15

PART I - GENERAL INFORMATION

- GENERAL

This section provides general information about the facility.

  - Name

National Weather Service (NWS)

Wichita Weather Forecast Office (WFO)

  - Type

This facility is an onshore facility (non-production) that operates as a river and weather forecast center and is staffed 24 hours per day, 7 days per week, and 365 days per year.

  - Date of Initial Operation

January 1992

  - Location

2142 South Tyler Road

Wichita, Sedgewick County, Kansas 67209

  - Name and Address of Operator

National Weather Service

2142 South Tyler Road

Wichita, Sedgewick County 67209

  - Facility Contacts

Name		Title				Telephone Number

Joe Rossner		Environmental Focal Point	(316) 942-8483 (24 hours/day)

Richard Elder		Meteorologist-In-Charge	(316) 942-8483

- SITE DESCRIPTION AND OPERATIONS

This section describes the site location, its operations that store diesel fuel, site drainage patterns, spill history, and spill potential.

  - Facility Location, Layout, and Operations

The facility is located in Wichita, Sedgewick County, Kansas, adjacent to the Wichita Municipal Airport (Figure 1).  Figure 2 shows the layout of the facility, including the location of a 1,000-gallon aboveground storage tank (AST), a 25-gallon day tank, and two 250-gallon Radar Data Acquisition (RDA) tanks.

The 1,000-gallon AST and day tank store fuel that is used to power a 300-kilowatt (kW) WFO emergency generator associated with the WFO building.  The WFO generator is used to supply a backup source of electricity for WFO operations.  The WFO generator and the day tank are located in the WFO generator room in the eastern portion of the WFO building and are not exposed to precipitation.  The 1,000-gallon AST is located immediately outside the WFO generator room to the south.

The two 250-gallon RDA tanks store fuel that is used to power the facility’s RDA emergency generator.  The RDA tanks and RDA generator are located in the RDA generator building and are not exposed to precipitation.

The estimated fuel usage is approximately 75 gallons per month.  This estimate is based on an automatic test of the generator once per week for 30 minutes.  Fuel consumption would increase based on the frequency and duration of any power outages.

  - Facility Storage

The 1,000-gallon AST is a welded steel plate tank enclosed inside a concrete outer shell that provides sufficiently impervious containment and protects the containment from exposure to precipitation.  The 1,000-gallon AST has a 2-inch-diameter vent and a 6-inch-diameter emergency vent.

The 1,000-gallon AST is connected to a pump on top of the day tank via a double-walled line that travels through the wall of the WFO generator building.  This pump moves fuel from the 1,000-gallon AST into the day tank.  The 25-gallon day tank is a single-walled rectangular steel tank set in an open top spill pan (rupture basin).  The day tank is connected to the generator by flexible rubber supply and return lines.

The two 250-gallon RDA tanks are rectangular, singled-walled and constructed of welded steel plates.  The tanks supply fuel to the RDA generator via rubber supply lines.

Table 1 summarizes the pertinent information on the tanks at the facility.

  - Drainage Pathway and Distance to Navigable Waters

Any fuel spilled outside the secondary containment of the 1,000-gallon AST or the day tank would travel east and then north toward culvert that directs flow west beneath the facility driveway and to a drainage ditch.  Any fuel spilled outside the secondary containment of the two 250-gallon RDA tanks would flow north to the same culvert.  The ditch directs runoff west and into a second drainage ditch that directs flow to the north along South Tyler Road.  The ditch along South Tyler Road directs flow to a low-lying wetland area.

  - Spill History

Reportable spill events from January 1992 (start of operations) to present (date on cover of this plan):

None.

  - Spill Potential, Volumes, and Rates

The most probable causes of spills from the 1,000-gallon AST and RDA tanks are from overfilling, a ruptured hose during fuel unloading, or failure of fuel supply lines.  For the day tank, the probable causes of spills are from a failure of the pump to shut down or failure of the line from the pump to the day tank.  Low probability events for any of the tanks could include loss of structural integrity because of vandalism or natural disaster.  It is possible that a vehicle collision could cause a spill from the 1,000-gallon AST, but the probability of such an event is low because the 1,000-gallon AST is not in the direct line of vehicle traffic and is separated from vehicle traffic by the WFO generator room.

Table 2 summarizes the potential type of failure, potential spill volume, estimated rate, and direction of spill flow from the tanks.

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES 
FOR SPILL PREVENTION AND CONTROL

This section discusses spill prevention and control measures that shall be implemented at the facility.

- SPILL PREVENTION

This section describes design components and operating procedures that shall be implemented at the facility to prevent oil spills.

  - Bulk Storage Tanks and Facility Transfer Operations

1,000-gallon AST:  The tank construction is compatible with the diesel fuel stored in the tank.  The concrete outer shell provides sufficiently impervious containment and completely encloses the AST such that precipitation does not enter the containment.  A 5-gallon-capacity round spill container surrounds the fill spout.  The AST is equipped with an audible high-level alarm set at 85 percent of the AST capacity (850 gallons) and an automatic shut-off valve on the cam-lock fitting fill spout set to close at 90 percent of the AST capacity (900 gallons).  An interstitial monitoring device between the primary tank and concrete outer shell (secondary containment) is connected to an audible alarm system.  A float-type level gauge indicates the fuel level (from empty to full) in the AST.

Day Tank:  The day tank is located inside the WFO generator building and is not exposed to precipitation.  The day tank is equipped with a liquid level gauge to indicate the amount of fuel in the tank (from empty to full).  It is situated over an open-top spill pan (rupture basin) designed to hold 110 percent of the day tank volume.  The rupture basin is equipped with a float switch designed to detect fuel within the basin and a high-level float switch; both switches shut off the fuel pump if engaged.

Piping:  An antisiphoning valve is located between the 1,000-gallon AST and the pump to prevent unwanted fuel from being siphoned from the 1,000-gallon AST.  The piping from the 1,000-gallon AST to the day tank is in a polyvinyl chloride pipe sleeve to protect it from corrosion.

RDA Tanks:  These tanks are located inside the RDA generator building that provides sufficient containment for the contents of the tanks.  The tanks are constructed of steel and are compatible with the diesel fuel stored.  The tanks are equipped with fuel sensors and a high-level audible alarm that sounds when the fuel level reaches 85 percent of the tank capacity.  The RDA generator building is designed with a “tub flooring” that is approximately 6- to 8-inches deep, with a raised door frame to keep potential spills from flowing out of the doorway.

  - Tank Truck Unloading Operations

All delivery drivers shall have U.S. Department of Transportation hazardous material transportation training as required by Federal law.

The remainder of this section discusses the procedures that shall be used during unloading of fuel from the tank truck into the storage tank to prevent spills.  Using the form in Appendix A, this procedure shall be documented every time refueling occurs.  Copies of this form shall be kept for 3 years.

The following procedure shall be used prior to fuel unloading:

    - Move spill containment equipment, such as booms or spill barriers, into the unloading area.

    - Ensure that the audible high-level alarm system and the automatic shutoff valve are functioning properly.

    - Determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (see Appendix A). This ullage is communicated to the fuel supply contractor and marked in the fueling log.

    - Block the tank truck wheels.

    - Place drip pans under all pump hose fittings (if applicable) prior to unloading.

    - Ensure the fill nozzle is placed in the appropriate tank appurtenance.

Both the NWS representative and the delivery driver shall remain with the vehicle at all times during unloading.  Gauges on the tank and the truck shall be continuously monitored to ensure the ullage is not exceeded.  If the audible high-level alarm sounds, the unloading of fuel shall be stopped as soon as possible.

After fuel unloading is completed:

    - Record the amount of fuel transferred to the tank in the log (Appendix A).

    - Drain the fill hose and then ensure that all drain valves are closed (if applicable) before removal of the hose from the tank.

    - Pour any fuel in the drip pans, tank truck containment pool, or spill container on the fill pipe into the AST (if it has the capacity), or dispose of it appropriately.

    - Inspect the tank truck before removing the blocks to ensure the lines have been disconnected from the tank.

    - Remove the blocks from the truck wheels.

    - Place a copy of the fuel unloading checklist in the SPCC plan.

  - Inspections and Records

Inspection and Maintenance of Tanks:  The 1,000-gallon AST, day tank, and RDA tanks shall be inspected weekly for any fuel outside the tank, especially at seams (including the underside).  The concrete outer shell is inspected for excess cracks.  The outside of exposed piping is inspected weekly, especially at the joints such as gasket fittings.  Monthly and annual inspections shall follow the checklists shown in Appendix B.

Record Keeping:  The Environmental Focal Point or designated alternate is responsible for completing the ullage logs and documenting the fuel unloading procedures.  These records, as well as records of all inspections, shall be maintained for at least 3 years from the time of inspection.

  - Site Security

Adequate lighting is provided for all tanks such that spills can be detected and vandalism deterred and there is electronic surveillance on the premises.  Both the WFO generator room and RDA generator building are kept locked.  A security fence surrounds the entire RDA area, including the RDA generator building.

Signage around all of the tanks warns of the presence of a combustible liquid, that the combustible liquid is diesel fuel number 2, and that smoking is not permitted near the tanks.  A fire extinguisher is located in the adjacent generator enclosures.  None of the tanks are located in the direct line of parking lot traffic.

  - Training

The Environmental Focal Point (person responsible for spill prevention) and an alternate shall be trained in the intent of applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in paragraph 3, above.  Spill control and countermeasures also shall be included in the training.

Training shall be repeated once per year.  All new personnel responsible for implementing this SPCC plan shall be properly trained before beginning the new position.  A record of who was trained, when, and by whom, shall be filed with this SPCC plan and kept for a period of 3 years.

- SPILL CONTROL

This section describes control measures that shall be implemented to prevent any spilled oil from entering navigable waters or adjoining shorelines.

  - Secondary Containment Designs, Construction Material, and Volume

For the 1,000-gallon AST, the concrete outer shell provides sufficiently impervious containment and completely encloses the AST such that precipitation does not enter the containment.  A 5-gallon-capacity round spill container surrounds the fill spout.  The AST is equipped with an audible high-level alarm set at 85 percent of the AST capacity (850 gallons) and an automatic shut-off valve on the cam-lock fitting fill spout set to close at 90 percent of the AST capacity (900 gallons).  An interstitial monitoring device between the primary tank and concrete outer shell (secondary containment) is connected to an audible alarm system.  A float-type level gauge indicates the fuel level (from empty to full) in the AST.

The day tank is contained within the WFO generator room that provides containment and protects the tank area.  The day tank is situated over a a rupture basin designed to hold 110 percent of the day tank volume.  The rupture basin is equipped with a float switch designed to detect fuel within the basin; the float switch will shut off the fuel pump if engaged.  The day tank is located inside the WFO generator room that does not allow precipitation into the area, and the floor of the WFO generator room building is constructed to provide adequate secondary containment.  The WFO generator room is designed with a “tub flooring” with a raised door frame to prevent spills from flowing from the building.

Secondary containment for the two RDA tanks is provided for in the RDA generator building design.  Adequate containment volume is provided in the building in the case of an instantaneous release.  The RDA generator building is designed with a “tub flooring” that is approximately 6 to 8 inches deep, with a raised door frame to keep fuel from spilling out of the doorway.

  - Spill Kits Type and Location

The facility shall maintain spill kit materials such as absorbent pads and mats sufficient to prevent a spill from reaching a nearby water body.  The kits include oil absorbent socks, pads, and booms in a 95-gallon polyethylene container that can be used as a disposal container.  These items are stored in the generator shed.

PART III - SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is on prevention.  The spill countermeasures presented do not constitute a contingency plan detailed in Title 40 CFR Part 109, nor is one required.  Such a plan is only required under Title 40 CFR 112.7(d) if it is impracticable to provide containment, diversionary structures, or equipment to prevent the discharge of oil to navigable waters.  In addition, this facility is not required to have a facility response plan under Title 40 CFR Part 112.20 because it does not:

C	Transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons, or

C	Have a total storage capacity over 1 million gallons.

- SPILL COUNTERMEASURES

This section presents countermeasures to contain, clean up, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasure activities will be undertaken until conditions are safe for workers.  The “SWIMS” procedure should be implemented as countermeasures:

S   -	Stop the leak and eliminate ignition sources.

a. 	Attempt to seal or some how stop leak if it can be done safely.

b. 	Attempt to divert flow away from catch basins with a spill barrier or the contents of the spill kit.

c. 	Eliminate all ignition sources in the immediate area.

W  -	Warn others.

a.  	Yell out “SPILL.”  Inform the person in-charge at your facility.

b. 	Account for all personnel and ensure their safety.

c. 	Notify contacts and emergency response contractor as described in the following section for assistance in control and cleanup.

I    -	Isolate the area.

a. 	Rope off the area.

M  -	Minimize your exposure.  Stay upwind.

S    -	Stand by to assist the emergency response contractor, if necessary.

- SPILL REPORTING

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The individuals and organizations that are notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

A spill report form that requests the information to be reported to all agencies in written form (to the extent known) is included in Appendix D.  Copies of the completed form should be submitted, preferably by e-mail, to the NWS Environmental Compliance Officer and the NOAA Regional Compliance Officer.

  - General Notification Procedures for All Spills

The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

    - First, call 9-1-1 (or the local emergency agency) if there is an immediate emergency

    - Next, notify the appropriate individuals within the NWS:

1.		Mike Jacob, (301) 713-1838 Ext. 165, JMichael.Jacob@noaa.gov, NWS Environmental Compliance Officer

2.		Olga Kebis, (301) 713-1838 Ext. 173, Olga.Kebis@noaa.gov, NWS Safety Officer

3.		Kirt Grahl, (816) 426-3226, Ext. 470, Kirt.Grahl@noaa.gov, NWS Central Regional Environmental/Safety Coordinator

4.		Sherilyn Villegas, (816) 426-3925, Ext. 263, Sherilyn.S.Villegas@noaa.gov, NOAA Central Regional Compliance Officer

  - Federal Notifications

The Federal Clean Water Act as described in Title 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency’s (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  Title 40 CFR Part 110.3 defines “may be harmful” as a discharge that:

    - Violates applicable water quality standards, or

    - Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or causes a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines.

If either of these criterion are met contact:

    - The National Response Center (EPA and USCG):  (800) 424-8802

Under the SPCC regulations, spill information listed in Title 40 CFR Part 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

    - A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shorelines in a single event, or

    - Two spill events that cause visible sheens upon navigable waters or adjoining shorelines within any 12-month period.

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA); therefore, no other notification to the EPA is required for discharges of diesel fuel other than those listed above.

  - State Notification

To satisfy the state reporting requirements, the location and quantity of the spill must be determined.  Under the Kansas Administrative Regulations, Part 28-44-24, a reportable quantity (RQ) is defined as follows:

    - Any spill over 25 gallons, or

    - Any spill which creates a sheen upon navigable waters of the State.

If one or both of these criteria are met, contact the Kansas Emergency Spill Hotline within 24 hours of obtaining knowledge of the release:

    - (785) 296-1679 (During business hours)

    - (785) 296-0614 (After business hours)

  - Cleanup Contractor Notification

An emergency response contractor also should be notified to assist with the clean up of a spill, if necessary.  Contact information for at least three emergency response vendors shall be maintained in this plan.  NWS has identified the following contractors that are available for emergency response:

    - Haz-Mat Response, Inc.:		(800) 229-5252

    - Integrated Solutions			(316) 264-7050

    - Safety Kleen				(316) 942-5001 or (316) 832-1778

    - 3E Company				(800) 468-1760

PART IV - RECOMMENDED IMPROVEMENTS

In accordance with Title 40 CFR Section 112.7, this section presents physical upgrades or procedural changes that are not yet fully operational but are called for in the plan.

- PHYSICAL UPGRADES

There are no recommended physical upgrades.

- PROCEDURAL CHANGES

  - Inspections and Preventative Maintenance

The inspection checklists found in Appendix B should be followed.  This requirement is found in Title 40 CFR Part 112.7(e)(8).  The area within and around all tanks shall be inspected for signs of leakage regularly.  Visual inspections of the outside each of the tank’s walls shall be inspected for potential problems with tank integrity such as leaks or evidence of cracking or breaching.  Also, the interstitial monitoring device in the 1,000-gallon AST is designed to monitor the integrity of its primary tank.  If a problem is suspected with any tank, tightness testing should be initiated soon after discovery.

  - Training

The Environmental Focal Point (person responsible for spill prevention at the facility) and an alternate should be trained in the intent of the applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in the previous section.  Spill control and countermeasures also should be included in the training.  The alternate should be designated in case the primary person is off the site at the time of a spill.  A recommended outline for the training is found in Appendix C.

Training should be repeated once per year.  All new personnel responsible for implementing the SPCC plan should be properly trained before beginning the new position.  A record of who was trained, when, and by whom, should be filed with this SPCC Plan and kept for a period of three years.  This requirement is found in Title 40 CFR 112.7(e)(10).

Spill prevention briefings for operating personnel should be conducted at frequent intervals to ensure adequate understanding of the SPCC plan and to describe spill events or failures, malfunctioning components, and recently developed precautionary measures.

Figure 1 Site Location

Figure 2 Site Layout

TABLE 1

DESCRIPTIVE INVENTORY OF FACILITY STORAGE

| Tank | Nominal Capacity (Gallons) | Product Stored | Type | Double Walled? |
| --- | --- | --- | --- | --- |
| 1,000-gallon AST | 1,000 | Diesel fuel number 2 | AST | Yes |
| Day Tank | 25 | Diesel fuel number 2 | AST | Yes1 |
| RDA Tank | 250 | Diesel fuel number 2 | AST | Yes2 |
| RDA Tank | 250 | Diesel fuel number 2 | AST | Yes2 |
| Total Capacity | 1,525 |  |  |  |

Notes:	AST	Aboveground storage tank

1	Tank is situated over a rupture basin and is located inside building capable of containing the entire volume of the tank.

2	Tank is in a storage building capable of containing the entire volume of the tank.

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1,000-gallon AST | Overfilling or a ruptured hose during fueling | >0 to 40a | 80b | East and north | Operational procedures are in place to prevent overfilling. |
|  | Failure of fuel supply line to pump | >0 to 1,000 | Variable | East and north | Can be minimized through routine inspections. |
|  | Structural failure or vandalism | >0 to 1,000 | Variable | East and north | Low probability event that both primary and secondary tank shells would fail. |
|  | Vehicle collision | >0 to 1,000 | Variable | East and north | Tank is not located in the direct line of traffic. |
|  | Overturn or puncture during a natural disaster | >0 to 1,000 | Variable | East and north | Low probability event. Double-walled tank gives extra protection from rupture, but a natural disaster could cause a spill. |
| Generator Day Tank | Failure of the pump to shut down after filling day tank or failure of the line from pump to day tank. | >0 to 1,000 | Variable | East and north | Can be minimized through routine inspections. Tank has both a rupture basin and the building floor for containment. |
|  | Failure of fuel return line | >0 | 10c | East and north | Can be minimized through routine inspections. Tank has both a rupture basin and the building floor for containment. |
|  | Structural failure or vandalism | >0 to 25 | Variable | East and north | Low probability event can be minimized through regular inspections and maintenance. Tank has both a rupture basin and the building floor for containment. |
|  | Overturn or puncture during a natural disaster | >0 to 25 | Variable | East and north | Low probability event. |

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| Each of two RDA Tanks | Overfilling or a ruptured hose during fueling | >0 to 40a | 80b | East and north | None. |
|  | Failure of fuel supply line to pump | >0 to 250 | Variable | East and north | Can be minimized through routine inspections. Tanks are in building designed to contain spills. |
|  | Structural failure or vandalism | >0 to 250 | Variable | East and north | Low probability event that both primary and secondary tank shells would fail. Tanks and supply lines are in a building designed to contain spills. |
|  | Overturn or puncture during a natural disaster | >0 to 250 | Variable | East and north | Low probability event. |

Notes:

a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump.

b	Approximate maximum pumping rate of fill truck.

c	Estimated return line flow rate.

APPENDIX A

TANK ULLAGE/FUELING LOG AND

FUEL UNLOADING PROCEDURE CHECKLIST

(2 Pages)

APPENDIX A-1

TANK ULLAGE AND FUELING LOG

Tank Capacity 			  gallons

| Date | Initials | Gauge Reading | Initial Volume of Fuel in Tanka (Gallons) | Available Capacity or Ullageb (Gallons) | Quantity Added (Gallons) | Comments |
| --- | --- | --- | --- | --- | --- | --- |

Notes:

a	From gauge reading

b	Available capacity = tank capacity - initial volume of fuel in tank

APPENDIX A-2

FUEL UNLOADING PROCEDURE CHECKLIST

Date:										Tank:

NWS Representative:								Supplier:

| / | ITEM | DESCRIPTION | COMMENT |
| --- | --- | --- | --- |
| The following six items must be completed prior to fuel unloading: |
|  | 1 | Move spill containment equipment, such as booms or spill barriers, into the unloading area. |  |
|  | 2 | Ensure the audible high-level alarm system and automatic shutoff valve are functioning properly. |  |
|  | 3 | Determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (see Appendix A, page A-1 in SPCC plan). This ullage should then be marked in the fueling log and communicated to the tank truck unloading contractor. |  |
|  | 4 | Block the wheels of the tank truck. |  |
|  | 5 | Place drip pans under all pump hose fittings (if applicable) after the hose is hooked up to the tank and prior to unloading. |  |
|  | 6 | Ensure the fill nozzle is placed in the appropriate tank appurtenance. |  |
| During unloading |
|  | 7 | Ensure that the NWS representative and the tank truck operator remain with the vehicle at all times during unloading. |  |
|  | 8 | Monitor the gauges on the tank and the truck continuously to ensure the ullage is not exceeded. If the audible high-level alarm sounds, the unloading of fuel is stopped as soon as possible. |  |
| After fuel unloading is completed |
|  | 9 | Record the amount of fuel unloaded in the log (Appendix A, page A-1). |  |
|  | 10 | Prior to removing the fill hose from the tank, ensure that it is drained and that all drain valves are closed (if applicable). |  |
|  | 11 | Any fuel accumulated in the drip pans or spill container on the fill pipe should be poured into the tank (if it has the capacity) or disposed of appropriately (describe how it was disposed of, if applicable). |  |
|  | 12 | Inspect the tank truck prior to removing the blocks to ensure the lines have been disconnected from the tank. |  |
|  | 13 | Remove the blocks from tank truck wheels. |  |
|  | 14 | Place a copy of this fuel-unloading checklist in the SPCC plan. |  |

APPENDIX B

INSPECTION CHECKLISTS

(3 Pages)

APPENDIX B

INSPECTION FORMS

| MONTHLY INSPECTION CHECKLIST (Page 1 of 2) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| TANKS | YES | NO | NOTES |
| 1. Are there any oil stains on the outside of the tank, including the underside? |  |  |  |
| 2. Is there any oil on the ground, concrete, or asphalt around the tank? |  |  |  |
| 3. Are there any visible cracks or indications of corrosion on the tank, at fittings, joints, or seals (such as paint peeling or rust spots)? |  |  |  |
| 4. Are there any raised spots, dents, or cracks on the tank? |  |  |  |
| 5. Does it appear that the foundation has shifted or settled? |  |  |  |
| 6. Is the fuel gauge working properly? |  |  |  |
| 7. Are all vents clear so they may properly operate? |  |  |  |
| 8. If rainwater is present in secondary containment area, does sufficient volume remain for spill control (if applicable)? |  |  |  |

| MONTHLY INSPECTION CHECKLIST (Page 2 of 2) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| B. PIPING | YES | NO | NOTES |
| 1. Is there any oil on the outside of or under any aboveground piping, hoses, fittings, or valves? |  |  |  |
| 2. Are aboveground piping, hoses, fittings, or valves in good working condition? |  |  |  |
| C. SECURITY/SAFETY/SPILL COUNTERMEASURES |  |  |  |
| 1. Are lights working properly to detect a spill at night? |  |  |  |
| 2. Are all locks in the “lock” position? |  |  |  |
| 3. Are all warning signs properly posted and readable? |  |  |  |
| 4. Are vehicle guard posts in place and properly secured (if applicable)? |  |  |  |
| 5. Are spill kits easily accessible, protected from the weather, and complete? |  |  |  |
| Corrective Actions Required: |  |  |  |

| ANNUAL INSPECTION CHECKLIST (Page 1 of 1) |
| --- |
| Date of Inspection: | Tank Name or No.: |
| Date of Last Inspection: | Inspected by: |
|  | Signature: |
| A. MONTHLY CHECKLIST | YES | NO | NOTES |
| 1. Have monthly inspection checklists been completed? |  |  |  |
| B. TANKS |  |  |  |
| 1. Are all alarms and automatic shutoff devices working properly? |  |  |  |
| 2. Is interstitial monitor functioning properly (if applicable)? |  |  |  |
| C. OTHER |  |  |  |
| 1. |  |  |  |
| Corrective Actions Required: |  |  |  |

APPENDIX C

TRAINING OUTLINE AND

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS

PARTS 112.1 THROUGH 112.20 - OIL POLLUTION PREVENTION

(29 Pages)

APPENDIX C

OUTLINE FOR SPILL PREVENTION, CONTROL, AND COUNTERMEASURES TRAINING

Training will be provided for facility personnel at the following times:

C	System startup or whenever new equipment is installed

C	Within the first week of employment for new personnel

C	Annually

The training will include complete instruction in the elements of the facility’s Spill Prevention, Control, and Countermeasures plan and will include the following:

A.	Pollution Control Laws, Rules, and Regulations Including a Summary of Title 40 of the Code of Federal Regulations Part 112, “Oil Pollution Prevention” (see Attachment)

B.	Fuel Storage

1.	Purpose and application of the following system elements:

a.	Tanks

b.	Piping

c.	Pumps

d.	Accessory equipment

e.	Electronic monitors

2.	Operation, maintenance, and inspection of system elements

C.	Spill Prevention

1.	Potential spill sources

2.	Spill flow direction and impact on navigable waters

3.	Procedures to prevent spills, especially during fuel unloading

D.	Spill Control

1.	Secondary containment

2.	Safety valves

3.	Pump and equipment shutoff switches

4.	Use of catch basin inlet covers or other diversionary devices

E.	Spill Countermeasures

1.	Location and use of emergency phone numbers

2.	Location and use of fire extinguishers

3.	Location and use of spill cleanup kit

4.	Stopping the leak

ATTACHMENT

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS

PARTS 112.1 THROUGH 112.20 - OIL POLLUTION PREVENTION

APPENDIX D

SPILL REPORTING FORM

(1 Page)

APPENDIX D

SPILL REPORTING FORM

| GENERAL |
| --- |
| Name of Facility: National Weather Service Wichita Weather Forecast Office | Address: 2142 South Tyler Road Wichita, Kansas 67209 |
| Completed By: | Organization: National Weather Service |
| Position: | Phone: |
| SPILL INFORMATION |
| Date: | Time: |
| Location at Facility: | Quantity: |
| Substance Spilled: | Other: |
| OUTSIDE NOTIFICATIONS |
| Agencies | Recorder at Outside Agency | Date and Time |
| Call 9-1-1 (or the local emergency agency), if there is an immediate emergency |  |  |
| NWS/NOAA: Mike Jacob: (301) 713-1838, Ext. 165 Olga Kebis: (301) 713-1838, Ext. 173 Kirt Grahl: (816) 426-3226, Ext. 470 Sherilyn Villegas: (816) 426-3925, Ext. 263 |  |  |
| EPA NATIONAL RESPONSE CENTER or U.S. COAST GUARD: (800) 424-8802 |  |  |
| Kansas Emergency Spill Hotline: During Business Hours: (785) 296-1679 After Business Hours: (785) 296-0614 |  |  |
| INFORMATION ON SOURCE AND CAUSE |
| 5. DESCRIPTION OF ENVIRONMENTAL DAMAGE |
| 6. CLEANUP ACTION(S) TAKEN |
| 7. CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |

Note:	All information must be filled in.  If something is unknown, write “unknown.”

Copies must be submitted to the NWS/NOAA personnel listed above.

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF

TITLE 40 OF THE CODE OF FEDERAL REGULATIONS,

PART 112.7, WITH THIS PLAN

(1 Page)

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF 40 CFR 112.7 WITH THIS PLAN

| CFR Citation | Item | Plan Location |
| --- | --- | --- |
| 112.7(a) | Spill History | Part I.B.4 |
| 112.7(b) | Potential Spill Prediction, Volumes, and Rates | Part I.B.5 and Table 2 |
| 112.7(c) | Containment and Diversionary Structures | Part I.B.2 and Part II.B.2 |
| 112.7(d) | Secondary Containment Impracticability | Not Applicable |
| 112.7(e)(1) | Drainage Control | Part I.B.3 |
| 112.7(e)(2) | Bulk Storage Tanks and Secondary Containment | See Subparts |
| 112.7(e)(2)(I) | Tank Compatibility with Its Contents | Part II.A.1 |
| 112.7(e)(2)(ii) | Diked Area Construction and Containment for Storage Tanks | Not Applicable |
| 112.7(e)(2)(iii) | Diked Area Inspection and Drainage of Rainwater | Not Applicable |
| 112.7(e)(2)(iv) | Corrosion Protection of Buried Metallic Storage Tanks | Not Applicable |
| 112.7(e)(2)(v) | Corrosion Protection of Partially Buried Metallic Tanks | Not Applicable |
| 112.7(e)(2)(vi) | Aboveground Tank Periodic Integrity Testing | Part IV.B.1 |
| 112.7(e)(2)(vii) | Control of Leakage through Internal Heating Coils | Not Applicable |
| 112.7(e)(2)(viii) | Tank Installation Fail-safe Engineered | Part II.A.1, B.1 |
| 112.7(e)(2)(ix) | Observation of Disposal Facilities for Effluent Discharge | Not Applicable |
| 112.7(e)(2)(x) | Visible Oil Leak Corrections from Tank Seams and Gaskets | Part II.A.3 & Appendix A |
| 112.7(e)(2)(xi) | Appropriate Position of Mobile or Portable Tanks | Not Applicable |
| 112.7(e)(3) | Facility Transfer Operations | See Subparts |
| 112.7(e)(3)(i) | Buried Piping Installation Protection and Examination | Part II.A.1 & Appendix A |
| 112.7(e)(3)(ii) | Not-in-service and Standby Terminal Connections | Not Applicable |
| 112.7(e)(3)(iii) | Pipe Support Designs | Not Applicable |
| 112.7(e)(3)(iv) | Aboveground Valve and Pipeline Examination | Not Applicable |
| 112.7(e)(3)(v) | Aboveground Piping Protection from Vehicular Traffic | Not Applicable |
| 112.7(e)(4) | Facility Truck Unloading Operations | Part II.A.2 |
| 112.7(e)(5-7) | Oil Production Facilities (Onshore) and Oil Drilling, Production, or Work over Facilities (On Shore and Offshore) | Not Applicable |
| 112.7(e)(8) | Inspections and Record Keeping | Part II.A.3 |
| 112.7(e)(9) | Security | See Subparts |
| 112.7(e)(9)(i) | Fencing | Part II.A.4 |
| 112.7(e)(9)(ii) | Flow Valves Locked | Not Applicable |
| 112.7(e)(9)(iii) | Starter Controls Locked | Not Applicable |
| 112.7(e)(9)(iv) | Pipeline Loading and Unloading Connections Securely Capped | Not Applicable |
| 112.7(e)(9)(v) | Lighting Adequate to Detect Spills | Part II.A.4 |
| 112.7(e)(10) | Training | See Subparts |
| 112.7(e)(10)(i) | Personnel Instructions | Part II.A.5 & Appendix C |
| 112.7(e)(10)(ii) | Designated Person Responsible for Spill Prevention | Page i |
| 112.7(e)(10)(iii) | Spill Prevention Briefings | Part IV.B.2 |

Note:	CFR	Code of Federal Regulations