## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 1017
EPA ID No. | TXD980808778
Facility Name | Sunoco Inc. (R&M) Pasadena Plant
Facility Location
City | Pasadena
State | TX
Unit ID Name/No. | Boiler F- 8
Other Sister Facilities | None
Number of Sister Facilities | 0
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics
Capacity (MMBtu/hr) | 100
Soot Blowing | Yes, but uncharacterized
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics | NA
Hazardous Wastes | Liq
Haz Waste Description | Waste liquid fuels and combined PA residues
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft) | 6.4583
Height (ft) | 75
Gas Velocity (ft/sec)
Gas Temperature (°F) | 304.6667
Permitting Status | Tier I for metals and chlorine
HWC Burn Status (Date if Terminated)

## cond
Cond Description
1017C1
Report Name/Date | Source Emission Survey - Aristech Chemical Corp. - F-8 Boiler Stack (EPN 84); File No. 95-165B, September 1995
Report Prepare | METCO Environmental
Testing Firm | METCO Environmental
Testing Dates | 1995-09-28
Cond Dates | 1995-09-01
Condition Descr | CoC; max feed waste liq 2EH
Content | PM, HCl/Cl2, & CO emissions; metals, ash, & chlorine in waste feedstreams
1017C2
Report Name/Date | Source Emission Survey - Aristech Chemical Corp. - F-8 Boiler Stack (EPN 84); File No. 95-165B, September 1995
Report Prepare | METCO Environmental
Testing Firm | METCO Environmental
Testing Dates | 1995-09-27
Cond Dates | 1995-09-01
Condition Descr | CoC; max feed waste liq 2EH and combined PA residue
Content | PM, HCl/Cl2, & CO emissions; metals, ash, & chlorine in waste feedstreams
1017C3
Report Name/Date | Source Emission Survey - Aristech Chemical Corp. - F-8 Boiler Stack (EPN 84); File No. 95-165B, September 1995
Report Prepare | METCO Environmental
Testing Firm | METCO Environmental
Testing Dates | 1995-09-29
Cond Dates | 1995-09-01
Condition Descr | CoC; max feed for combined PA residue
Content | PM, HCl/Cl2, & CO emissions; metals, ash, & chlorine in waste feedstreams
1017C4
Report Name/Date | Source Emission Survey - Aristech Chemical Corp. - F-8 Boiler Stack (EPN 84); 2000
Report Prepare | METCO Environmental
Testing Firm | METCO Environmental
Testing Dates | 3/1-3/2000
Cond Dates | 2000-03-01
Condition Descr | Risk burn, normal operations
Content | HCl/Cl2, CO, D/Fs, VOC/SVOC, total organics, aldehydes/ketones, & particle size emissions; metals, ash, & chlorine in waste feedstreams
1017C5
Report Name/Date | Source Emission Survey - Aristech Chemical Corp. - F-8 Boiler Stack (EPN 84); 2000
Report Prepare | METCO Environmental
Testing Firm | METCO Environmental
Testing Dates | 2000-02-28
Cond Dates | 2000-02-01
Condition Descr | CoC
Content | PM
1017C6
Report Name/Date | Source Emission Survey - Aristech Chemical Corp. - F-8 Boiler Stack (EPN 84); 2000
Report Prepare | METCO Environmental
Testing Firm | METCO Environmental
Testing Dates | 2000-02-29
Cond Dates | 2000-02-01
Condition Descr | CoC
Content | PM

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
Sootblow
1 | 1017C1 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0114 | 0.0104 | 0.1344 | 0.0172
| PM (total) | E1 | gr/dscf | y | 0.0118 | 0.0108 | 0.1347 | 0.0175
| HCl | E1 | ppmv | y | 0.047191 | 0.055056 | 0.12667 | 0.076305
| Cl2 | E1 | ppmv | y | 0.01573 | 0.01573 | 0.02 | 0.017154
| Total Chlorine | E1 | ppmv | y | 0.078652 | 0.086517 | 0.16667 | 0.11061
| CO (RA) | E1 | ppmv | y | 0.1 | 0.1 | 0.1 | 0.1
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 14414 | 14739 | 14489 | 14547.3333
| O2 |  | % |  | 3.2 | 3.2 | 3.4 | 3.2667
| Moisture |  | % |  | 21.67 | 21.67 | 22.96 | 22.1
| Temperature |  | °F |  | 313 | 314 | 312 | 313
Sootblow
2 | 1017C2 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0195 | 0.0202 | 0.1149 | 0.051533
| PM (total) | E1 | gr/dscf | y | 0.0202 | 0.0208 | 0.1153 | 0.0521
| HCl | E1 | ppmv | y | 0.065882 | 0.090588 | 0.066667 | 0.074379
| Cl2 | E1 | ppmv | y | 0.032941 | 0.041176 | 0.0066667 | 0.026928
| Total Chlorine | E1 | ppmv | y | 0.13176 | 0.17294 | 0.08 | 0.12824
| CO (RA) | E1 | ppmv | y | 0.1 | 1.4 | 0.9 | 0.8
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 15473 | 15776 | 15221 | 15490
| O2 |  | % |  | 4 | 4 | 3.4 | 3.8
| Moisture |  | % |  | 19.04 | 19.17 | 20.56 | 19.59
| Temperature |  | °F |  | 333 | 337 | 335 | 335
Sootblow
3 | 1017C3 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0293 | 0.0294 | 0.1746 | 0.077767
| PM (total) | E1 | gr/dscf | y | 0.0296 | 0.0296 | 0.1749 | 0.078033
| HCl | E1 | ppmv | y | 0.023864 | 0.031818 | 0.04 | 0.031894
| Cl2 | E1 | ppmv | y | 0.023864 | 0.023864 | 0.013333 | 0.020354
| Total Chlorine | E1 | ppmv | y | 0.071591 | 0.079545 | 0.066667 | 0.072601
| CO (RA) | E1 | ppmv | y | 5.4 | 3.6 | 4.5 | 4.5
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 15221 | 15158 | 14879 | 15086
| O2 |  | % |  | 3.4 | 3.4 | 3.6 | 3.4667
| Moisture |  | % |  | 18.02 | 18.07 | 19.82 | 18.6367
| Temperature |  | °F |  | 306 | 304 | 304 | 304.6667
| 1017C4 |  |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) | E1 | ppmv | y | 0.007 | 0.007 | 0.007 | 0.007
| HCl | E1 | ppmv | y | 0.56495 | 0.52149 | 0.63066 | 0.57237
| Cl2 | E1 | ppmv | y | 0.060849 | 0.065919 | 0.07099 | 0.065919
| Total Chlorine | E1 | ppmv | y | 0.68664 | 0.65333 | 0.77264 | 0.7042
| Sampling Train | HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 11197 | 9986 | 10402 | 10528.3333
| O2 |  | % |  | 4 | 4 | 4.6 | 4.2
| Moisture |  | % |  | 20.37 | 19.58 | 18.37 | 19.44
| Temperature |  | °F |  | 299 | 299 | 298 | 298.6667
| Sampling Train | PSD | E2
| Stack Gas Flowrate |  | dscfm |  | 10159 | 9856 | 9974 | 9996.3333
| O2 |  | % |  | 4 | 3.8 | 4.6 | 4.1333
| Moisture |  | % |  | 21.05 | 22.01 | 24.06 | 22.3733
| Temperature |  | °F |  | 300 | 298 | 299 | 299
| 1017C5 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.0172 | 0.0117 | 0.0267 | 0.018533
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 16824 | 13638 | 14369 | 14943.6667
| O2 |  | % |  | 6 | 4.8 | 4.6 | 5.1333
| Moisture |  | % |  | 15.59 | 16.92 | 18.42 | 16.9767
| Temperature |  | °F |  | 364 | 346 | 345 | 351.6667
| 1017C6 |  |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.011 | 0.0136 | 0.0237 | 0.0161
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 16050 | 14202 | 15205 | 15152.3333
| O2 |  | % |  | 4.8 | 4.8 | 4.7 | 4.7667
| Moisture |  | % |  | 20.33 | 19.43 | 20.67 | 20.1433
| Temperature |  | °F |  | 341 | 343 | 348 | 344

## feed
Feedstreams
* | 1017C1 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Liquid Fuels |  | Waste Liquid Fuels |  | Waste Liquid Fuels |  | Waste Liquid Fuels |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 2518 |  | 2472 |  | 2418
| Heating Value | Btu/lb |  | 17000 |  | 18000 |  | 15700
| Ash | g/hr | nd | 571.122 | nd | 560.84 | nd | 548.52
| Chlorine | g/hr |  | 121.078 |  | 162.643 |  | 140.241
| Antimony | g/hr | nd | 2.284 | nd | 2.243 | nd | 2.194
| Arsenic | g/hr |  | 0.114 |  | 2.356 | nd | 0.088
| Barium | g/hr | nd | 0.057 |  | 0.079 | nd | 0.055
| Beryllium | g/hr | nd | 0.011 | nd | 0.011 | nd | 0.011
| Cadmium | g/hr | nd | 0.011 |  | 0.022 | nd | 0.011
| Chromium | g/hr |  | 0.126 |  | 0.146 |  | 0.132
| Lead | g/hr | nd | 1.713 | nd | 1.683 | nd | 1.646
| Mercury | g/hr |  | 0.023 |  | 5.16 | nd | 0.022
| Silver | g/hr | nd | 0.263 | nd | 0.247 | nd | 0.252
| Thallium | g/hr | nd | 10.166 | nd | 9.871 | nd | 9.764
| Stack Gas Flowrate | dscfm |  | 14414 |  | 14739 |  | 14489 |  | 14547.3333
| Oxygen | % |  | 3.2 |  | 3.2 |  | 3.4 |  | 3.2667
| Thermal Feedrate | MMBtu/hr |  | 42.806 |  | 44.496 |  | 37.9626 |  | 41.7549 |  | 42.806 |  | 44.496 |  | 37.9626 |  | 41.7549
| Estimated Firing Rate | MMBtu/hr | [7 empty] | 81.8961
Feedrate MTEC Calculations
| Ash | mg/dscm | 100 | 18.3533 | 100 | 17.6255 | 100 | 17.735 | 100 | 17.9046 | 100 | 18.3533 | 100 | 17.6255 | 100 | 17.735 | 100 | 17.9046
| Chlorine | ug/dscm |  | 3890.909 |  | 5111.3745 |  | 4534.342 |  | 4512.2085 |  | 3890.909 |  | 5111.3745 |  | 4534.342 |  | 4512.2085
| Antimony | ug/dscm | 100 | 73.3976 | 100 | 70.4907 | 100 | 70.9375 | 100 | 71.6086 | 100 | 73.3976 | 100 | 70.4907 | 100 | 70.9375 | 100 | 71.6086
| Arsenic | ug/dscm |  | 3.6635 |  | 74.0419 | 100 | 2.8453 | 3.5323 | 26.8502 |  | 3.6635 |  | 74.0419 | 100 | 2.8453 | 3.5323 | 26.8502
| Barium | ug/dscm | 100 | 1.8317 |  | 2.4827 | 100 | 1.7783 | 59.251 | 2.0309 | 100 | 1.8317 |  | 2.4827 | 100 | 1.7783 | 59.251 | 2.0309
| Beryllium | ug/dscm | 100 | 0.35349 | 100 | 0.3457 | 100 | 0.35566 | 100 | 0.35162 | 100 | 0.35349 | 100 | 0.3457 | 100 | 0.35566 | 100 | 0.35162
| Cadmium | ug/dscm | 100 | 0.35349 |  | 0.69139 | 100 | 0.35566 | 50.6339 | 0.46685 | 100 | 0.35349 |  | 0.69139 | 100 | 0.35566 | 50.6339 | 0.46685
| Chromium | ug/dscm |  | 4.0491 |  | 4.5883 |  | 4.2679 |  | 4.3018 |  | 4.0491 |  | 4.5883 |  | 4.2679 |  | 4.3018
| Lead | ug/dscm | 100 | 55.0482 | 100 | 52.8916 | 100 | 53.2193 | 100 | 53.7197 | 100 | 55.0482 | 100 | 52.8916 | 100 | 53.2193 | 100 | 53.7197
| Mercury | ug/dscm |  | 0.73912 |  | 162.1631 | 100 | 0.71131 | 0.43475 | 54.5378 |  | 0.73912 |  | 162.1631 | 100 | 0.71131 | 0.43475 | 54.5378
| Silver | ug/dscm | 100 | 8.4517 | 100 | 7.7625 | 100 | 8.1478 | 100 | 8.1206 | 100 | 8.4517 | 100 | 7.7625 | 100 | 8.1478 | 100 | 8.1206
| Thallium | ug/dscm | 100 | 326.6901 | 100 | 310.2155 | 100 | 315.6945 | 100 | 317.5334 | 100 | 326.6901 | 100 | 310.2155 | 100 | 315.6945 | 100 | 317.5334
| SVM | ug/dscm | 100 | 55.4017 | 49.3548 | 53.583 | 100 | 53.575 | 83.3063 | 54.1865 | 100 | 55.4017 | 49.3548 | 53.583 | 100 | 53.575 | 83.3063 | 54.1865
| LVM | ug/dscm | 4.3825 | 8.066 | 0.43772 | 78.9759 | 42.8571 | 7.4688 | 0.77439 | 31.5036 | 4.3825 | 8.066 | 0.43772 | 78.9759 | 42.8571 | 7.4688 | 0.77439 | 31.5036
* | 1017C2 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Liquid and Combined PA Residues |  | Waste Liquid and Combined PA Residues |  | Waste Liquid and Combined PA Residues |  | Waste Liquid and Combined PA Residues |  | Total |  | Total |  | Total |  | Total
| Feedrate Waste Liq | lb/hr |  | 1224 |  | 1255 |  | 1257
| Feedrate Residues | lb/hr |  | 2047 |  | 1924 |  | 2011
| Heating Value Liq | Btu/lb |  | 17800 |  | 15600 |  | 15900
| Heating Value Res | Btu/lb |  | 13400 |  | 10300 |  | 13600
| Ash | g/hr | nd | 2134.72 | nd | 2729.4 | nd | 2931.37
| Chlorine | g/hr | nd | 192.241 | nd | 144.24 | nd | 175.672
| Antimony | g/hr | nd | 3.023 | nd | 2.885 | nd | 3.057
| Arsenic | g/hr | nd | 0.202 | nd | 0.116 | nd | 0.228
| Barium | g/hr | nd | 0.121 | nd | 0.194 | nd | 0.093
| Beryllium | g/hr | nd | 0.015 | nd | 0.015 | nd | 0.015
| Cadmium | g/hr | nd | 0.015 | nd | 0.015 | nd | 0.015
| Chromium | g/hr |  | 0.336 |  | 0.258 |  | 0.256
| Lead | g/hr | nd | 2.281 | nd | 2.164 | nd | 2.316
| Mercury | g/hr | nd | 0.025 | nd | 0.032 | nd | 0.066
| Silver | g/hr | nd | 0.342 | nd | 0.332 | nd | 0.335
| Thallium | g/hr | nd | 13.168 | nd | 12.837 | nd | 13.175
| Stack Gas Flowrate | dscfm |  | 15473 |  | 15776 |  | 15221 |  | 15490
| Oxygen | % |  | 4 |  | 4 |  | 3.4 |  | 3.8
| Thermal Feedrate | MMBtu/hr |  | 49.217 |  | 39.3952 |  | 47.3359 |  | 45.316 |  | 49.217 |  | 39.3952 |  | 47.3359 |  | 45.316
| Estimated Firing Rate | MMBtu/hr |  | 83.5051 |  | 85.1403 |  | 85.0443 |  | 84.5803
Feedrate MTEC Calculations
| Ash | mg/dscm | 100 | 66.9126 | 100 | 83.9096 | 100 | 90.2205 | 100 | 80.3476 | 100 | 33.4563 | 100 | 41.9548 | 100 | 45.1102 | 100 | 80.3476
| Chlorine | ug/dscm | 100 | 6025.7751 | 100 | 4434.3528 | 100 | 5406.7594 | 100 | 5288.9624 | 100 | 6025.7751 | 100 | 4434.3528 | 100 | 5406.7594 | 100 | 5288.9624
| Antimony | ug/dscm | 100 | 94.7556 | 100 | 88.6932 | 100 | 94.0871 | 100 | 92.512 | 100 | 94.7556 | 100 | 88.6932 | 100 | 94.0871 | 100 | 92.512
| Arsenic | ug/dscm | 100 | 6.3317 | 100 | 3.5662 | 100 | 7.0173 | 100 | 5.6384 | 100 | 6.3317 | 100 | 3.5662 | 100 | 7.0173 | 100 | 5.6384
| Barium | ug/dscm | 100 | 3.7927 | 100 | 5.9641 | 100 | 2.8623 | 100 | 4.2064 | 100 | 3.7927 | 100 | 5.9641 | 100 | 2.8623 | 100 | 4.2064
| Beryllium | ug/dscm | 100 | 0.47017 | 100 | 0.46114 | 100 | 0.46166 | 100 | 0.46433 | 100 | 0.47017 | 100 | 0.46114 | 100 | 0.46166 | 100 | 0.46433
| Cadmium | ug/dscm | 100 | 0.47017 | 100 | 0.46114 | 100 | 0.46166 | 100 | 0.46433 | 100 | 0.47017 | 100 | 0.46114 | 100 | 0.46166 | 100 | 0.46433
| Chromium | ug/dscm |  | 10.5319 |  | 7.9317 |  | 7.8791 |  | 8.7809 |  | 5.2659 |  | 3.9658 |  | 3.9395 |  | 8.7809
| Lead | ug/dscm | 100 | 71.4977 | 100 | 66.5276 | 100 | 71.2809 | 100 | 69.7687 | 100 | 71.4977 | 100 | 66.5276 | 100 | 71.2809 | 100 | 69.7687
| Mercury | ug/dscm | 100 | 0.78362 | 100 | 0.98377 | 100 | 2.0313 | 100 | 1.2662 | 100 | 0.39181 | 100 | 0.49189 | 100 | 1.0157 | 100 | 1.2662
| Silver | ug/dscm | 100 | 10.72 | 100 | 10.2066 | 100 | 10.3105 | 100 | 10.4124 | 100 | 10.72 | 100 | 10.2066 | 100 | 10.3105 | 100 | 10.4124
| Thallium | ug/dscm | 100 | 412.7497 | 100 | 394.6463 | 100 | 405.4946 | 100 | 404.2969 | 100 | 412.7497 | 100 | 394.6463 | 100 | 405.4946 | 100 | 404.2969
| SVM | ug/dscm | 100 | 71.9679 | 100 | 66.9887 | 100 | 71.7425 | 100 | 70.2331 | 100 | 71.9679 | 100 | 66.9887 | 100 | 71.7425 | 100 | 70.2331
| LVM | ug/dscm | 28.3427 | 23.9986 | 25.709 | 15.665 | 32.4058 | 23.0791 | 29.1797 | 20.9142 | 28.3427 | 23.9986 | 25.709 | 15.665 | 32.4058 | 23.0791 | 29.1797 | 20.9142
* | 1017C3 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  | HW |  | HW |  | HW |  | HW |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | Waste Liquid and Combined PA Residues |  | Waste Liquid and Combined PA Residues |  | Waste Liquid and Combined PA Residues |  | Waste Liquid and Combined PA Residues |  | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 2041 |  | 2071 |  | 1876
| Heating Value | Btu/lb |  | 13400 |  | 10400 |  | 14400
| Ash | g/hr |  | 2315.2 |  | 2819.1 |  | 2808.9
| Chlorine | g/hr | nd | 92.6 | nd | 93.97 | nd | 85.11
| Antimony | g/hr | nd | 1.852 | nd | 1.879 | nd | 1.702
| Arsenic | g/hr |  | 0.157 |  | 0.16 | nd | 0.068
| Barium | g/hr | nd | 0.046 | nd | 0.047 | nd | 0.043
| Beryllium | g/hr | nd | 0.009 | nd | 0.009 | nd | 0.009
| Cadmium | g/hr |  | 0.009 |  | 0.009 | nd | 0.009
| Chromium | g/hr |  | 0.056 |  | 0.028 |  | 0.043
| Lead | g/hr | nd | 1.389 | nd | 1.41 | nd | 1.277
| Mercury | g/hr |  | 0.083 | nd | 0.009 | nd | 0.009
| Silver | g/hr | nd | 0.204 | nd | 0.216 | nd | 0.196
| Thallium | g/hr | nd | 8.15 | nd | 8.363 | nd | 7.49
| Stack Gas Flowrate | dscfm |  | 15221 |  | 15158 |  | 14879 |  | 15086
| Oxygen | % |  | 3.4 |  | 3.4 |  | 3.6 |  | 3.4667
| Thermal Feedrate | MMBtu/hr |  | 27.3494 |  | 21.5384 |  | 27.0144 |  | 25.3007 |  | 27.3494 |  | 21.5384 |  | 27.0144 |  | 25.3007
| Estimated Firing Rate | MMBtu/hr | [7 empty] | 83.9708
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 71.2563 |  | 87.1257 |  | 89.4548 |  | 82.6123 |  | 35.6281 |  | 43.5628 |  | 44.7274 |  | 82.6123
| Chlorine | ug/dscm | 100 | 2850.0041 | 100 | 2904.1899 | 100 | 2710.4909 | 100 | 2821.5616 | 100 | 2850.0041 | 100 | 2904.1899 | 100 | 2710.4909 | 100 | 2821.5616
| Antimony | ug/dscm | 100 | 57.0001 | 100 | 58.0714 | 100 | 54.2034 | 100 | 56.425 | 100 | 57.0001 | 100 | 58.0714 | 100 | 54.2034 | 100 | 56.425
| Arsenic | ug/dscm |  | 4.8321 |  | 4.9449 | 100 | 2.1656 | 18.1334 | 3.9809 |  | 2.416 |  | 2.4724 | 100 | 1.0828 | 18.1334 | 3.9809
| Barium | ug/dscm | 100 | 1.4158 | 100 | 1.4526 | 100 | 1.3694 | 100 | 1.4126 | 100 | 1.4158 | 100 | 1.4526 | 100 | 1.3694 | 100 | 1.4126
| Beryllium | ug/dscm | 100 | 0.277 | 100 | 0.27815 | 100 | 0.28662 | 100 | 0.28059 | 100 | 0.277 | 100 | 0.27815 | 100 | 0.28662 | 100 | 0.28059
| Cadmium | ug/dscm |  | 0.277 |  | 0.27815 | 100 | 0.28662 | 34.0499 | 0.28059 |  | 0.1385 |  | 0.13907 | 100 | 0.14331 | 34.0499 | 0.28059
| Chromium | ug/dscm |  | 1.7235 |  | 0.86535 |  | 1.3694 |  | 1.3194 |  | 0.86177 |  | 0.43268 |  | 0.68471 |  | 1.3194
| Lead | ug/dscm | 100 | 42.7501 | 100 | 43.5768 | 100 | 40.6685 | 100 | 42.3318 | 100 | 42.7501 | 100 | 43.5768 | 100 | 40.6685 | 100 | 42.3318
| Mercury | ug/dscm |  | 2.5545 | 100 | 0.27815 | 100 | 0.28662 | 18.1057 | 1.0398 |  | 1.2773 | 100 | 0.13907 | 100 | 0.14331 | 18.1057 | 1.0398
| Silver | ug/dscm | 100 | 6.2786 | 100 | 6.6756 | 100 | 6.242 | 100 | 6.3987 | 100 | 6.2786 | 100 | 6.6756 | 100 | 6.242 | 100 | 6.3987
| Thallium | ug/dscm | 100 | 250.8373 | 100 | 258.4627 | 100 | 238.5334 | 100 | 249.2778 | 100 | 250.8373 | 100 | 258.4627 | 100 | 238.5334 | 100 | 249.2778
| SVM | ug/dscm | 99.3562 | 43.0271 | 99.3658 | 43.8549 | 99.3002 | 40.9551 | 99.3415 | 42.6124 | 99.3562 | 43.0271 | 99.3658 | 43.8549 | 99.3002 | 40.9551 | 99.3415 | 42.6124
| LVM | ug/dscm | 4.0541 | 6.8326 | 4.5685 | 6.0884 | 7.5 | 3.8216 | 5.0277 | 5.5809 | 4.0541 | 6.8326 | 4.5685 | 6.0884 | 7.5 | 3.8216 | 5.0277 | 5.5809
* | 1017C4 |  |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  | F1 |  | F1 |  | F1 |  | F1 |  | F2 |  | F2 |  | F2 |  | F2 | [9 empty] | F3 |  | F3 |  | F3 |  | F3
| Feed Class |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | [9 empty] | Total |  | Total |  | Total |  | Total
| Feed Class 2 | [18 empty] | HW |  | HW |  | HW |  | HW |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  | PA Residue |  | PA Residue |  | PA Residue |  | PA Residue |  | 2-EH Waste Liq |  | 2-EH Waste Liq |  | 2-EH Waste Liq |  | 2-EH Waste Liq | [9 empty] | Total |  | Total |  | Total |  | Total
| Feed Rate | lb/hr |  | 693.7224 |  | 692.7228 |  | 694.2222 |  | 693.5558 |  | 869.652 |  | 868.6524 |  | 868.6524 |  | 868.9856
| Heating Value | Btu/lb |  | 11418 |  | 11321 |  | 11308 |  | 11349 |  | 16014 |  | 15866 |  | 15922 |  | 15934
| Ash | g/hr |  | 0.62435 |  | 0.62345 |  | 0.6248 |  | 0.6242 | nd | 0.043483 | nd | 0.043433 | nd | 0.043433 |  | 0.043449
| Chlorine | g/hr | nd | 0.069372 | nd | 0.069272 | nd | 0.069422 |  | 0.069356 | nd | 0.086965 | nd | 0.086865 | nd | 0.7961 |  | 0.32331
| Antimony | g/hr |  | 0.28006 |  | 0.24195 | nd | 0.23303 |  | 0.25168 |  | 0.59171 |  | 0.43342 | nd | 0.30734 |  | 0.44416
| Arsenic | g/hr |  | 0.66081 |  | 0.47133 |  | 0.59831 |  | 0.57682 |  | 1.6568 |  | 1.7731 |  | 1.3791 |  | 1.603
| Barium | g/hr |  | 0.024544 | nd | 0.059702 |  | 0.044086 |  | 0.042777 |  | 0.043392 |  | 0.039402 |  | 0.047282 |  | 0.043359
| Beryllium | g/hr |  | 0.022656 |  | 0.016025 | nd | 0.010392 |  | 0.016358 |  | 0.039447 |  | 0.055163 |  | 0.032704 |  | 0.042438
| Cadmium | g/hr |  | 0.044054 |  | 0.0053417 | nd | 0.021098 |  | 0.023498 |  | 0.10651 |  | 0.074864 |  | 0.055163 |  | 0.078845
| Chromium | g/hr |  | 0.18251 |  | 0.62844 |  | 0.56682 |  | 0.45926 |  | 0.21696 | nd | 0.059103 |  | 0.13397 |  | 0.13668
| Lead | g/hr |  | 0.50348 |  | 0.40848 |  | 0.53533 |  | 0.48243 |  | 0.51282 |  | 0.74864 |  | 0.51223 |  | 0.59123
| Mercury | g/hr |  | 0.0044054 | nd | 0.0050275 | nd | 0.0050384 |  | 0.0048238 |  | 0.029586 |  | 0.043342 |  | 0.03034 |  | 0.034422
| Silver | g/hr |  | 0.081815 |  | 0.15083 |  | 0.097619 |  | 0.11009 |  | 0.26035 | nd | 0.063043 |  | 0.14185 |  | 0.15508
| Thallium | g/hr | nd | 0.28321 | nd | 1.8853 | nd | 2.2043 |  | 1.4576 | nd | 2.7613 | nd | 2.7581 | nd | 2.7581 |  | 2.7592
0
| Stack Gas Flowrate | dscfm |  | 11197 |  | 9986 |  | 10402 |  | 10528.3333 |  | 11197 |  | 9986 |  | 10402 |  | 10528.3333 | [9 empty] | 11197 |  | 9986 |  | 10402 |  | 10528.3333
| Oxygen | % |  | 4 |  | 4 |  | 4.6 |  | 4.2 |  | 4 |  | 4 |  | 4.6 |  | 4.2 | [9 empty] | 4 |  | 4 |  | 4.6 |  | 4.2
[30 empty] | 4 |  | 0 |  | 0
| Thermal Feedrate | MMBtu/hr |  | 7.9209 |  | 7.8423 |  | 7.8503 |  | 7.8712 |  | 13.9266 |  | 13.782 |  | 13.8307 |  | 13.8464 |  | 21.8475 |  | 21.6244 |  | 21.6809 |  | 21.7176 |  | 21.8475 |  | 21.6244 |  | 21.6809 |  | 21.7176
Feedrate MTEC Calculations
| Ash | mg/dscm |  | 0.027044 |  | 0.03028 |  | 0.030197 |  | 0.029174 | 100 | 0.00094173 | 100 | 0.0010547 | 100 | 0.0010496 | 100 | 0.0010153 | 3.365 | 0.027986 | 3.366 | 0.031334 | 3.359 | 0.031247 | 3.3633 | 0.030189 | 3.365 | 0.027986 | 3.366 | 0.031334 | 3.359 | 0.031247 | 3.3633 | 0.030189
| Chlorine | ug/dscm | 100 | 3.0049 | 100 | 3.3644 | 100 | 3.3553 | 100 | 3.2415 | 100 | 1.8835 | 100 | 2.1094 | 100 | 19.2383 | 100 | 7.7437 | 100 | 4.8883 | 100 | 5.4738 | 100 | 22.5936 | 100 | 10.9853 | 100 | 4.8883 | 100 | 5.4738 | 100 | 22.5936 | 100 | 10.9853
| Antimony | ug/dscm |  | 12.1308 |  | 11.751 | 100 | 11.2625 | 32.0464 | 11.7147 |  | 25.6301 |  | 21.0505 | 100 | 7.427 | 13.7264 | 18.0358 | 0 | 37.7608 | 0 | 32.8014 | 100 | 18.6894 | 20.9402 | 29.7506 | 0 | 37.7608 | 0 | 32.8014 | 100 | 18.6894 | 20.9402 | 29.7506
| Arsenic | ug/dscm |  | 28.6232 |  | 22.8915 |  | 28.9171 |  | 26.8106 |  | 71.7642 |  | 86.1155 |  | 66.6525 |  | 74.8441 | 0 | 100.3873 | 0 | 109.007 | 0 | 95.5697 | 0 | 101.6547 | 0 | 100.3873 | 0 | 109.007 | 0 | 95.5697 | 0 | 101.6547
| Barium | ug/dscm |  | 1.0631 | 100 | 2.8996 |  | 2.1307 | 47.5852 | 2.0312 |  | 1.8795 |  | 1.9137 |  | 2.2852 |  | 2.0261 | 0 | 2.9427 | 60.2416 | 4.8133 | 0 | 4.416 | 23.8219 | 4.0573 | 0 | 2.9427 | 60.2416 | 4.8133 | 0 | 4.416 | 23.8219 | 4.0573
| Beryllium | ug/dscm |  | 0.98137 |  | 0.77831 | 100 | 0.50224 | 22.2043 | 0.75397 |  | 1.7087 |  | 2.6791 |  | 1.5806 |  | 1.9895 | 0 | 2.69 | 0 | 3.4575 | 24.1132 | 2.0829 | 6.1023 | 2.7435 | 0 | 2.69 | 0 | 3.4575 | 24.1132 | 2.0829 | 6.1023 | 2.7435
| Cadmium | ug/dscm |  | 1.9082 |  | 0.25944 | 100 | 1.0197 | 31.9923 | 1.0625 |  | 4.6134 |  | 3.636 |  | 2.6661 |  | 3.6385 | 0 | 6.5216 | 0 | 3.8954 | 27.6658 | 3.6858 | 7.2305 | 4.701 | 0 | 6.5216 | 0 | 3.8954 | 27.6658 | 3.6858 | 7.2305 | 4.701
| Chromium | ug/dscm |  | 7.9054 |  | 30.522 |  | 27.3952 |  | 21.9409 |  | 9.3977 | 100 | 1.4353 |  | 6.4748 | 8.2926 | 5.7693 | 0 | 17.3031 | 4.4912 | 31.9572 | 0 | 33.87 | 1.7265 | 27.7101 | 0 | 17.3031 | 4.4912 | 31.9572 | 0 | 33.87 | 1.7265 | 27.7101
| Lead | ug/dscm |  | 21.8081 |  | 19.8393 |  | 25.8732 |  | 22.5069 |  | 22.2127 |  | 36.3599 |  | 24.7567 |  | 27.7764 | 0 | 44.0208 | 0 | 56.1992 | 0 | 50.6299 | 0 | 50.2833 | 0 | 44.0208 | 0 | 56.1992 | 0 | 50.6299 | 0 | 50.2833
| Mercury | ug/dscm |  | 0.19082 | 100 | 0.24418 | 100 | 0.24351 | 71.8764 | 0.22617 |  | 1.2815 |  | 2.105 |  | 1.4664 |  | 1.6176 | 0 | 1.4723 | 10.3939 | 2.3492 | 14.2416 | 1.7099 | 8.8167 | 1.8438 | 0 | 1.4723 | 10.3939 | 2.3492 | 14.2416 | 1.7099 | 8.8167 | 1.8438
| Silver | ug/dscm |  | 3.5438 |  | 7.3253 |  | 4.7181 |  | 5.1957 |  | 11.2772 | 100 | 1.5309 |  | 6.8557 | 7.7856 | 6.5546 | 0 | 14.821 | 17.2867 | 8.8562 | 0 | 11.5737 | 4.343 | 11.7503 | 0 | 14.821 | 17.2867 | 8.8562 | 0 | 11.5737 | 4.343 | 11.7503
| Thallium | ug/dscm | 100 | 12.2671 | 100 | 91.5659 | 100 | 106.5367 | 100 | 70.1232 | 100 | 59.8035 | 100 | 66.9787 | 100 | 66.6525 | 100 | 64.4783 | 100 | 72.0705 | 100 | 158.5446 | 100 | 173.1892 | 100 | 134.6015 | 100 | 72.0705 | 100 | 158.5446 | 100 | 173.1892 | 100 | 134.6015
| SVM | ug/dscm |  | 23.7163 |  | 20.0987 |  | 26.8929 |  | 23.5693 |  | 26.8261 |  | 39.9959 |  | 27.4228 |  | 31.4149 |  | 50.5425 |  | 60.0946 |  | 54.3157 |  | 54.9842 |  | 50.5425 |  | 60.0946 |  | 54.3157 |  | 54.9842
| LVM | ug/dscm |  | 37.51 |  | 54.1917 |  | 56.8145 |  | 49.5054 |  | 82.8705 |  | 90.2299 |  | 74.708 |  | 82.6028 |  | 120.3805 |  | 144.4217 |  | 131.5225 |  | 132.1082 |  | 120.3805 |  | 144.4217 |  | 131.5225 |  | 132.1082

## process
Process Information
1017C1
None reported
1017C2
None reported
1017C3
None reported