## 25F nomo
Covington-Creston (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 015
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6648.0687
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 487.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1573.06 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1026.47 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1785.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1573.06 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2052.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 712.3 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2621.91 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1256.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3118.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1785.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1026.47 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1070 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1256.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1581.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1581.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2052.69 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2192.76 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1630.45 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2649.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2192.76 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 487.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 2621.91 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 712.3 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2159.35 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1070 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2649.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1630.45 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3118.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2159.35 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Covington-Creston (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 015
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6330.3613
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 966.39 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1967.83 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1548.82 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2208.84 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1967.83 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2518.51 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1182.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3117.76 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1731.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3550.03 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2208.84 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1548.82 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1506.75 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1731.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2059.32 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2059.32 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2518.51 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2618.22 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2087.29 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3067.33 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2618.22 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 966.39 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3117.76 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1182.59 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2592.32 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1506.75 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3067.33 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2087.29 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3550.03 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 2592.32 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Covington-Creston (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 015
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6055.25
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1376.63 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2405.36 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1867.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2599.78 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2405.36 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2901.5 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1630.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3447.9 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2169.28 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3003.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2599.78 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1867.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1951.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2169.28 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2477.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2477.71 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2901.5 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2979.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2478.61 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3088.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2979.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1376.63 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3447.9 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1630.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2976.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1951.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3088.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2478.61 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3003.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2976.96 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Covington-Creston (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 015
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4979.4253
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2780.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2825.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2806.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2920.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2825.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2854.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2881.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3309.76 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 460 | 2901.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1831.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2920.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2806.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3050.98 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2901.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3067.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3067.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2854.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3145.9 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3306.99 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1938.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3145.9 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2780.21 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3309.76 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2881.71 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 2007.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3050.98 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1938.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3306.99 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1400 | 775 | 1831.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2007.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Covington-Creston (SCL) #1 230kV Line(COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 015
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4635.3847
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2658.09 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2450.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2675.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2567.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2450.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2776.78 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2533.59 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3077.25 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2544.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1596.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2567.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2675.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2733.99 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2544.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2743.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2743.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2776.78 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3058.99 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3037.65 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1697 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3058.99 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2658.09 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3077.25 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2533.59 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1805.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2733.99 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1697 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3037.65 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1596.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1805.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Covington-Creston (SCL) #1 230kV Line(COV-CRES BYP @ COV)
G0 | 487.96 | 966.39 | 1376.63 | 2780.21 | 2658.09
G1 | 1026.47 | 1548.82 | 1867.9 | 2806.33 | 2675.32 | Season/Year: | WINTER 2009
G2 | 1573.06 | 1967.83 | 2405.36 | 2825.64 | 2450.2 | Direction: | South-to-North (SN)
G3 | 712.3 | 1182.59 | 1630.7 | 2881.71 | 2533.59 | Case Loads: | Heavy Loads
G4 | 1256.9 | 1731.41 | 2169.28 | 2901.86 | 2544.61 | Outage: | 015
G5 | 1785.65 | 2208.84 | 2599.78 | 2920.19 | 2567.39 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1070 | 1506.75 | 1951.37 | 3050.98 | 2733.99 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1581.68 | 2059.32 | 2477.71 | 3067.72 | 2743.67 | Study Person: | FRP9899
G8 | 2052.69 | 2518.51 | 2901.5 | 2854.02 | 2776.78 | Source: | 015WINTER09v1SNH
G9 | 1630.45 | 2087.29 | 2478.61 | 3306.99 | 3037.65
G10 | 2192.76 | 2618.22 | 2979.87 | 3145.9 | 3058.99
G11 | 2621.91 | 3117.76 | 3447.9 | 3309.76 | 3077.25
G12 | 2159.35 | 2592.32 | 2976.96 | 2007.41 | 1805.5
G13 | 2649.96 | 3067.33 | 3088.7 | 1938.96 | 1697
G14 | 3118.71 | 3550.03 | 3003.34 | 1831.65 | 1596.4
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL
| FULL | FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 015 | Covington-Creston (SCL) #1 230kV Line(COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6648.0687 | 487.96 | 1026.47 | 1573.06 | 712.3 | 1256.9 | 1785.65 | 1070 | 1581.68 | 2052.69 | 1630.45 | 2192.76 | 2621.91 | 2159.35 | 2649.96 | 3118.71
35F | 6330.3613 | 966.39 | 1548.82 | 1967.83 | 1182.59 | 1731.41 | 2208.84 | 1506.75 | 2059.32 | 2518.51 | 2087.29 | 2618.22 | 3117.76 | 2592.32 | 3067.33 | 3550.03
45F | 6055.25 | 1376.63 | 1867.9 | 2405.36 | 1630.7 | 2169.28 | 2599.78 | 1951.37 | 2477.71 | 2901.5 | 2478.61 | 2979.87 | 3447.9 | 2976.96 | 3088.7 | 3003.34
60F | 4979.4253 | 2780.21 | 2806.33 | 2825.64 | 2881.71 | 2901.86 | 2920.19 | 3050.98 | 3067.72 | 2854.02 | 3306.99 | 3145.9 | 3309.76 | 2007.41 | 1938.96 | 1831.65
70F | 4635.3847 | 2658.09 | 2675.32 | 2450.2 | 2533.59 | 2544.61 | 2567.39 | 2733.99 | 2743.67 | 2776.78 | 3037.65 | 3058.99 | 3077.25 | 1805.5 | 1697 | 1596.4

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 487.03 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 545.17 | 545.14 | 6668.16 | 487.96 | -469.3 | FULL
G1 | 1026.42 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 544.44 | 544.49 | 6611.87 | 1026.47 | -748.35 | FULL
G2 | 1571.18 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 543.69 | 543.78 | 6641.52 | 1573.06 | -1034.13 | FULL
G3 | 711.83 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 545.25 | 545.39 | 6669.25 | 712.3 | -528.25 | FULL
G4 | 1256.73 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 544.91 | 544.83 | 6613.65 | 1256.9 | -816.15 | FULL
G5 | 1785.4 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 549.91 | 549.81 | 6641.11 | 1785.65 | -1094.97 | FULL
G6 | 1069.56 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 546.35 | 546.31 | 6670.65 | 1070 | -617.26 | FULL
G7 | 1581.57 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 545.33 | 545.25 | 6615.95 | 1581.68 | -888.48 | FULL
G8 | 2052.61 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 540.49 | 540.52 | 6642.1 | 2052.69 | -1133.71 | FULL
G9 | 1630.41 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 546.24 | 546.16 | 6678.95 | 1630.45 | -731.79 | FULL
G10 | 2192.78 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 551.11 | 551.15 | 6624.59 | 2192.76 | -1026.91 | FULL
G11 | 2622.18 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 540.76 | 540.8 | 6652.95 | 2621.91 | -1255.61 | FULL
G12 | 2159.34 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 546.22 | 546.27 | 6689.04 | 2159.35 | -883.07 | FULL
G13 | 2650.1 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 541.17 | 541.18 | 6634.51 | 2649.96 | -1144.26 | FULL
G14 | 3119.09 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 540.45 | 540.4 | 6666.73 | 3118.71 | -1391.61 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 965.96 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 531.51 | 531.54 | 6346.1 | 966.39 | -707.83 | FULL
G1 | 1548.87 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 532.09 | 532.03 | 6294.35 | 1548.82 | -1011.46 | FULL
G2 | 1967.68 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 527.45 | 527.35 | 6323.02 | 1967.83 | -1228.27 | FULL
G3 | 1182.28 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 531.98 | 531.87 | 6347.34 | 1182.59 | -767.8 | FULL
G4 | 1731.64 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 531.86 | 531.97 | 6295.4 | 1731.41 | -1054.92 | FULL
G5 | 2208.87 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 527.92 | 527.81 | 6325.75 | 2208.84 | -1300.48 | FULL
G6 | 1506.47 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 531.94 | 531.99 | 6349.64 | 1506.75 | -834.56 | FULL
G7 | 2059.4 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 531.98 | 531.89 | 6298.26 | 2059.32 | -1133.75 | FULL
G8 | 2518.59 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 528.2 | 528.12 | 6329.12 | 2518.51 | -1360.05 | FULL
G9 | 2087.34 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 532.22 | 532.27 | 6359.68 | 2087.29 | -963.66 | FULL
G10 | 2617.93 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 529 | 529.02 | 6307.87 | 2618.22 | -1243 | FULL
G11 | 3118 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 528.52 | 528.61 | 6342.25 | 3117.76 | -1501.16 | FULL
G12 | 2592.48 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 532.01 | 531.83 | 6370.73 | 2592.32 | -1099.89 | FULL
G13 | 3067.32 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 528.44 | 528.48 | 6318.42 | 3067.33 | -1360.36 | FULL
G14 | 3551.04 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3516.44 | 3519.26 | 6347.49 | 3550.03 | -1605.97 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1376.68 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 518.92 | 518.88 | 6074.06 | 1376.63 | -935.5 | FULL
G1 | 1868.04 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 512.73 | 514.31 | 6022.2 | 1867.9 | -1182.23 | FULL
G2 | 2405.65 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.67 | -486.9 | -484.43 | 6050.55 | 2405.36 | -1455.75 | CTG_FAIL_IN_FULL
G3 | 1630.82 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 519.48 | 519.39 | 6076.72 | 1630.7 | -1005.44 | FULL
G4 | 2168.72 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 522.57 | 522.5 | 6026.1 | 2169.28 | -1291.62 | FULL
G5 | 2600.02 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 515.17 | 514.27 | 6056.2 | 2599.78 | -1523.08 | FULL
G6 | 1951.74 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 519.54 | 519.49 | 6079.69 | 1951.37 | -1069.83 | FULL
G7 | 2477.7 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 524.13 | 524.08 | 6028.52 | 2477.71 | -1351.2 | FULL
G8 | 2901.86 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 515.27 | 515.23 | 6059.86 | 2901.5 | -1567.06 | FULL
G9 | 2478.59 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 522.32 | 522.64 | 6088.91 | 2478.61 | -1175.72 | FULL
G10 | 2980.02 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 515.75 | 515.78 | 6038.78 | 2979.87 | -1435.81 | FULL
G11 | 3448.02 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2534.62 | -2534.49 | 6063.53 | 3447.9 | -1686.96 | CTG_FAIL_IN_FULL
G12 | 2977.2 | Branch COVINGTN (40303) TO DUWAMISH (46423) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 3.75 | 519.31 | 519.25 | 6101.04 | 2976.96 | -1323.78 | FULL
G13 | 3089.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -435.75 | -435.72 | 6027.98 | 3088.7 | -1344.11 | FULL
G14 | 3003.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -436.08 | -435.87 | 6034.61 | 3003.34 | -1264.81 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2780.64 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2405.66 | -2405.29 | 5037.96 | 2780.21 | -1632.56 | CTG_FAIL_IN_FULL
G1 | 2806.31 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2409.38 | -2409.12 | 4966.2 | 2806.33 | -1611.29 | CTG_FAIL_IN_FULL
G2 | 2826.89 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2411.55 | -2410.7 | 4977.82 | 2825.64 | -1593.78 | CTG_FAIL_IN_FULL
G3 | 2882.1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2411.02 | -2410.75 | 5034.5 | 2881.71 | -1638.37 | CTG_FAIL_IN_FULL
G4 | 2901.8 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2409.87 | -2409.57 | 4964.07 | 2901.86 | -1603.7 | CTG_FAIL_IN_FULL
G5 | 2920.67 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2410.79 | -2410.07 | 4975.51 | 2920.19 | -1585.49 | CTG_FAIL_IN_FULL
G6 | 3051.48 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2400.19 | -2400.04 | 5032.28 | 3050.98 | -1618.72 | CTG_FAIL_IN_FULL
G7 | 3068.15 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2391.12 | -2390.4 | 4962.73 | 3067.72 | -1584.39 | CTG_FAIL_IN_FULL
G8 | 2854.49 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2218.04 | -2219.57 | 4967.97 | 2854.02 | -1417.4 | FULL
G9 | 3307.39 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3277.4 | 3277.96 | 5030.25 | 3306.99 | -1541.21 | FULL
G10 | 3146.45 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2221.81 | -2220.84 | 4956.98 | 3145.9 | -1419.8 | FULL
G11 | 3310.17 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3280.68 | 3277.96 | 4971.18 | 3309.76 | -1481.5 | FULL
G12 | 2007.44 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -424.01 | -423.91 | 4980.94 | 2007.41 | -628.68 | FULL
G13 | 1941.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -426.42 | -426.32 | 4910.6 | 1938.96 | -556.74 | FULL
G14 | 1831.54 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -425.4 | -425.35 | 4922.39 | 1831.65 | -462.78 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2657.99 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2298.24 | -2297.91 | 4693.02 | 2658.09 | -1517.07 | CTG_FAIL_IN_FULL
G1 | 2675.68 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.02 | -2297.34 | -2296.67 | 4623.14 | 2675.32 | -1496.57 | CTG_FAIL_IN_FULL
G2 | 2452.39 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2138.09 | -2136.71 | 4628.76 | 2450.2 | -1346.67 | FULL
G3 | 2533.79 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2146.39 | -2147.3 | 4684.48 | 2533.59 | -1389.56 | FULL
G4 | 2544.91 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2136.23 | -2137.85 | 4615.87 | 2544.61 | -1358.13 | FULL
G5 | 2566.79 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2149.36 | -2150.64 | 4626.18 | 2567.39 | -1345.45 | FULL
G6 | 2735.55 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2148.44 | -2146.42 | 4683.87 | 2733.99 | -1377.93 | FULL
G7 | 2746.11 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2142.68 | -2143.28 | 4614.14 | 2743.67 | -1353.21 | FULL
G8 | 2778.44 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2154.45 | -2152.73 | 4627.15 | 2776.78 | -1342.33 | FULL
G9 | 3039.78 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2140.8 | -2139.17 | 4685.66 | 3037.65 | -1347.08 | FULL
G10 | 3061.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2144.18 | -2142.77 | 4616.4 | 3058.99 | -1329.34 | FULL
G11 | 3079.57 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.43 | -2145.08 | -2143.53 | 4629.14 | 3077.25 | -1309.67 | FULL
G12 | 1805.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -424.83 | -424.78 | 4642.93 | 1805.5 | -481.05 | FULL
G13 | 1696.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -422.81 | -422.76 | 4573.49 | 1697 | -379.07 | FULL
G14 | 1597.09 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.56 | -423.22 | -423.17 | 4586.54 | 1596.4 | -295.7 | FULL
015WINTER09v1SNH