## 25F nomo
Sno-King-Maple Valley #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 045
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6662.19
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1025.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2106.33 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1684.2 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2281.71 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2106.33 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2573.75 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1173.62 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3096.54 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1671.76 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3523.56 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2281.71 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1684.2 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1423.56 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1671.76 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1939.86 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1939.86 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2573.75 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2691.73 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2040.46 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3108.9 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2691.73 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1025.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3096.54 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1173.62 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2469.35 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1423.56 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3108.9 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2040.46 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3523.56 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2469.35 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Sno-King-Maple Valley #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 045
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6332.1267
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1074.1 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2251.81 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1655.86 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2420.4 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2251.81 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2712.74 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1306.04 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3232.49 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1816.28 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3575.45 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2420.4 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1655.86 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1566.89 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1816.28 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2091.55 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2091.55 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2712.74 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2822.13 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2065.16 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3250.26 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2822.13 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1074.1 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3232.49 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1306.04 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2551.36 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1566.89 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3250.26 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2065.16 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3575.45 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 2551.36 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Sno-King-Maple Valley #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 045
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6045.1693
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1061.98 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2287.74 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1724.29 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2243.59 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2287.74 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2774.76 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1270.87 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3267.32 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1903.75 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3019.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2243.59 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1724.29 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1583.86 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1903.75 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2199.44 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2199.44 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2774.76 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2702.69 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2139.64 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3096.31 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2702.69 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1061.98 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3267.32 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1270.87 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2601.47 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1583.86 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3096.31 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2139.64 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 3019.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2601.47 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Sno-King-Maple Valley #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 045
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4968.4373
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1751.67 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2818.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2338.1 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2919.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2818.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2849.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1891 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3307.83 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 460 | 2519.57 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1816.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2919.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2338.1 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2210.71 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2519.57 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2799.96 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2799.96 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2849.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3138.35 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 2777.43 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1928.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3138.35 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1751.67 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3307.83 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1891 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2005.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2210.71 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1928.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2777.43 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1816.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2005.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Sno-King-Maple Valley #1 or #2 230kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 045
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4631.172
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1941.4 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2442 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2426.99 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2580.75 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2442 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2783.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2112.97 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3085.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2545.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1576.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2580.75 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2426.99 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2431.95 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2545.02 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2761.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2761.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2783.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3064.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3037.56 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1684.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3064.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1941.4 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3085.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2112.97 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1799.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2431.95 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1684.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3037.56 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1576.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1799.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Sno-King-Maple Valley #1 or #2 230kV Line (COV-CRES BYP @ COV)
G0 | 1025.79 | 1074.1 | 1061.98 | 1751.67 | 1941.4
G1 | 1684.2 | 1655.86 | 1724.29 | 2338.1 | 2426.99 | Season/Year: | WINTER 2009
G2 | 2106.33 | 2251.81 | 2287.74 | 2818.92 | 2442 | Direction: | South-to-North (SN)
G3 | 1173.62 | 1306.04 | 1270.87 | 1891 | 2112.97 | Case Loads: | Heavy Loads
G4 | 1671.76 | 1816.28 | 1903.75 | 2519.57 | 2545.02 | Outage: | 045
G5 | 2281.71 | 2420.4 | 2243.59 | 2919.51 | 2580.75 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1423.56 | 1566.89 | 1583.86 | 2210.71 | 2431.95 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1939.86 | 2091.55 | 2199.44 | 2799.96 | 2761.84 | Study Person: | JGO7470
G8 | 2573.75 | 2712.74 | 2774.76 | 2849.38 | 2783.67 | Source: | 045WINTER09v1SNH
G9 | 2040.46 | 2065.16 | 2139.64 | 2777.43 | 3037.56
G10 | 2691.73 | 2822.13 | 2702.69 | 3138.35 | 3064.63
G11 | 3096.54 | 3232.49 | 3267.32 | 3307.83 | 3085.86
G12 | 2469.35 | 2551.36 | 2601.47 | 2005.47 | 1799.25
G13 | 3108.9 | 3250.26 | 3096.31 | 1928.72 | 1684.62
G14 | 3523.56 | 3575.45 | 3019.16 | 1816.72 | 1576.97
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 045 | Sno-King-Maple Valley #1 or #2 230kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6662.19 | 1025.79 | 1684.2 | 2106.33 | 1173.62 | 1671.76 | 2281.71 | 1423.56 | 1939.86 | 2573.75 | 2040.46 | 2691.73 | 3096.54 | 2469.35 | 3108.9 | 3523.56
35F | 6332.1267 | 1074.1 | 1655.86 | 2251.81 | 1306.04 | 1816.28 | 2420.4 | 1566.89 | 2091.55 | 2712.74 | 2065.16 | 2822.13 | 3232.49 | 2551.36 | 3250.26 | 3575.45
45F | 6045.1693 | 1061.98 | 1724.29 | 2287.74 | 1270.87 | 1903.75 | 2243.59 | 1583.86 | 2199.44 | 2774.76 | 2139.64 | 2702.69 | 3267.32 | 2601.47 | 3096.31 | 3019.16
60F | 4968.4373 | 1751.67 | 2338.1 | 2818.92 | 1891 | 2519.57 | 2919.51 | 2210.71 | 2799.96 | 2849.38 | 2777.43 | 3138.35 | 3307.83 | 2005.47 | 1928.72 | 1816.72
70F | 4631.172 | 1941.4 | 2426.99 | 2442 | 2112.97 | 2545.02 | 2580.75 | 2431.95 | 2761.84 | 2783.67 | 3037.56 | 3064.63 | 3085.86 | 1799.25 | 1684.62 | 1576.97

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1025.32 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 514.54 | 514.87 | 6683.59 | 1025.79 | -782.39 | FULL
G1 | 1683.59 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 535.02 | 534.93 | 6632.36 | 1684.2 | -1130.92 | CTG_FAIL_IN_FULL
G2 | 2106.4 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 536.68 | 536.64 | 6658.56 | 2106.33 | -1351.27 | CTG_FAIL_IN_FULL
G3 | 1173.55 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 14.09 | 499.05 | 499.27 | 6682.66 | 1173.62 | -805.41 | FULL
G4 | 1672 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 514.66 | 514.32 | 6626.99 | 1671.76 | -1056.71 | FULL
G5 | 2281.82 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 534.66 | 534.64 | 6658.05 | 2281.71 | -1384.25 | CTG_FAIL_IN_FULL
G6 | 1423.47 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 511.83 | 511.51 | 6681.99 | 1423.56 | -823.94 | FULL
G7 | 1939.86 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 14.09 | 512.6 | 512.2 | 6627.83 | 1939.86 | -1091.2 | FULL
G8 | 2574.8 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 534.8 | 534.52 | 6658.69 | 2573.75 | -1432.28 | CTG_FAIL_IN_FULL
G9 | 2040.38 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 516.91 | 517.15 | 6691.19 | 2040.46 | -969.58 | FULL
G10 | 2692.62 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 535.56 | 535.45 | 6639.1 | 2691.73 | -1320.87 | CTG_FAIL_IN_FULL
G11 | 3097.15 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 536.39 | 536.35 | 6667.15 | 3096.54 | -1531.38 | CTG_FAIL_IN_FULL
G12 | 2469.63 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 519.93 | 520.17 | 6697.69 | 2469.35 | -1073.2 | FULL
G13 | 3109.34 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 534.51 | 534.5 | 6647.33 | 3108.9 | -1410.87 | CTG_FAIL_IN_FULL
G14 | 3524.19 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 535.48 | 535.43 | 6679.67 | 3523.56 | -1620.56 | CTG_FAIL_IN_FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1073.68 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 496.32 | 496.58 | 6350.06 | 1074.1 | -773.84 | FULL
G1 | 1655.73 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 500.38 | 500 | 6297.49 | 1655.86 | -1077.09 | FULL
G2 | 2252.4 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 518.69 | 518.68 | 6329.54 | 2251.81 | -1385.39 | CTG_FAIL_IN_FULL
G3 | 1305.76 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 497.95 | 497.75 | 6350.94 | 1306.04 | -838.69 | FULL
G4 | 1816.3 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 502.05 | 501.68 | 6297.77 | 1816.28 | -1108.17 | FULL
G5 | 2420.55 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 517.18 | 517.16 | 6328.87 | 2420.4 | -1431.37 | CTG_FAIL_IN_FULL
G6 | 1566.73 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 498.94 | 498.65 | 6352.06 | 1566.89 | -872.73 | FULL
G7 | 2091.15 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 14.09 | 505.45 | 505.66 | 6298.77 | 2091.55 | -1145.88 | FULL
G8 | 2713.19 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 517.76 | 517.75 | 6330.01 | 2712.74 | -1480.52 | CTG_FAIL_IN_FULL
G9 | 2065.23 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 501.57 | 501.98 | 6358.36 | 2065.16 | -959.81 | FULL
G10 | 2822.31 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 518.53 | 518.46 | 6311.51 | 2822.13 | -1377.07 | CTG_FAIL_IN_FULL
G11 | 3232.83 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 517.65 | 517.59 | 6338.57 | 3232.49 | -1573.38 | CTG_FAIL_IN_FULL
G12 | 2551.51 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 498.61 | 498.95 | 6368.95 | 2551.36 | -1079 | FULL
G13 | 3250.48 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 519.85 | 519.81 | 6322.27 | 3250.26 | -1470.13 | CTG_FAIL_IN_FULL
G14 | 3576.29 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3542.92 | 3544.87 | 6346.73 | 3575.45 | -1617.18 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1061.56 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 14.22 | 462.54 | 462.2 | 6064.12 | 1061.98 | -749.96 | FULL
G1 | 1724.17 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 14.22 | 488.63 | 488.67 | 6013.05 | 1724.29 | -1100.97 | FULL
G2 | 2287.97 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 504.2 | 504.14 | 6044.73 | 2287.74 | -1402.93 | CTG_FAIL_IN_FULL
G3 | 1270.5 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 14.22 | 479.73 | 479.36 | 6064.83 | 1270.87 | -805.07 | FULL
G4 | 1903.68 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 487.63 | 487.42 | 6013.87 | 1903.75 | -1130.98 | FULL
G5 | 2243.68 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 469.03 | 468.75 | 6039.18 | 2243.59 | -1310.13 | FULL
G6 | 1583.73 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 14.22 | 461.39 | 461.8 | 6066.65 | 1583.86 | -856.98 | FULL
G7 | 2199.26 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 489.78 | 489.9 | 6015.31 | 2199.44 | -1188.99 | FULL
G8 | 2774.84 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 503.5 | 503.44 | 6048.2 | 2774.76 | -1493.59 | CTG_FAIL_IN_FULL
G9 | 2139.39 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 488.12 | 487.86 | 6076.24 | 2139.64 | -978.29 | FULL
G10 | 2702.62 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 490.59 | 490.42 | 6023.55 | 2702.69 | -1272.99 | FULL
G11 | 3267.62 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.86 | 503.41 | 503.37 | 6055.59 | 3267.32 | -1564.98 | CTG_FAIL_IN_FULL
G12 | 2601.31 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 487.11 | 487.51 | 6086.25 | 2601.47 | -1095.3 | FULL
G13 | 3096.54 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 492.41 | 491.99 | 6029.98 | 3096.31 | -1351.1 | FULL
G14 | 3019.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.5 | -434.57 | -434.53 | 6035.99 | 3019.16 | -1272.63 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1752.84 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 452.85 | 452.59 | 4996.63 | 1751.67 | -1031.33 | FULL
G1 | 2337.58 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 14.22 | 469.99 | 469.82 | 4947.31 | 2338.1 | -1343.57 | FULL
G2 | 2819.37 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.15 | -2399.39 | -2400.37 | 4979.27 | 2818.92 | -1583.26 | CTG_FAIL_IN_FULL
G3 | 1890.86 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 14.22 | 445.54 | 445.71 | 4998.13 | 1891 | -1046.07 | FULL
G4 | 2518.9 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 14.22 | 471.42 | 471.68 | 4949.6 | 2519.57 | -1382.04 | FULL
G5 | 2919.97 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.15 | -2405.31 | -2404.55 | 4976.67 | 2919.51 | -1575.14 | CTG_FAIL_IN_FULL
G6 | 2210.35 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 451.8 | 451.97 | 5001.36 | 2210.71 | -1110 | FULL
G7 | 2801.65 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 14.22 | 471.13 | 471.55 | 4952.44 | 2799.96 | -1427.4 | FULL
G8 | 2849.77 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2223.79 | -2225.53 | 4967.78 | 2849.38 | -1423.89 | FULL
G9 | 2777.93 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 452.98 | 453.16 | 5012.12 | 2777.43 | -1236.76 | FULL
G10 | 3139.64 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2213.04 | -2215.1 | 4958.22 | 3138.35 | -1418.32 | FULL
G11 | 3308.33 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3278.87 | 3276.35 | 4971.67 | 3307.83 | -1482.15 | FULL
G12 | 2005.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.5 | -424.07 | -423.95 | 4981.74 | 2005.47 | -627.55 | FULL
G13 | 1931.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.5 | -426.28 | -426.26 | 4911.02 | 1928.72 | -548.77 | FULL
G14 | 1816.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.5 | -425.34 | -425.28 | 4922.6 | 1816.72 | -450.38 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1941.02 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.81 | 438.04 | 437.7 | 4665.97 | 1941.4 | -1110.29 | FULL
G1 | 2429.26 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2139.02 | -2138.12 | 4614.96 | 2426.99 | -1363.44 | FULL
G2 | 2443.9 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2125.66 | -2124.29 | 4629.63 | 2442 | -1344.23 | FULL
G3 | 2112.74 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 14.22 | 433.81 | 433.98 | 4667.48 | 2112.97 | -1149.72 | FULL
G4 | 2545.32 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2137.47 | -2138.99 | 4616.4 | 2545.02 | -1360.19 | FULL
G5 | 2580.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2161 | -2162.07 | 4627.11 | 2580.75 | -1353.37 | FULL
G6 | 2431.81 | Branch MAPLE VL (40689) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 14.22 | 449.33 | 449.06 | 4670.86 | 2431.95 | -1208.08 | FULL
G7 | 2764.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2171.27 | -2169.96 | 4614.42 | 2761.84 | -1372.96 | FULL
G8 | 2786.21 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2167.74 | -2166.54 | 4627 | 2783.67 | -1353.27 | FULL
G9 | 3037.86 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2149.22 | -2147.62 | 4684.75 | 3037.56 | -1360.61 | FULL
G10 | 3066.86 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2161.82 | -2161.2 | 4616.45 | 3064.63 | -1340.51 | FULL
G11 | 3088.09 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.57 | -2158.69 | -2156.66 | 4629.03 | 3085.86 | -1320.59 | FULL
G12 | 1799.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.5 | -424.83 | -424.68 | 4643.43 | 1799.25 | -475.76 | FULL
G13 | 1684.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.5 | -422.71 | -422.66 | 4573.63 | 1684.62 | -368.52 | FULL
G14 | 1577.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.5 | -423.1 | -423.06 | 4586.46 | 1576.97 | -279.24 | FULL
045WINTER09v1SNH