July 22, 1994

Contract # TW0592

SPECIAL SPECIFICATION

SECTION 15755

HEAT EXCHANGERS

Page

PART 1 - GENERAL

1.01 Description.	2

1.02Related Work.	2

1.03Quality Assurance.	2

1.04References.	2

1.05Submittals.	3

1.06 Delivery, Storage, and Handling.	3

1.07 Project/Site Conditions.	3

PART 2 - PRODUCTS

2.01Acceptable Manufacturers.	4

2.02 Ratings.	4

2.03 Shell-and-Tube Heat Exchangers.	6

2.04 Plate Heat Exchangers.	7

PART 3 - EXECUTION

3.01 Inspection.	8

3.02 Installation/Application/Erection.	8

3.03 Adjusting and Cleaning.	8

3.04 Commissioning..	8

3.05 Demonstration.	9

SPECIAL SPECIFICATION

SECTION 15755

HEAT EXCHANGERS

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This Section includes heat exchangers for mechanical systems.

1.02	RELATED WORK

A.  	Section 01300

B.  	Section 15010

C.  	Section 15250

D.  	Section 15995

1.03	QUALITY ASSURANCE

A.  	Manufacturer Qualifications:  Firm experienced in manufacturing heat exchangers similar to those indicated for this Project and that have a record of successful in-service performance.

B.  	Fabricate and stamp heat exchangers to comply with American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code, Section VIII, Division 1.

C.  	Provide completely fill-out ASME Form No. U-1 for each heat exchanger to be approved prior to shipping.

1.04	REFERENCES

A.  	ASME Boiler and Pressure Vessel Code, Section VIII, Division 1.

B.  	ASME Form No. U-1.

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15010, and Section 01300.

B.  	Submit a completed ASME Form No. U-1 to be approved prior to shipping.

C. 	Submit product data for each heat exchanger, including rated capacities, pressure drop, weights (shipping, installed, and operating), and installation and startup instructions.

D.  	Submit shop drawings indicating heat exchanger dimensions, rough-in requirements, weight loadings and distribution, and clearances required around the heat exchanger.

E. 	Submit maintenance data for heat exchangers in the operation and maintenance manual as specified in Section 01300.  Include detailed manufacturer's instructions for servicing heat exchangers.

1.06	DELIVERY, STORAGE, AND HANDLING

A.  	See Section 15010.

1.07	PROJECT/SITE CONDITIONS

A.  	Coordinate layout and installation of heat exchangers with piping system and adjacent work.  Revise locations and elevations to suit field conditions and as approved by the Architect/Engineer (A/E).

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Provide products by one of the following:

1.  	Shell-and-Tube Heat Exchangers:

a. 		Amtrol Inc.

b. 		Armstrong Pumps, Inc.

c. 		Dunham-Bush, Inc.

d. 		Harsco Corp.; Patterson-Kelley Co.

e.		ITT Fluid Technology Corporation.; ITT Bell & Gossett.

f. 		Taco, Inc.

2.  	Plate Heat Exchangers:

a. 		Alfa-Laval Thermal, Inc.

b. 		Armstrong Pumps, Inc.

c. 		Baltimore Aircoil Company.

d.		ITT Fluid Technology Corporation.; ITT Bell & Gossett.

2.02	RATINGS

A.  	Shell and Tube

1.  	Heating Water, Equipment No. 320.

a. 		Maximum Design Temperature:  375 deg F (190 deg C).

b. 		Maximum Shell Pressure:

1)  	Test:  250 psig (1723 kPa).

2)  	Design:  125 psig (862 kPa).

c. 		Maximum Tube Pressure:

1)  	Test:  250 psig (1723 kPa).

2)  	Design:  125 psig (862 kPa).

d.		Heat Exchanger Type:  Steam to water.

e. 		See Drawing Schedule for additional information.

2.  	Process Deioninzed Water, Equipment No. 335.

a. 		Maximum Design Temperature:  450 deg F (228 deg C).

b. 		Maximum Shell Pressure:

1)  	Test:  335 psig (2309 kPa).

2)  	Design:  225 psig (1551 kPa).

c. 		Maximum Tube Pressure:

1)  	Test:  225 psig (1551 kPa).

2)  	Design:  150 psig (1034 kPa).

d. 		Heat Exchanger Type:  Water to water.

e.		See Drawing Schedule for additional information.

3.  	High Temperature Process cooling Water, Equipment No. 337.

a. 		Maximum Design Temperature:  220 deg F (111 deg C).

b. 		Maximum Shell Pressure:

1)  	Test:  150 psig (1034 kPa).

2)  	Design:  75 psig (517 kPa).

c. 		Maximum Tube Pressure:

1)  	Test:  150 psig (1034 kPa).

2)  	Design:  75 psig (517 kPa).

d. 		Heat Exchanger Type:  Steam to water.

e. 		See Drawing Schedule for additional information.

B.  	Plate and Frame

1.  	Process Cooling Water, Equipment No. 315

a. 		Maximum Design Temperature:

1) 	Primary:  225 deg. F.

2)  	Secondary:  225 deg. F.

b. 		Maximum Test Pressure:

1)  	Primary:  225 psi (1551 kPa).

2)  	Secondary:  225 psi (1551 kPa).

c. 		Maximum Design Pressure:

1)  	Primary:  150 psi (1034 kPa).

2)  	Secondary:  150 psi (1034 kPa).

d. 		See Drawing Schedule for additional information.

2.03	SHELL-AND-TUBE HEAT EXCHANGERS

A.  	Heating Water, Equipment No. 320.

1.  	Shell and Head Materials:  Steel shell and cast-iron head.

2.  	Tube and Tube Sheet Materials:  Seamless copper tubes with steel tube sheets.

3.  	Piping Connections:  Flanged shell fluid entry and threaded shell fluid exit.  Flanged head ports.

B.  	Process Deioninzed Water, Equipment No. 335.

1.  	Shell and Head Materials:  316 stainless-steel shell and fabricated 316 stainless-steel head.

2. 	Tube and Tube Sheet Materials:  Seamless copper tubes with steel tube sheets.

3.  	Piping Connections:  Threaded shell and head ports.

C.  	High Temperature Process Cooling Water, Equipment No. 337.

1.  	Shell and Head Materials:  Ductile iron shell and head.

2.  	Tube: Seamless copper tubes.

3.  	Piping Connections:  Victaulic

2.04	PLATE HEAT EXCHANGERS

A.  	Process Cooling Water, Equipment No. 315

1.  	Plate Material:  ASTM A 167, Type 304 stainless-steel shell.

2. 	End Plate Material:  Painted carbon steel.

3.  	Gasket Material:  Nitrile rubber.

4. 	Piping Connections:  Threaded, 2 in. and smaller.

5.  	Piping Connections:  Studded for ANSI flange connection, 4 in. and larger.

PART 3 - EXECUTION

3.01	INSPECTION

A.  	Inspect elements and surfaces to receive work for compliance with installation tolerances and for structural rigidity, strength, anchors, and other conditions affecting performance of the heat exchanger.  Do not proceed with installation until unsatisfactory conditions have been corrected.

3.02	INSTALLATION/APPLICATION/ERECTION

A.  	Install heat exchangers according to manufacturer's written instructions.

B. 	Install heat exchangers plumb and level; anchor with supports.

C.  	Maintain manufacturer's recommended clearances for service and maintenance.  Install piping connections maintaining clearances for service and maintenance of heat exchangers.

D.  	Install threaded or flanged connections at heat exchangers.

E. 	Install shutoff valves at heat exchanger inlet and outlet connections.

F. 	Insulate as indicated on the Drawings.

3.03	ADJUSTING AND CLEANING

A. 	Inspect exposed finish after completing system installation, including pipe connections, fittings, valves, and specialties.  Remove burrs, dirt, and construction debris, and repair damaged finishes, including chips, scratches, and abrasions.

3.04	COMMISSIONING

A.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.

B. 	Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

3.05	DEMONSTRATION

A.  Provide the services of a factory-authorized service representative to start-up equipment, demonstrate operation, and train personnel.

B.  	See Section 15995.

END OF SECTION