LARP IR Cryogenics:  Sector 4-5 Heat Load Study for the 1035/cm2-s LHC Luminosity Upgrade

Roger Rabehl

July 25, 2006

# Introduction

The goal of the LHC Accelerator Research Program (LARP) is to contribute to the LHC luminosity upgrade from 1034/cm2-s to 1035/cm2-s.  This upgrade will likely occur in a number of phases [1].  One contribution LARP is focusing on is the interaction region (IR) upgrades.  The increased heat loads resulting from the luminosity upgrade will affect not only the thermal design of the IR’s, but also the LHC cryogenics system as a whole.  This document attempts to address this question by scaling the cryogenics system heat loads and determining the significance of the IR heat loads relative to the system heat loads.

Sector 4-5 (a high-load sector) is analyzed in this document.  Only the heat loads to 1.9 K and 4.6-20 K are considered because they are the temperature levels most relevant to the inner triplet.

Analysis

LHC Luminosity Upgrade Options

Two of the LHC luminosity upgrades being considered are the short bunch and long bunch options.  The short bunch option has twice as many total particles as ultimate luminosity with twice as many bunches but half the bunch length.  The long bunch option has about 15% more total particles than ultimate luminosity but only one-third the number of bunches and a bunch length twice as long.  The parameters listed in Table 1 are relevant for estimating the system heat load for the two luminosity upgrade scenarios.

Table 1  Parameters for LHC upgrade options [2, except for the next to last row].

| Parameter | Nominal luminosity | Ultimate luminosity | Short bunch luminosity upgrade | Long bunch luminosity upgrade |
| --- | --- | --- | --- | --- |
| Beam current, Ibeam [A] | 0.58 | 0.86 | 1.72 | 1.0 |
| No. of bunches, nbunch | 2808 | 2808 | 5616 | 936 |
| Bunch length (r.m.s.), z [cm] | 7.55 | 7.55 | 3.78 | 14.4 |
| Luminosity, L [1034/cm2-s] | 1.0 | 2.3 | 9.2 | 8.9 |
| Bunch current, Ibunch [mA] | 0.21 | 0.31 | 0.31 | 1.07 |
| Long. Profile | Gaussian | Gaussian | Gaussian | Flat |

The bunch current, or bunch intensity, is calculated by Equation 1.

(1)

Heat Load Scaling

The scaling laws of Table 2 can be used to estimate cryogenic system heat loads for each of the luminosity upgrade scenarios based on the parameters in Table 1.  For the upgrade scenarios considered here, the relevant parameters are bunch current Ibunch, number of bunches nbunch, bunch length z, and luminosity L.

Table 2  Scaling laws of beam-induced loads [3].

| Beam parameter | Energy E | Bunch current Ibunch | Bunch number nbunch | Bunch length z [r.m.s.] | Luminosity L |
| --- | --- | --- | --- | --- | --- |
| Resistive heating | E2 | - | - | - | - |
| Synchrotron radiation | E4 | Ibunch | nbunch | - | - |
| Image current | - | Ibunch2 | nbunch | z-3/2 | - |
| Photo-electron cloud | - | Ibunch3 | nbunch | - | - |
| Beam gas scattering | - | Ibunch | nbunch | - | - |
| Random particle loss | - | Ibunch | nbunch | - | - |
| Secondaries | E | - | - | - | L |
| RF losses | - | Ibunch2 | nbunch | - | - |

At nominal luminosity, the latest photo-electron cloud numbers are reduced by 2/3 from those in the LHC Design Report.  At ultimate luminosity, these numbers are reduced by slightly more than 2/3.  The electron cloud heat load varies with bunch intensity by a third-power law but there is often a weaker dependence, especially at higher bunch intensities.  Also, a decrease in heat load becomes noticeable from about twice the nominal bunch length.  Long, flat bunches or super-bunches generate less heat load per proton than at the nominal LHC conditions [4].  Therefore, the photo-electron heat load for the long bunch upgrade is assumed to be equal to that at ultimate luminosity due to the high bunch intensity and the long, flat bunch profile.

Table 3  Distributed steady-state beam-induced loads in an LHC cell [mW/m]

[5; 6 (photo-electron cloud numbers)]

|  | Nominal luminosity | Ultimate luminosity |
| --- | --- | --- |
| Temperature | 4.6-20 K | 1.9 K | 4.6-20 K | 1.9 K |
| Synchrotron radiation | 330 | 1 | 500 | 1 |
| Image current | 360 | 1 | 820 | 2 |
| Photo-electron cloud | 600 | 6 | 900 | 9 |
| Beam-gas scattering | 0.4 | 48 | 0.4 | 48 |
| Random particle loss | 0-0.1 | 0-32 | 0-0.3 | 0-48 |
| Total beam-induced | 1290 | 56-88 | 2220 | 60-108 |
|  | Short bunch upgrade | Long bunch upgrade |
| Temperature | 4.6-20 K | 1.9 K | 4.6-20 K | 1.9 K |
| Synchrotron radiation | 1000 | 2 | 575 | 1 |
| Image current | 4629 | 11 | 1236 | 3 |
| Photo-electron cloud | 1800 | 18 | 900 | 9 |
| Beam-gas scattering | 0.8 | 96 | 0.5 | 55 |
| Random particle loss | 0-0.6 | 0-96 | 0-0.3 | 0-55 |
| Total beam-induced | 7430 | 127-223 | 2712 | 68-123 |

Sector Heat Load Calculations

The heat load estimates of Table 3 can be applied to estimate the heat load for a given sector of the LHC.  This document presents calculated results for sector 4-5, a high-load sector.  Table A-1 in the Appendix summarizes the sector 4-5 heat load calculations for nominal luminosity, ultimate luminosity, short bunch upgrade, and long bunch upgrade operation, respectively.  The calculations are detailed in Tables A-2 through A-5 of the Appendix.

With the exception of the photo-electron heat loads, the nominal and ultimate heat loads are taken from the LHC Design Report as indicated.  Heat loads for the short bunch and long bunch upgrades are then calculated using the scaling laws of Table 2.  The dispersion suppressor heat loads are assumed to scale similarly to the arc heat loads.  The 4.6-20 K inner triplet heat load is assumed to be dominated by the photo-electron effect and is scaled accordingly.  The 1.9 K inner triplet heat load is assumed to be dominated by the secondary particles as calculated by N. Mokhov (FNAL).

Table 4  Installed refrigeration capacity in the LHC sectors [7].

| Temperature level | High-load sector | Low-load sector |
| --- | --- | --- |
| 50-75 K [W] | 33000 | 31000 |
| 4.6-20 K [W] | 7700 | 7600 |
| 4.5 K [W] | 300 | 150 |
| 1.9 K LHe [W] | 2400 | 2100 |
| 4 K VLP [W] | 430 | 380 |
| 20-280 K [g/s] | 41 | 27 |

Figure 1 summarizes the calculated 4.6-20 K heat loads.  Based on current estimates, the installed refrigeration capacity is slightly below the ultimate luminosity heat load.  Both the short and long bunch upgrades would require system upgrades, with the short bunch upgrade requiring a significantly more extensive upgrade due to the photo-electron effect.

Figure 1  Calculated 4.6-20 K heat loads for sector 4-5 at nominal, ultimate, short bunch upgrade, and long bunch upgrade luminosities.

Similarly, Figure 2 shows the calculated 1.9 K heat loads.  The installed capacity is estimated to be sufficient for nominal and ultimate luminosity operations.  The installed capacity is exceeded by the heat loads of both the short bunch and long bunch upgrades.  The inner triplet dynamic heat load to 1.9 K is indicated for each luminosity, and for both upgrade scenarios it is a significant fraction of the total sector heat load.

Figure 2  Calculated 1.9 K heat loads for sector 4-5 at nominal, ultimate, short bunch upgrade, and long bunch upgrade luminosities.

Conclusions

Both luminosity upgrade scenarios will require cryogenic upgrades to the 4.6-20 K system.  A much more extensive cryogenic upgrade will be required if the short bunch luminosity upgrade is chosen.

The installed 1.9 K capacity is not sufficient for either luminosity upgrade scenario.  The inner triplet heat load is significant for both luminosity upgrade scenarios.

A number of possible cryogenic system upgrades can be envisioned and have been discussed elsewhere [8].  Among the possibilities are:

- Upgrade the 4.6-20 K and 1.9 K systems to meet the heat loads of Figure 1 and 2.

- Intercept a sizable fraction of the inner triplet 1.9 K heat load at a higher temperature (e.g., using 4.6-20 K absorbers).  This would minimize or even eliminate a 1.9 K capacity upgrade while requiring a larger 4.6-20 K capacity upgrade.

- Upgrade the 4.6-20 K system to meet the heat loads of Figure 1 while adding 1.9 K plants dedicated to cooling the inner triplets.

#### References

[1]  F. Ruggiero, “LHC Upgrade Scenarios and Interaction Region Design,” LHC IR Upgrades Workshop, St. Charles, IL, October 3-4, 2005.

[2]  Ibid

[3]  LHC Design Report Volume 1, Chap. 8, Table 11.7, p. 316.

(http://ab-div.web.cern.ch/ab-div/Publications/LHC-DesignReport.html)

[4]  F. Zimmerman, private communication, February 2006.

[5]  LHC Design Report Volume 1, Chap. 8, Table 11.8, p. 316.

(http://ab-div.web.cern.ch/ab-div/Publications/LHC-DesignReport.html)

[6]  F. Zimmerman, “LHC electron-cloud update,” p.10, LHC MAC 10, June 2005.

(http://mgt-lhc-machine-advisory-committee.web.cern.ch/mgt-lhc-machine-advisory-committee/lhcmac17/ClosedSession/Zimmermann.pdf)

[7]  LHC Design Report Volume 1, Chap. 8, Table 11.11, p. 328.

(http://ab-div.web.cern.ch/ab-div/Publications/LHC-DesignReport.html)

[8]  F. Ruggiero, et al., “LHC Luminosity and Energy Upgrade:  A Feasibility Study,” LHC Project Report 626, December 2002.

Appendix

Table A-1  Sector 4-5 heat load summary.

Table A-2  Nominal luminosity sector 4-5 heat load summary.

Table A-3  Ultimate luminosity sector 4-5 heat load summary.

Table A-4  Short bunch luminosity upgrade sector 4-5 heat load summary.

Table A-5  Long bunch luminosity upgrade sector 4-5 heat load summary.