## 25F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 027
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6657.4
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -73.75 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 828.42 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 792.22 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1052.87 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 828.42 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1455.09 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 233.1 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2183.34 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1069.85 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2115.31 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1052.87 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 792.22 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 764.95 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1069.85 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1490.81 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1490.81 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1455.09 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2193.09 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1461.21 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2155.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2193.09 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -73.75 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 2183.34 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 233.1 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 2156.04 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 764.95 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 2155.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1461.21 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2115.31 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2156.04 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 027
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6324.2273
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 316.68 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 883.79 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 909.37 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1161.27 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 883.79 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1549.87 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 575.98 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2194.71 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1156.37 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1876.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1161.27 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 909.37 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 984.15 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1156.37 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1561.39 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1561.39 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1549.87 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2192.67 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1873.33 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1905.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2192.67 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 316.68 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 2194.71 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 575.98 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1958.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 984.15 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1905.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1873.33 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1876.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1958.08 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 027
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6038.468
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 500.47 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 885.1 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 895.34 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1151.14 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 885.1 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1540.11 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 854.42 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2211.41 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1161.43 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1560.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1151.14 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 895.34 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1281.5 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1161.43 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1550.96 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1550.96 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1540.11 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2233.15 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1934.28 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1606.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2233.15 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 500.47 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 2211.41 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 854.42 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1647.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1281.5 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1606.67 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1934.28 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1560.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1647.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 027
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4959.3333
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1297.51 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1184.85 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1259.95 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1453.07 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1184.85 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1836.83 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1564.57 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1877.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1516.27 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 982.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1453.07 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 1259.95 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1885.7 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1516.27 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1900.15 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1900.15 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1836.83 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1916.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 1963.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 1029.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1916.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1297.51 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1877.32 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1564.57 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1078.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1885.7 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1029.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1963.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 982.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1078.59 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 027
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4619.544
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1242.11 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1163.45 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1216.24 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1417.86 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1163.45 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1790.61 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1534.3 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1665.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1451.02 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 872.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1417.86 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1216.24 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1903.05 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1451.02 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1847 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1847 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1790.61 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1700.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 1743.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 920.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1700.84 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1242.11 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1665.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1534.3 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 966.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1903.05 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 920.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1743.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 872.54 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 966.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
G0 | -73.75 | 316.68 | 500.47 | 1297.51 | 1242.11
G1 | 792.22 | 909.37 | 895.34 | 1259.95 | 1216.24 | Season/Year: | WINTER 2009
G2 | 828.42 | 883.79 | 885.1 | 1184.85 | 1163.45 | Direction: | South-to-North (SN)
G3 | 233.1 | 575.98 | 854.42 | 1564.57 | 1534.3 | Case Loads: | Heavy Loads
G4 | 1069.85 | 1156.37 | 1161.43 | 1516.27 | 1451.02 | Outage: | 027
G5 | 1052.87 | 1161.27 | 1151.14 | 1453.07 | 1417.86 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 764.95 | 984.15 | 1281.5 | 1885.7 | 1903.05 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1490.81 | 1561.39 | 1550.96 | 1900.15 | 1847 | Study Person: | FRP9899
G8 | 1455.09 | 1549.87 | 1540.11 | 1836.83 | 1790.61 | Source: | 027WINTER09v1SNH
G9 | 1461.21 | 1873.33 | 1934.28 | 1963.22 | 1743.5
G10 | 2193.09 | 2192.67 | 2233.15 | 1916.19 | 1700.84
G11 | 2183.34 | 2194.71 | 2211.41 | 1877.32 | 1665.76
G12 | 2156.04 | 1958.08 | 1647.24 | 1078.59 | 966.51
G13 | 2155.77 | 1905.19 | 1606.67 | 1029.86 | 920.47
G14 | 2115.31 | 1876.45 | 1560.34 | 982.78 | 872.54
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 027 | Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6657.4 | -73.75 | 792.22 | 828.42 | 233.1 | 1069.85 | 1052.87 | 764.95 | 1490.81 | 1455.09 | 1461.21 | 2193.09 | 2183.34 | 2156.04 | 2155.77 | 2115.31
35F | 6324.2273 | 316.68 | 909.37 | 883.79 | 575.98 | 1156.37 | 1161.27 | 984.15 | 1561.39 | 1549.87 | 1873.33 | 2192.67 | 2194.71 | 1958.08 | 1905.19 | 1876.45
45F | 6038.468 | 500.47 | 895.34 | 885.1 | 854.42 | 1161.43 | 1151.14 | 1281.5 | 1550.96 | 1540.11 | 1934.28 | 2233.15 | 2211.41 | 1647.24 | 1606.67 | 1560.34
60F | 4959.3333 | 1297.51 | 1259.95 | 1184.85 | 1564.57 | 1516.27 | 1453.07 | 1885.7 | 1900.15 | 1836.83 | 1963.22 | 1916.19 | 1877.32 | 1078.59 | 1029.86 | 982.78
70F | 4619.544 | 1242.11 | 1216.24 | 1163.45 | 1534.3 | 1451.02 | 1417.86 | 1903.05 | 1847 | 1790.61 | 1743.5 | 1700.84 | 1665.76 | 966.51 | 920.47 | 872.54

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -74.99 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -543.48 | -543.46 | 6666.3 | -73.75 | -65.69 | FULL
G1 | 792.53 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -510.44 | -510.38 | 6625.81 | 792.22 | -461.57 | FULL
G2 | 827.32 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -527.03 | -526.92 | 6636.15 | 828.42 | -460.9 | FULL
G3 | 234.46 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -542.55 | -542.53 | 6667.02 | 233.1 | -153.38 | FULL
G4 | 1069.27 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -515.67 | -515.81 | 6631.3 | 1069.85 | -554.16 | FULL
G5 | 1052.46 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -516.19 | -516.01 | 6640.4 | 1052.87 | -522.43 | FULL
G6 | 764.58 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -9.13 | -544.06 | -544.24 | 6676.79 | 764.95 | -324.1 | FULL
G7 | 1490.04 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -530.28 | -529.9 | 6640.24 | 1490.81 | -657.31 | FULL
G8 | 1454.99 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -516.61 | -516.94 | 6647.11 | 1455.09 | -613.48 | FULL
G9 | 1461.36 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -7.29 | -521.74 | -547.02 | 6693.31 | 1461.21 | -490.51 | FULL
G10 | 2193.2 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -530.49 | -530.05 | 6660.75 | 2193.09 | -839.26 | FULL
G11 | 2183.19 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -515.73 | -515.65 | 6667.96 | 2183.34 | -812.66 | FULL
G12 | 2156.44 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -537.88 | -538.08 | 6715.16 | 2156.04 | -713.83 | FULL
G13 | 2155.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -479.31 | -479.3 | 6642.87 | 2155.77 | -677.44 | FULL
G14 | 2116.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -478.18 | -478.18 | 6649.83 | 2115.31 | -627.19 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 316.4 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -533.01 | -532.94 | 6340.65 | 316.68 | -222.49 | FULL
G1 | 909.16 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -514.17 | -514.35 | 6293.63 | 909.37 | -494.46 | FULL
G2 | 884.22 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -500.54 | -500.86 | 6301.9 | 883.79 | -452.52 | FULL
G3 | 575.77 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -9.13 | -526.97 | -526.94 | 6344.32 | 575.98 | -299.09 | FULL
G4 | 1155.98 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -497.12 | -497.27 | 6298.53 | 1156.37 | -563.65 | FULL
G5 | 1161.16 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -513.33 | -512.93 | 6307.89 | 1161.27 | -535.99 | FULL
G6 | 983.86 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -531.66 | -531.53 | 6350.17 | 984.15 | -390.14 | FULL
G7 | 1561.03 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -512.09 | -511.82 | 6306.8 | 1561.39 | -662.68 | FULL
G8 | 1549.59 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -512.51 | -512.26 | 6315.08 | 1549.87 | -627.54 | FULL
G9 | 1873.69 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -534.12 | -533.92 | 6377.81 | 1873.33 | -666.8 | FULL
G10 | 2192.9 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -500.83 | -500.49 | 6326 | 2192.67 | -819.66 | FULL
G11 | 2195.28 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -501.82 | -501.74 | 6334.84 | 2194.71 | -769.44 | FULL
G12 | 1958.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -469.41 | -469.21 | 6368.36 | 1958.08 | -579.11 | FULL
G13 | 1904.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -469.09 | -468.96 | 6294.39 | 1905.19 | -509.71 | FULL
G14 | 1878.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -467.02 | -467 | 6303.04 | 1876.45 | -473.55 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 499.96 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -9.13 | -516.86 | -516.63 | 6061.52 | 500.47 | -309.4 | FULL
G1 | 897.36 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -489.34 | -489.75 | 6007.26 | 895.34 | -478.84 | FULL
G2 | 884.89 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -500.54 | -500.49 | 6017.01 | 885.1 | -444.54 | FULL
G3 | 854.4 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -523.45 | -523.49 | 6068.53 | 854.42 | -428.24 | FULL
G4 | 1159.38 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -500.14 | -500.53 | 6012.83 | 1161.43 | -556.26 | FULL
G5 | 1149.2 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -488.21 | -488.16 | 6022.85 | 1151.14 | -522.72 | FULL
G6 | 1281.75 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -523.21 | -523.32 | 6076.57 | 1281.5 | -537.42 | FULL
G7 | 1550.48 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -500.1 | -499.95 | 6020.62 | 1550.96 | -647.56 | FULL
G8 | 1539.82 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -500.41 | -500.45 | 6029.86 | 1540.11 | -612.46 | FULL
G9 | 1934.79 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -9.06 | -519.36 | -519.44 | 6095.33 | 1934.28 | -679.49 | FULL
G10 | 2233.11 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -489.8 | -489.68 | 6041.1 | 2233.15 | -814.92 | FULL
G11 | 2211.26 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -485.75 | -486.18 | 6049.31 | 2211.41 | -775 | FULL
G12 | 1647.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -431.15 | -431.35 | 6069.6 | 1647.24 | -405.61 | FULL
G13 | 1606.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -430.08 | -429.83 | 5997.35 | 1606.67 | -344.91 | FULL
G14 | 1560.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -429.43 | -429.03 | 6007.28 | 1560.34 | -291.59 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1297.32 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -468.54 | -468.39 | 5006.64 | 1297.51 | -607.42 | FULL
G1 | 1259.99 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -470.49 | -470.89 | 4933.62 | 1259.95 | -561.9 | FULL
G2 | 1184.42 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 462.86 | 462.95 | 4942.24 | 1184.85 | -495.26 | FULL
G3 | 1566.66 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -470.97 | -470.87 | 5013.35 | 1564.57 | -689.36 | FULL
G4 | 1516.28 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -469.44 | -469.65 | 4939.92 | 1516.27 | -635.38 | FULL
G5 | 1453.04 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 469.1 | 468.62 | 4948.58 | 1453.07 | -570.8 | FULL
G6 | 1885.13 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -15.5 | -471.69 | -471.53 | 5021.16 | 1885.7 | -748.09 | FULL
G7 | 1899.64 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 465.75 | 466.35 | 4948.93 | 1900.15 | -723.75 | FULL
G8 | 1836.57 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 469.27 | 469.69 | 4957.6 | 1836.83 | -650.02 | FULL
G9 | 1963.32 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 4.83 | 119.8 | 119.77 | 5006.56 | 1963.22 | -586.4 | FULL
G10 | 1916.47 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 4.83 | 119.75 | 119.73 | 4934.44 | 1916.19 | -540.88 | FULL
G11 | 1877.99 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 4.83 | 119.76 | 119.74 | 4944.43 | 1877.32 | -491.49 | FULL
G12 | 1080.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -428.37 | -428.13 | 4972.1 | 1078.59 | -11.86 | FULL
G13 | 1029.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -427.91 | -427.74 | 4903.79 | 1029.86 | 43.23 | FULL
G14 | 984.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -426.44 | -426.12 | 4916.64 | 982.78 | 105.57 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1241.88 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 445.59 | 445.69 | 4666.24 | 1242.11 | -560.49 | FULL
G1 | 1214.38 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 455.92 | 456.15 | 4593.91 | 1216.24 | -514.1 | FULL
G2 | 1163.3 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 456.12 | 456.29 | 4603.52 | 1163.45 | -456.92 | FULL
G3 | 1534.39 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 449.1 | 449.22 | 4673.1 | 1534.3 | -641.48 | FULL
G4 | 1451.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 452.85 | 452.97 | 4600.21 | 1451.02 | -571.92 | FULL
G5 | 1418.11 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 455.99 | 456.05 | 4609.63 | 1417.86 | -528.81 | FULL
G6 | 1903.15 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 454.41 | 454.09 | 4681.81 | 1903.05 | -722.12 | FULL
G7 | 1847.12 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 448.93 | 449.21 | 4608.8 | 1847 | -672.62 | FULL
G8 | 1790.93 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | 21 | 446.81 | 447.04 | 4618.17 | 1790.61 | -605.9 | FULL
G9 | 1743.71 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 4.83 | 114.01 | 114 | 4659.6 | 1743.5 | -464.17 | FULL
G10 | 1700.69 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 4.83 | 113.87 | 114.01 | 4588.54 | 1700.84 | -411.63 | FULL
G11 | 1663.43 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 4.83 | 114.05 | 114.04 | 4600.47 | 1665.76 | -364.46 | FULL
G12 | 968.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -426.48 | -426.42 | 4636.57 | 966.51 | 82.01 | FULL
G13 | 922.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -426.49 | -426.15 | 4569.02 | 920.47 | 134.79 | FULL
G14 | 874.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -15.9 | -426.36 | -425.99 | 4583.57 | 872.54 | 188.43 | FULL
027WINTER09v1SNH