## 25F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023R2
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6524.8407
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 200.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 333.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 263.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 950.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 333.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1638.53 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 809.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1334.8 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 878.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1081.74 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 950.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 263.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1465.98 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 878.96 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 1558.1 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1558.1 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1638.53 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1261.4 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 1167.02 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1029.37 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1261.4 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 200.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1334.8 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 809.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 971.04 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1465.98 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1029.37 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1167.02 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1081.74 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 971.04 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023R2
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6387.578
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 365.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 441.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 379.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1052.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 441.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1467.34 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 901.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1173.5 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 978.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 962.97 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1052.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 379.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1299.79 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 978.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 1393.2 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1393.2 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1467.34 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1097.38 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 994.47 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 881.26 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1097.38 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 365.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1173.5 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 901.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 739.82 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1299.79 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 881.26 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 994.47 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 962.97 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 739.82 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023R2
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5947.5807
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 258.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 395.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 329.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 970.37 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 395.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1388.56 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 827.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1089.87 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 899.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 882.31 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 970.37 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 329.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1224.04 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 899.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 1311.4 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1311.4 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1388.56 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1012.76 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 962.4 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 766.3 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1012.76 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 258.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1089.87 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 827.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 686.77 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1224.04 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 766.3 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 962.4 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 882.31 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 686.77 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023R2
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4908.798
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1077.37 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1229.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1152.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1403.47 | N-1: Monroe - HRNCHTAP MS | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1229.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1228.75 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1278.35 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 776.88 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1354.87 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 654.32 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1403.47 | N-1: Monroe - HRNCHTAP MS | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 1152.5 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1104.9 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1354.87 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1185.35 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1185.35 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1228.75 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 701.24 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 620.18 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 584.2 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 701.24 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1077.37 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 776.88 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1278.35 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 496.11 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1104.9 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 584.2 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 620.18 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 654.32 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 496.11 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 023R2
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4586.04
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1214.81 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1365.13 | N-1: Monroe - HRNCHTAP MS | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1295.27 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1286.01 | N-1: Monroe - HRNCHTAP MS | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1365.13 | N-1: Monroe - HRNCHTAP MS | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1110.86 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1131.98 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 663.27 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1210.16 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 488.21 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1286.01 | N-1: Monroe - HRNCHTAP MS | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1295.27 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 798.46 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1210.16 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 1032.06 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1032.06 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1110.86 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 570.06 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 498.3 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 456.07 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 570.06 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1214.81 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 663.27 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1131.98 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 376.42 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 798.46 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 456.07 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 498.3 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 488.21 | BFR: Bothell 230kV Bus Sect #1 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 376.42 | BFR: Horse Ranch 230kV Bus | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
G0 | 200.29 | 365.89 | 258.62 | 1077.37 | 1214.81
G1 | 263.8 | 379.38 | 329.05 | 1152.5 | 1295.27 | Season/Year: | WINTER 2009
G2 | 333.71 | 441.42 | 395.25 | 1229.33 | 1365.13 | Direction: | North-to-South (NS)
G3 | 809.82 | 901.17 | 827.71 | 1278.35 | 1131.98 | Case Loads: | Heavy Loads
G4 | 878.96 | 978.17 | 899.82 | 1354.87 | 1210.16 | Outage: | 023R2
G5 | 950.11 | 1052.35 | 970.37 | 1403.47 | 1286.01 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1465.98 | 1299.79 | 1224.04 | 1104.9 | 798.46 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1558.1 | 1393.2 | 1311.4 | 1185.35 | 1032.06 | Study Person: | FRP9899
G8 | 1638.53 | 1467.34 | 1388.56 | 1228.75 | 1110.86 | Source: | 023R2WINTER09v5NSH(COV-CRES BYP)
G9 | 1167.02 | 994.47 | 962.4 | 620.18 | 498.3
G10 | 1261.4 | 1097.38 | 1012.76 | 701.24 | 570.06
G11 | 1334.8 | 1173.5 | 1089.87 | 776.88 | 663.27
G12 | 971.04 | 739.82 | 686.77 | 496.11 | 376.42
G13 | 1029.37 | 881.26 | 766.3 | 584.2 | 456.07
G14 | 1081.74 | 962.97 | 882.31 | 654.32 | 488.21
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 023R2 | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6524.8407 | 200.29 | 263.8 | 333.71 | 809.82 | 878.96 | 950.11 | 1465.98 | 1558.1 | 1638.53 | 1167.02 | 1261.4 | 1334.8 | 971.04 | 1029.37 | 1081.74
35F | 6387.578 | 365.89 | 379.38 | 441.42 | 901.17 | 978.17 | 1052.35 | 1299.79 | 1393.2 | 1467.34 | 994.47 | 1097.38 | 1173.5 | 739.82 | 881.26 | 962.97
45F | 5947.5807 | 258.62 | 329.05 | 395.25 | 827.71 | 899.82 | 970.37 | 1224.04 | 1311.4 | 1388.56 | 962.4 | 1012.76 | 1089.87 | 686.77 | 766.3 | 882.31
60F | 4908.798 | 1077.37 | 1152.5 | 1229.33 | 1278.35 | 1354.87 | 1403.47 | 1104.9 | 1185.35 | 1228.75 | 620.18 | 701.24 | 776.88 | 496.11 | 584.2 | 654.32
70F | 4586.04 | 1214.81 | 1295.27 | 1365.13 | 1131.98 | 1210.16 | 1286.01 | 798.46 | 1032.06 | 1110.86 | 498.3 | 570.06 | 663.27 | 376.42 | 456.07 | 488.21

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 199.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 473.49 | 473.24 | 6561.04 | 200.29 | 0 | FULL
G1 | 262.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 473.89 | 473.72 | 6487.53 | 263.8 | 0 | FULL
G2 | 332.21 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 473.59 | 473.34 | 6496.24 | 333.71 | 0 | FULL
G3 | 809.8 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 483.46 | 483.41 | 6554.35 | 809.82 | 0 | FULL
G4 | 879.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 483.17 | 483.05 | 6483.47 | 878.96 | 0 | FULL
G5 | 952.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 483.49 | 483.37 | 6494.63 | 950.11 | 0 | FULL
G6 | 1468.54 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 657.55 | 657.43 | 6565.7 | 1465.98 | 0 | FULL
G7 | 1561.12 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 659.24 | 659.1 | 6497.89 | 1558.1 | 0 | FULL
G8 | 1641.57 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 659.62 | 659.53 | 6513.09 | 1638.53 | 0 | FULL
G9 | 1168.08 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 658.56 | 658.46 | 6572.2 | 1167.02 | 0 | FULL
G10 | 1263.66 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 660.6 | 660.01 | 6505.69 | 1261.4 | 0 | FULL
G11 | 1337.19 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 661.01 | 660.91 | 6521.64 | 1334.8 | 0 | FULL
G12 | 971.33 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 659.96 | 659.86 | 6579.02 | 971.04 | 0 | FULL
G13 | 1029.61 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 661.96 | 661.88 | 6512.05 | 1029.37 | 0 | FULL
G14 | 1082.75 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 663.14 | 663.04 | 6528.07 | 1081.74 | 0 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 364.74 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 470.18 | 470.04 | 6422.17 | 365.89 | 0 | FULL
G1 | 377.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 468.06 | 467.88 | 6350.06 | 379.38 | 0 | FULL
G2 | 440.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 467.14 | 466.97 | 6359.67 | 441.42 | 0 | FULL
G3 | 901.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 476.1 | 475.82 | 6418.91 | 901.17 | 0 | FULL
G4 | 978.31 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 476.02 | 475.92 | 6348.26 | 978.17 | 0 | FULL
G5 | 1052.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 476.43 | 476.05 | 6360.98 | 1052.35 | 0 | FULL
G6 | 1301 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 628.37 | 628.27 | 6427.16 | 1299.79 | 0 | FULL
G7 | 1395.31 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 630.88 | 630.81 | 6359.77 | 1393.2 | 0 | FULL
G8 | 1470.52 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 631.45 | 630.94 | 6374.77 | 1467.34 | 0 | FULL
G9 | 996.53 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 629.85 | 629.52 | 6433.5 | 994.47 | 0 | FULL
G10 | 1098.1 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 628.06 | 627.59 | 6367.5 | 1097.38 | 0 | FULL
G11 | 1174.61 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 628.06 | 627.7 | 6383.7 | 1173.5 | 0 | FULL
G12 | 741.92 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 634.36 | 634.52 | 6439.37 | 739.82 | 0 | FULL
G13 | 881.59 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 631.66 | 631.26 | 6375.19 | 881.26 | 0 | FULL
G14 | 963.55 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 632.13 | 631.72 | 6392.66 | 962.97 | 0 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 259.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 435.57 | 435.48 | 5981.24 | 258.62 | 0 | FULL
G1 | 329.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 435.03 | 434.96 | 5908.69 | 329.05 | 0 | FULL
G2 | 395.78 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 435.06 | 434.98 | 5919.26 | 395.25 | 0 | FULL
G3 | 827.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 440.97 | 440.76 | 5977.4 | 827.71 | 0 | FULL
G4 | 899.74 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 440.68 | 440.85 | 5907.9 | 899.82 | 0 | FULL
G5 | 970.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 440.75 | 440.97 | 5921.11 | 970.37 | 0 | FULL
G6 | 1225.37 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 599.06 | 598.99 | 5986.22 | 1224.04 | 0 | FULL
G7 | 1313.14 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 600.07 | 600.27 | 5919.35 | 1311.4 | 0 | FULL
G8 | 1390.82 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 600.35 | 600.36 | 5935.12 | 1388.56 | 0 | FULL
G9 | 963.37 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 592.33 | 592.22 | 5995.03 | 962.4 | 0 | FULL
G10 | 1014.34 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 597.35 | 597.06 | 5927.57 | 1012.76 | 0 | FULL
G11 | 1090.92 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 597.05 | 597.04 | 5944.33 | 1089.87 | 0 | FULL
G12 | 685.29 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 598.46 | 598.27 | 6000.96 | 686.77 | 0 | FULL
G13 | 768.11 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 598.69 | 598.7 | 5935.58 | 766.3 | 0 | FULL
G14 | 883 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 596.77 | 596.45 | 5953.95 | 882.31 | 0 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1078 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 441.48 | 441.39 | 4935.17 | 1077.37 | 0 | FULL
G1 | 1154.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 441.62 | 441.82 | 4868.83 | 1152.5 | 0 | FULL
G2 | 1231.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.69 | 442.45 | 442.36 | 4885.35 | 1229.33 | 0 | FULL
G3 | 1280.63 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 546.9 | 547.03 | 4940.25 | 1278.35 | 0 | FULL
G4 | 1356.95 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 546.71 | 547.23 | 4875.32 | 1354.87 | 0 | FULL
G5 | 1406.01 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | N-1: Monroe - HRNCHTAP MS | 19.72 | 545.25 | 545.47 | 4892.56 | 1403.47 | 0 | FULL
G6 | 1107.27 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 548.71 | 549.04 | 4943.01 | 1104.9 | 0 | FULL
G7 | 1185.56 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 549.36 | 549.21 | 4878.79 | 1185.35 | 0 | FULL
G8 | 1229.17 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 545.76 | 545.89 | 4896.16 | 1228.75 | 0 | FULL
G9 | 618.68 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 541.9 | 542.42 | 4949.23 | 620.18 | 0 | FULL
G10 | 702.6 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 542.46 | 542.59 | 4885.01 | 701.24 | 0 | FULL
G11 | 776.14 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 541.58 | 542.1 | 4903.69 | 776.88 | 0 | FULL
G12 | 496.48 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 542.19 | 542.75 | 4961.6 | 496.11 | 0 | FULL
G13 | 582.5 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 543.48 | 544.15 | 4898.72 | 584.2 | 0 | FULL
G14 | 655.24 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 550.94 | 546.64 | 4918.28 | 654.32 | 0 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1216.68 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 504.02 | 504.27 | 4615.08 | 1214.81 | 0 | FULL
G1 | 1297.11 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 504.11 | 503.9 | 4550.49 | 1295.27 | 0 | FULL
G2 | 1368.15 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | N-1: Monroe - HRNCHTAP MS | 19.72 | 505.36 | 505.39 | 4568.53 | 1365.13 | 0 | FULL
G3 | 1132.42 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 504.35 | 504.87 | 4615.55 | 1131.98 | 0 | FULL
G4 | 1211.59 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 504.97 | 504.84 | 4551.01 | 1210.16 | 0 | FULL
G5 | 1287.98 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | N-1: Monroe - HRNCHTAP MS | 19.72 | 506.33 | 506.36 | 4569.83 | 1286.01 | 0 | FULL
G6 | 799.76 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 501.5 | 501.5 | 4614.85 | 798.46 | 0 | FULL
G7 | 1033.04 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 499.96 | 500.08 | 4554.37 | 1032.06 | 0 | FULL
G8 | 1111.15 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 19.83 | 506.04 | 506.59 | 4573.38 | 1110.86 | 0 | FULL
G9 | 497.21 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 504.74 | 505.09 | 4625.57 | 498.3 | 0 | FULL
G10 | 570.16 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 507 | 507.4 | 4561.56 | 570.06 | 0 | FULL
G11 | 664.05 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 497.83 | 498.09 | 4581.03 | 663.27 | 0 | FULL
G12 | 375.23 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 505.49 | 505.57 | 4638.67 | 376.42 | 0 | FULL
G13 | 455.03 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: Horse Ranch 230kV Bus | 23.11 | 505.11 | 505.2 | 4575.98 | 456.07 | 0 | FULL
G14 | 488.01 | Branch BOTHELL (46403) TO SNOH S1 (41327) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #1 | -13.26 | -467.65 | -467.77 | 4594.7 | 488.21 | 0 | FULL
023R2WINTER09v5NSH(COV-CRES BYP)