## 25F nomo
Massachusetts-Union Tap-Broad St 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 025
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6646.252
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 632.36 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1633.75 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
100 | 460 | 1092.44 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1591.31 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
100 | 775 | 1633.75 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1913.02 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
260 | 140 | 818.12 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 2463.58 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
260 | 460 | 1283.12 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3051.28 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
260 | 775 | 1591.31 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1092.44 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
525 | 140 | 1104.79 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1283.12 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
525 | 460 | 1504.5 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1504.5 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
525 | 775 | 1913.02 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2055.02 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
1000 | 140 | 1590.6 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2559.53 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
1000 | 460 | 2055.02 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 632.36 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
1000 | 775 | 2463.58 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 818.12 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
1400 | 140 | 2021.83 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1104.79 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
1400 | 460 | 2559.53 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1590.6 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
1400 | 775 | 3051.28 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2021.83 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Massachusetts-Union Tap-Broad St 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 025
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6337.3347
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1159.65 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2034.81 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
100 | 460 | 1668.27 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2222.33 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
100 | 775 | 2034.81 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2515.67 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
260 | 140 | 1558.32 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3026.34 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
260 | 460 | 1926.88 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 3463.43 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
260 | 775 | 2222.33 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1668.27 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
525 | 140 | 2100.06 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1926.88 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV]
525 | 460 | 2279.5 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2279.5 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 2515.67 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2726.09 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 3058.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3161.93 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2726.09 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1159.65 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3026.34 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1558.32 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3521.52 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2100.06 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3161.93 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3058.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3463.43 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 3521.52 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Massachusetts-Union Tap-Broad St 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 025
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6057.4153
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1426.88 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2335.8 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
100 | 460 | 1939.55 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2535.94 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
100 | 775 | 2335.8 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2825.24 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
260 | 140 | 1855.88 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3350.31 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
260 | 460 | 2123.66 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2972.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2535.94 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1939.55 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
525 | 140 | 2433.26 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2123.66 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
525 | 460 | 2413.32 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2413.32 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
525 | 775 | 2825.24 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2926.52 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV]
1000 | 140 | 3075.21 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3083.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2926.52 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1426.88 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3350.31 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1855.88 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3176.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2433.26 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3083.8 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3075.21 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 2972.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3176.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Massachusetts-Union Tap-Broad St 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 025
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4977.5767
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2542.74 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2540.74 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2798.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2652.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2540.74 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2852.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2512.21 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3180.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2636.58 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1751.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2652.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2798.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2808.79 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2636.58 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2835.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2835.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2852.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3148.56 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3145.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1911.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3148.56 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2542.74 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV]
1000 | 775 | 3180.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2512.21 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 2007.66 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2808.79 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1911.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3145.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1751.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2007.66 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Massachusetts-Union Tap-Broad St 115kV Line (SCL) (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 025
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4636.0247
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2422.08 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2464.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2445.31 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2580.47 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2464.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2726.82 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2540.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3067.41 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2539.95 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1558.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2580.47 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2445.31 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2675.03 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2539.95 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2705.54 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2705.54 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2726.82 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3046.9 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3016.41 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1626.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3046.9 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2422.08 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3067.41 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2540.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1749.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2675.03 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1626.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3016.41 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1558.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1749.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Massachusetts-Union Tap-Broad St 115kV Line (SCL) (COV-CRES BYP @ COV)
G0 | 632.36 | 1159.65 | 1426.88 | 2542.74 | 2422.08
G1 | 1092.44 | 1668.27 | 1939.55 | 2798.06 | 2445.31 | Season/Year: | WINTER 2009
G2 | 1633.75 | 2034.81 | 2335.8 | 2540.74 | 2464.62 | Direction: | South-to-North (SN)
G3 | 818.12 | 1558.32 | 1855.88 | 2512.21 | 2540.61 | Case Loads: | Heavy Loads
G4 | 1283.12 | 1926.88 | 2123.66 | 2636.58 | 2539.95 | Outage: | 025
G5 | 1591.31 | 2222.33 | 2535.94 | 2652.64 | 2580.47 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1104.79 | 2100.06 | 2433.26 | 2808.79 | 2675.03 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1504.5 | 2279.5 | 2413.32 | 2835.24 | 2705.54 | Study Person: | FRP9899
G8 | 1913.02 | 2515.67 | 2825.24 | 2852.37 | 2726.82 | Source: | 025WINTER09v2SNH(COV-CRES BYP)
G9 | 1590.6 | 3058.15 | 3075.21 | 3145.48 | 3016.41
G10 | 2055.02 | 2726.09 | 2926.52 | 3148.56 | 3046.9
G11 | 2463.58 | 3026.34 | 3350.31 | 3180.41 | 3067.41
G12 | 2021.83 | 3521.52 | 3176.93 | 2007.66 | 1749.23
G13 | 2559.53 | 3161.93 | 3083.8 | 1911.57 | 1626.29
G14 | 3051.28 | 3463.43 | 2972.21 | 1751.97 | 1558.19
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 025 | Massachusetts-Union Tap-Broad St 115kV Line (SCL) (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6646.252 | 632.36 | 1092.44 | 1633.75 | 818.12 | 1283.12 | 1591.31 | 1104.79 | 1504.5 | 1913.02 | 1590.6 | 2055.02 | 2463.58 | 2021.83 | 2559.53 | 3051.28
35F | 6337.3347 | 1159.65 | 1668.27 | 2034.81 | 1558.32 | 1926.88 | 2222.33 | 2100.06 | 2279.5 | 2515.67 | 3058.15 | 2726.09 | 3026.34 | 3521.52 | 3161.93 | 3463.43
45F | 6057.4153 | 1426.88 | 1939.55 | 2335.8 | 1855.88 | 2123.66 | 2535.94 | 2433.26 | 2413.32 | 2825.24 | 3075.21 | 2926.52 | 3350.31 | 3176.93 | 3083.8 | 2972.21
60F | 4977.5767 | 2542.74 | 2798.06 | 2540.74 | 2512.21 | 2636.58 | 2652.64 | 2808.79 | 2835.24 | 2852.37 | 3145.48 | 3148.56 | 3180.41 | 2007.66 | 1911.57 | 1751.97
70F | 4636.0247 | 2422.08 | 2445.31 | 2464.62 | 2540.61 | 2539.95 | 2580.47 | 2675.03 | 2705.54 | 2726.82 | 3016.41 | 3046.9 | 3067.41 | 1749.23 | 1626.29 | 1558.19

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 631.96 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | -3.86 | -225.77 | -225.87 | 6673.28 | 632.36 | -557.15 | FULL
G1 | 1092.08 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -224.62 | -224.51 | 6613.88 | 1092.44 | -798.24 | FULL
G2 | 1633.39 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -3.71 | -230.92 | -230.95 | 6642.13 | 1633.75 | -1083.13 | CTG_FAIL_IN_FULL
G3 | 817.93 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -225.83 | -225.92 | 6673.11 | 818.12 | -599.91 | FULL
G4 | 1282.83 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -224.79 | -224.83 | 6613.63 | 1283.12 | -843.74 | FULL
G5 | 1591.33 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -221.66 | -221.6 | 6635.92 | 1591.31 | -992.3 | FULL
G6 | 1104.74 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -225.64 | -225.74 | 6673.86 | 1104.79 | -645.29 | FULL
G7 | 1504.74 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -224.39 | -224.44 | 6614.51 | 1504.5 | -843.07 | FULL
G8 | 1913.18 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -222.39 | -222.49 | 6637.78 | 1913.02 | -1057.4 | FULL
G9 | 1590.82 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -4.02 | -225.64 | -225.58 | 6679.26 | 1590.6 | -709.85 | FULL
G10 | 2055.74 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -224.77 | -224.83 | 6620.58 | 2055.02 | -945.45 | FULL
G11 | 2463.91 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -222.92 | -222.81 | 6644.27 | 2463.58 | -1162.77 | FULL
G12 | 2022.24 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -4.02 | -225.35 | -225.26 | 6685.88 | 2021.83 | -803.04 | FULL
G13 | 2560.39 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | -3.86 | -225.06 | -225.13 | 6628.65 | 2559.53 | -1093.51 | FULL
G14 | 3051.69 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -231.48 | -231.48 | 6657.04 | 3051.28 | -1356.76 | CTG_FAIL_IN_FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1159.25 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.31 | -534.45 | -534.49 | 6352.59 | 1159.65 | -821.44 | FULL
G1 | 1668.26 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -3.71 | -232.31 | -232.34 | 6297.6 | 1668.27 | -1093.33 | CTG_FAIL_IN_FULL
G2 | 2035.2 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -231.93 | -231.94 | 6322.85 | 2034.81 | -1282.76 | CTG_FAIL_IN_FULL
G3 | 1558.25 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.31 | -533.3 | -533.34 | 6358.69 | 1558.32 | -996.67 | FULL
G4 | 1927.2 | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -235.81 | -235.86 | 6300.96 | 1926.88 | -1177.49 | CTG_FAIL_IN_FULL
G5 | 2223.03 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -231.8 | -231.78 | 6322.2 | 2222.33 | -1308.43 | CTG_FAIL_IN_FULL
G6 | 2100.33 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.31 | -530.61 | -530.68 | 6370.39 | 2100.06 | -1187.22 | FULL
G7 | 2279.94 | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | -3.71 | -236.16 | -236.16 | 6304.24 | 2279.5 | -1258.85 | CTG_FAIL_IN_FULL
G8 | 2516 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -231.89 | -231.87 | 6323.51 | 2515.67 | -1357.64 | CTG_FAIL_IN_FULL
G9 | 3058 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 519.81 | 519.73 | 6398.14 | 3058.15 | -1538.22 | CTG_FAIL_IN_FULL
G10 | 2726.63 | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -235.67 | -235.73 | 6309.24 | 2726.09 | -1314.41 | CTG_FAIL_IN_FULL
G11 | 3026.71 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -232.11 | -232.1 | 6331.19 | 3026.34 | -1461.74 | CTG_FAIL_IN_FULL
G12 | 3522.05 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 519.61 | 519.6 | 6408.61 | 3521.52 | -1642.95 | CTG_FAIL_IN_FULL
G13 | 3162.5 | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -235.79 | -235.81 | 6318.01 | 3161.93 | -1415.73 | CTG_FAIL_IN_FULL
G14 | 3463.97 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -231.9 | -231.9 | 6341.8 | 3463.43 | -1561.72 | CTG_FAIL_IN_FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1426.82 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.31 | -521.39 | -521.43 | 6075.4 | 1426.88 | -959.12 | FULL
G1 | 1940.33 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -233.02 | -232.98 | 6022.01 | 1939.55 | -1234.18 | CTG_FAIL_IN_FULL
G2 | 2336.35 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -232.15 | -232.15 | 6049.34 | 2335.8 | -1423.9 | CTG_FAIL_IN_FULL
G3 | 1856.02 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.31 | -521.98 | -522.03 | 6084.66 | 1855.88 | -1145.86 | FULL
G4 | 2124.42 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -233.07 | -233.03 | 6022.44 | 2123.66 | -1274.98 | CTG_FAIL_IN_FULL
G5 | 2536.18 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -232.87 | -232.85 | 6051.13 | 2535.94 | -1491.1 | CTG_FAIL_IN_FULL
G6 | 2433.63 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.31 | -520.44 | -520.51 | 6098.53 | 2433.26 | -1363.73 | FULL
G7 | 2414.31 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -233.12 | -233.08 | 6023.93 | 2413.32 | -1322.18 | CTG_FAIL_IN_FULL
G8 | 2825.59 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -232.88 | -232.87 | 6052.64 | 2825.24 | -1537.79 | CTG_FAIL_IN_FULL
G9 | 3075.77 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 504.34 | 504.49 | 6113.41 | 3075.21 | -1530.49 | CTG_FAIL_IN_FULL
G10 | 2926.88 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -232.99 | -232.98 | 6031.96 | 2926.52 | -1411.1 | CTG_FAIL_IN_FULL
G11 | 3350.95 | Branch EASTPINE (46425) TO EASTPINE (46427) CKT 1 [115.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -233.15 | -233.16 | 6061.98 | 3350.31 | -1633.03 | CTG_FAIL_IN_FULL
G12 | 3177.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -438.21 | -438 | 6107.19 | 3176.93 | -1439.78 | FULL
G13 | 3084.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -434.97 | -434.93 | 6030.61 | 3083.8 | -1347.67 | FULL
G14 | 2972.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -434.04 | -433.99 | 6036 | 2972.21 | -1241.9 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2543.34 | Branch BROAD ST (46409) TO EASTPINE (46425) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -3.77 | -232.08 | -232.08 | 5029.59 | 2542.74 | -1501.78 | CTG_FAIL_IN_FULL
G1 | 2798.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.07 | -2398.33 | -2398.16 | 4970.22 | 2798.06 | -1618.62 | CTG_FAIL_IN_FULL
G2 | 2541.13 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | N-1: Monroe - Custer #1 500kV | -67.01 | -2206.38 | -2207.3 | 4973.28 | 2540.74 | -1438.52 | FULL
G3 | 2512.68 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 12.75 | 449.66 | 449.87 | 5024.34 | 2512.21 | -1414.98 | FULL
G4 | 2636.72 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2220.01 | -2218.72 | 4958.85 | 2636.58 | -1453.75 | FULL
G5 | 2653.11 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2216.77 | -2215.11 | 4971.67 | 2652.64 | -1426.88 | FULL
G6 | 2809.21 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2214.88 | -2214.03 | 5027.41 | 2808.79 | -1471.15 | FULL
G7 | 2835.46 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2222.98 | -2221.98 | 4958.67 | 2835.24 | -1452.6 | FULL
G8 | 2852.53 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2214.54 | -2216.13 | 4970.65 | 2852.37 | -1420.5 | FULL
G9 | 3145.77 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2238.91 | -2239.71 | 5029.6 | 3145.48 | -1457 | FULL
G10 | 3148.9 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2216.55 | -2217.54 | 4959.91 | 3148.56 | -1419.6 | FULL
G11 | 3180.99 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2238.88 | -2239.67 | 4970.89 | 3180.41 | -1410.96 | FULL
G12 | 2007.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -424.07 | -423.95 | 4983.26 | 2007.66 | -635.73 | FULL
G13 | 1911.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -426.24 | -426.19 | 4912.28 | 1911.57 | -538.74 | FULL
G14 | 1751.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -417.17 | -417.02 | 4923.03 | 1751.97 | -410.62 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2422.12 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2131.97 | -2133.78 | 4689.3 | 2422.08 | -1386.39 | FULL
G1 | 2446.5 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2138.02 | -2139.97 | 4619.23 | 2445.31 | -1368.91 | FULL
G2 | 2465.03 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2140.58 | -2142.39 | 4631.01 | 2464.62 | -1349.17 | FULL
G3 | 2540.91 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2143.68 | -2144.45 | 4687.83 | 2540.61 | -1393.23 | FULL
G4 | 2540.32 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | -67.01 | -2095.21 | -2096.33 | 4616.98 | 2539.95 | -1368.86 | FULL
G5 | 2580.78 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.48 | -2155.42 | -2153.52 | 4629.88 | 2580.47 | -1360.1 | FULL
G6 | 2677.26 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.01 | -2128.41 | -2130.02 | 4684.73 | 2675.03 | -1352.34 | FULL
G7 | 2705.93 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.01 | -2135.36 | -2137.33 | 4615.23 | 2705.54 | -1337.52 | FULL
G8 | 2727.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.01 | -2127.62 | -2129.43 | 4628.22 | 2726.82 | -1313.48 | FULL
G9 | 3018.31 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.01 | -2130.25 | -2132.12 | 4686.93 | 3016.41 | -1346.12 | FULL
G10 | 3047.44 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.01 | -2137.75 | -2139.45 | 4617.3 | 3046.9 | -1330.82 | FULL
G11 | 3067.96 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -67.01 | -2147.54 | -2149.24 | 4630.02 | 3067.41 | -1313.69 | FULL
G12 | 1749.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -419.12 | -419.02 | 4643.39 | 1749.23 | -447.19 | FULL
G13 | 1624.17 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -416.51 | -416.39 | 4573.66 | 1626.29 | -335.33 | FULL
G14 | 1558.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -420.93 | -420.86 | 4586.66 | 1558.19 | -265.37 | FULL
025WINTER09v2SNH(COV-CRES BYP)