## 25F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 049
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6698.7427
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1111.92 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2350.52 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2320.58 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2649.91 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2350.52 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3150.53 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1797.52 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3595.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2738.34 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3650.48 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2649.91 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2320.58 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1691.63 | N-1: Bothell - SnoKing #2 230kV | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2738.34 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3209.68 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3209.68 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3150.53 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3599.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3346.58 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3635.83 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 3599.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1111.92 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3595.62 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1797.52 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3631.86 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G7 | 525 | 140 | 1691.63 | N-1: Bothell - SnoKing #2 230kV | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 3635.83 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 3346.58 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3650.48 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 3631.86 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 049
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6366.0447
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1675.61 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2382.14 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2411.85 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2764.08 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2382.14 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3249.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2173.07 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3546.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2791.88 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3581.58 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2764.08 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2411.85 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2612.93 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2791.88 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3230 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3230 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3249.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3534.93 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3302.2 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3575.12 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 3534.93 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1675.61 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3546.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2173.07 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3566.35 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G7 | 525 | 140 | 2612.93 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3575.12 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 3302.2 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3581.58 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 3566.35 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 049
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6076.4787
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1929.5 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2404.36 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2429.42 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2754.53 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2404.36 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3144.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2500.54 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3448.09 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2789.18 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3002.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2754.53 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2429.42 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2941.23 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2789.18 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3124.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3124.2 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3144.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3427.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3417.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 3095.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3427.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1929.5 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3448.09 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2500.54 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3213.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2941.23 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3095.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3417.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 3002.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3213.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 049
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4981.5347
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2777.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2811.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2777.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2649.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2811.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2852.78 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2604.47 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3169.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2645.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1796.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2649.19 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2777.45 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2812.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2645.94 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2819.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2819.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2852.78 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3150.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3144.47 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1944.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3150.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2777.91 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3169.41 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2604.47 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 2016.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2812.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1944.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3144.47 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1796.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2016.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 049
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4638.424
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2414.95 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2454.07 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2442.59 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2582.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2454.07 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2712.88 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2538.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 3067.49 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2562.76 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1585.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2582.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2442.59 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2672.85 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2562.76 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2691.07 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2691.07 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2712.88 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3041.47 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3017.51 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1665.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3041.47 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2414.95 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 3067.49 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2538.87 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1782.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2672.85 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1665.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3017.51 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1585.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1782.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
G0 | 1111.92 | 1675.61 | 1929.5 | 2777.91 | 2414.95
G1 | 2320.58 | 2411.85 | 2429.42 | 2777.45 | 2442.59 | Season/Year: | WINTER 2009
G2 | 2350.52 | 2382.14 | 2404.36 | 2811.57 | 2454.07 | Direction: | South-to-North (SN)
G3 | 1797.52 | 2173.07 | 2500.54 | 2604.47 | 2538.87 | Case Loads: | Heavy Loads
G4 | 2738.34 | 2791.88 | 2789.18 | 2645.94 | 2562.76 | Outage: | 049
G5 | 2649.91 | 2764.08 | 2754.53 | 2649.19 | 2582.51 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1691.63 | 2612.93 | 2941.23 | 2812.69 | 2672.85 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3209.68 | 3230 | 3124.2 | 2819.8 | 2691.07 | Study Person: | JGO7470
G8 | 3150.53 | 3249.91 | 3144.54 | 2852.78 | 2712.88 | Source: | 049WINTER09v2SNH
G9 | 3346.58 | 3302.2 | 3417.18 | 3144.47 | 3017.51
G10 | 3599.03 | 3534.93 | 3427.27 | 3150.88 | 3041.47
G11 | 3595.62 | 3546.49 | 3448.09 | 3169.41 | 3067.49
G12 | 3631.86 | 3566.35 | 3213.43 | 2016.89 | 1782.17
G13 | 3635.83 | 3575.12 | 3095.11 | 1944.06 | 1665.19
G14 | 3650.48 | 3581.58 | 3002.74 | 1796.09 | 1585.34
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 049 | Tacoma-Raver #1&2 500kV Line***Includes Tacoma 500/230kV Transformer Bank #5 (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6698.7427 | 1111.92 | 2320.58 | 2350.52 | 1797.52 | 2738.34 | 2649.91 | 1691.63 | 3209.68 | 3150.53 | 3346.58 | 3599.03 | 3595.62 | 3631.86 | 3635.83 | 3650.48
35F | 6366.0447 | 1675.61 | 2411.85 | 2382.14 | 2173.07 | 2791.88 | 2764.08 | 2612.93 | 3230 | 3249.91 | 3302.2 | 3534.93 | 3546.49 | 3566.35 | 3575.12 | 3581.58
45F | 6076.4787 | 1929.5 | 2429.42 | 2404.36 | 2500.54 | 2789.18 | 2754.53 | 2941.23 | 3124.2 | 3144.54 | 3417.18 | 3427.27 | 3448.09 | 3213.43 | 3095.11 | 3002.74
60F | 4981.5347 | 2777.91 | 2777.45 | 2811.57 | 2604.47 | 2645.94 | 2649.19 | 2812.69 | 2819.8 | 2852.78 | 3144.47 | 3150.88 | 3169.41 | 2016.89 | 1944.06 | 1796.09
70F | 4638.424 | 2414.95 | 2442.59 | 2454.07 | 2538.87 | 2562.76 | 2582.51 | 2672.85 | 2691.07 | 2712.88 | 3017.51 | 3041.47 | 3067.49 | 1782.17 | 1665.19 | 1585.34

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1111.73 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.54 | -546.25 | -546.3 | 6688.93 | 1111.92 | -858.4 | FULL
G1 | 2320.97 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -513.38 | -513.29 | 6669.66 | 2320.58 | -1520.85 | FULL
G2 | 2350.71 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -514.54 | -514.75 | 6677.5 | 2350.52 | -1510.01 | FULL
G3 | 1797.56 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.54 | -547.94 | -548.05 | 6707.31 | 1797.52 | -1193.72 | FULL
G4 | 2738.9 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -512.23 | -512.45 | 6680.57 | 2738.34 | -1700.12 | FULL
G5 | 2650.29 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -507.92 | -507.71 | 6685.48 | 2649.91 | -1607.75 | FULL
G6 | 1691.95 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #2 230kV | -4.52 | -529.87 | -522.34 | 6698.75 | 1691.63 | -996.08 | FULL
G7 | 3210.86 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -513.59 | -513.35 | 6694.49 | 3209.68 | -1845.13 | FULL
G8 | 3151.25 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -508.93 | -509.05 | 6698.6 | 3150.53 | -1780.27 | FULL
G9 | 3347.03 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.76 | 536.62 | 536.61 | 6751.95 | 3346.58 | -1754.06 | CTG_FAIL_IN_FULL
G10 | 3599.6 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2688.29 | -2688.88 | 6692.19 | 3599.03 | -1868.6 | CTG_FAIL_IN_FULL
G11 | 3595.78 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2671.27 | -2671.02 | 6703 | 3595.62 | -1833.27 | CTG_FAIL_IN_FULL
G12 | 3631.47 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3591.3 | 3592.73 | 6756.74 | 3631.86 | -1772.2 | FULL
G13 | 3636.48 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3596.92 | 3605.11 | 6683.56 | 3635.83 | -1737.58 | FULL
G14 | 3648.6 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3611.14 | 3609.82 | 6692.41 | 3650.48 | -1712.79 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1675.49 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.54 | -532.58 | -532.67 | 6372.93 | 1675.61 | -1142.33 | FULL
G1 | 2412.12 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -498.73 | -498.97 | 6335.47 | 2411.85 | -1527.53 | FULL
G2 | 2382.33 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -514.06 | -514.21 | 6344.28 | 2382.14 | -1484.93 | FULL
G3 | 2174.29 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.54 | -533.13 | -533.06 | 6386.63 | 2173.07 | -1361.7 | FULL
G4 | 2792.32 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -493.79 | -493.55 | 6345.51 | 2791.88 | -1687.64 | FULL
G5 | 2763.89 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -500.8 | -500.96 | 6354.48 | 2764.08 | -1633.27 | FULL
G6 | 2615.92 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.54 | -533.93 | -527.11 | 6396.41 | 2612.93 | -1482.27 | FULL
G7 | 3229.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2626.43 | -2625.24 | 6353.45 | 3230 | -1820.77 | CTG_FAIL_IN_FULL
G8 | 3251.94 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2624.19 | -2625.5 | 6363.51 | 3249.91 | -1806.13 | CTG_FAIL_IN_FULL
G9 | 3304.58 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 13.23 | 582.95 | 592.4 | 6414.3 | 3302.2 | -1680.45 | CTG_FAIL_IN_FULL
G10 | 3535.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2621.54 | -2621.66 | 6350.16 | 3534.93 | -1788.97 | CTG_FAIL_IN_FULL
G11 | 3547.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2610.41 | -2610.53 | 6361.32 | 3546.49 | -1774.12 | CTG_FAIL_IN_FULL
G12 | 3568.51 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3532.32 | 3531.3 | 6416.22 | 3566.35 | -1685.38 | FULL
G13 | 3575.84 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3540.04 | -3542.13 | 6343.6 | 3575.12 | -1661.58 | FULL
G14 | 3581.28 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3545.86 | -3547.71 | 6352.4 | 3581.58 | -1639.62 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1928.93 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.54 | -519.97 | -520.08 | 6097.69 | 1929.5 | -1273.54 | FULL
G1 | 2429.79 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -487.79 | -488.01 | 6048.35 | 2429.42 | -1534.95 | FULL
G2 | 2404.72 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -488.84 | -489.03 | 6055.56 | 2404.36 | -1492.29 | FULL
G3 | 2501 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -4.54 | -521.4 | -521.28 | 6117.15 | 2500.54 | -1540.33 | FULL
G4 | 2789.03 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -489.14 | -489.3 | 6059.32 | 2789.18 | -1673.95 | FULL
G5 | 2755.71 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -8.68 | -488.47 | -488.53 | 6066.46 | 2754.53 | -1629.51 | FULL
G6 | 2941.71 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.76 | 504.6 | 504.81 | 6125.19 | 2941.23 | -1672.36 | CTG_FAIL_IN_FULL
G7 | 3124.86 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2538.17 | -2538.17 | 6062.01 | 3124.2 | -1749.68 | CTG_FAIL_IN_FULL
G8 | 3145.06 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2538.45 | -2538.4 | 6072.02 | 3144.54 | -1734.07 | CTG_FAIL_IN_FULL
G9 | 3419.57 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2534.52 | -2536.12 | 6131.11 | 3417.18 | -1737.37 | CTG_FAIL_IN_FULL
G10 | 3427.94 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2531.59 | -2531.69 | 6058.8 | 3427.27 | -1719.57 | CTG_FAIL_IN_FULL
G11 | 3448.73 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2534.1 | -2534.17 | 6069.98 | 3448.09 | -1705.71 | CTG_FAIL_IN_FULL
G12 | 3213.96 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -435.45 | -435.4 | 6110.95 | 3213.43 | -1469.92 | FULL
G13 | 3095.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -435.94 | -435.91 | 6033.24 | 3095.11 | -1362.92 | FULL
G14 | 3003.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -434.23 | -434.2 | 6039.35 | 3002.74 | -1277.21 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2778.19 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2400.39 | -2400.1 | 5041.79 | 2777.91 | -1651.31 | CTG_FAIL_IN_FULL
G1 | 2777.56 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2387.53 | -2387.39 | 4972.01 | 2777.45 | -1617.9 | CTG_FAIL_IN_FULL
G2 | 2809.6 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.01 | -2394.36 | -2395.27 | 4983.34 | 2811.57 | -1609.61 | CTG_FAIL_IN_FULL
G3 | 2604.66 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2204.54 | -2202.51 | 5031.89 | 2604.47 | -1484.94 | FULL
G4 | 2646.14 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2232.67 | -2231.27 | 4960.45 | 2645.94 | -1466.84 | FULL
G5 | 2649.24 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2215.07 | -2213.22 | 4973.63 | 2649.19 | -1437.79 | FULL
G6 | 2813.04 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2224.64 | -2225.81 | 5029.42 | 2812.69 | -1480.98 | FULL
G7 | 2819.95 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2273.61 | -2272.09 | 4961.52 | 2819.8 | -1461.69 | FULL
G8 | 2853.28 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2223.04 | -2223.83 | 4971.83 | 2852.78 | -1444.3 | FULL
G9 | 3144.95 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2245.8 | -2246.49 | 5030.5 | 3144.47 | -1464.97 | FULL
G10 | 3151.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2226.47 | -2227.36 | 4961.59 | 3150.88 | -1431.33 | FULL
G11 | 3169.95 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2234.09 | -2234.96 | 4973.43 | 3169.41 | -1417.86 | FULL
G12 | 2017.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -420.08 | -419.93 | 4986.84 | 2016.89 | -648.96 | FULL
G13 | 1944.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -426.1 | -426.19 | 4916.68 | 1944.06 | -573.27 | FULL
G14 | 1794.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -417.87 | -417.81 | 4928.1 | 1796.09 | -453.7 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2414.96 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2132.98 | -2134.32 | 4690.94 | 2414.95 | -1406.01 | FULL
G1 | 2443.74 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2136.79 | -2138.23 | 4620.7 | 2442.59 | -1377.55 | FULL
G2 | 2455.34 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2136.63 | -2137.64 | 4633.06 | 2454.07 | -1355.27 | FULL
G3 | 2539.2 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2153.01 | -2153.68 | 4688.44 | 2538.87 | -1409.18 | FULL
G4 | 2563.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2157.82 | -2158.44 | 4618.96 | 2562.76 | -1391.2 | FULL
G5 | 2582.92 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.42 | -2152.54 | -2150.51 | 4632.17 | 2582.51 | -1363.73 | FULL
G6 | 2674.94 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.94 | -2135.92 | -2135.21 | 4685.56 | 2672.85 | -1370.9 | FULL
G7 | 2693.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.94 | -2123.02 | -2124.89 | 4617.16 | 2691.07 | -1339.62 | FULL
G8 | 2715.03 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.94 | -2131.21 | -2132.67 | 4629.09 | 2712.88 | -1328.85 | FULL
G9 | 3017.11 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.94 | -2137.94 | -2137.21 | 4688.67 | 3017.51 | -1362.48 | FULL
G10 | 3042.01 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.94 | -2143.54 | -2144.71 | 4619.9 | 3041.47 | -1343.68 | FULL
G11 | 3068.74 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -66.94 | -2147.05 | -2146.06 | 4632.53 | 3067.49 | -1320.1 | FULL
G12 | 1785.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -419.49 | -419.52 | 4648.17 | 1782.17 | -485.3 | FULL
G13 | 1665.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -418.09 | -417.99 | 4578.81 | 1665.19 | -382.36 | FULL
G14 | 1585.3 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -419.64 | -419.55 | 4592.2 | 1585.34 | -304.42 | FULL
049WINTER09v2SNH