## 25F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6588.32
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 336.56 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1917.33 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 1875.39 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2434.75 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1917.33 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3128.76 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1119.14 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3417.83 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2529.17 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3544.7 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2434.75 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1875.39 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2293.58 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2529.17 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3138.81 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 3138.81 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 3128.76 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3411.22 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3228.38 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3582.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3411.22 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 336.56 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3417.83 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1119.14 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3569.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G7 | 525 | 140 | 2293.58 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3582.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3228.38 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3544.7 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3569.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6448.4607
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 508.78 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1902.77 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2037 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2532.68 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 1902.77 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3066.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1193.5 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3347.95 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2542.45 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3304.87 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2532.68 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2037 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2177.56 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2542.45 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 3052.76 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3052.76 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3066.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3329.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3287.45 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3362.81 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3329.04 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 508.78 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3347.95 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1193.5 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 3422.12 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2177.56 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3362.81 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3287.45 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3304.87 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 3422.12 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6005.9953
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1289.33 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2096.42 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2119.27 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2597.08 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2096.42 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2982.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2046.54 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3019.9 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2647.64 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2821.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2597.08 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2119.27 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2791.87 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2647.64 | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2966.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2966.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2982.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3223.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3222.75 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 2868.72 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3223.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1289.33 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3019.9 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2046.54 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 2946.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2791.87 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 2868.72 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3222.75 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 2821.82 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2946.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4949.4133
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2388.06 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2426.34 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2411.1 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2524.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2426.34 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2690.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2492.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2823.43 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2508.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1766.75 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2524.53 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2411.1 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2644.96 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2508.89 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2665.46 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2665.46 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2690.26 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 2949.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 2934.22 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1801.16 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2949.37 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 2388.06 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2823.43 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2492.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1930.92 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2644.96 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1801.16 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2934.22 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1766.75 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1930.92 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 001R2
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4617.9807
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2305.29 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2339.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2325.71 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2384.74 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2339.88 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2554.05 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2345.9 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2677.1 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2368.79 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1294.43 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2384.74 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2325.71 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2511.99 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2368.79 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2536.37 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2536.37 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2554.05 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 2679.08 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2732.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 1380.18 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2679.08 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2305.29 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2677.1 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2345.9 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 1479.56 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2511.99 | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1380.18 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2732.14 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 1294.43 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1479.56 | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
G0 | 336.56 | 508.78 | 1289.33 | 2388.06 | 2305.29
G1 | 1875.39 | 2037 | 2119.27 | 2411.1 | 2325.71 | Season/Year: | WINTER 2009
G2 | 1917.33 | 1902.77 | 2096.42 | 2426.34 | 2339.88 | Direction: | South-to-North (SN)
G3 | 1119.14 | 1193.5 | 2046.54 | 2492.8 | 2345.9 | Case Loads: | Heavy Loads
G4 | 2529.17 | 2542.45 | 2647.64 | 2508.89 | 2368.79 | Outage: | 001R2
G5 | 2434.75 | 2532.68 | 2597.08 | 2524.53 | 2384.74 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2293.58 | 2177.56 | 2791.87 | 2644.96 | 2511.99 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3138.81 | 3052.76 | 2966.89 | 2665.46 | 2536.37 | Study Person: | FRP9899
G8 | 3128.76 | 3066.64 | 2982.72 | 2690.26 | 2554.05 | Source: | 001R2WINTER09v5SNH
G9 | 3228.38 | 3287.45 | 3222.75 | 2934.22 | 2732.14
G10 | 3411.22 | 3329.04 | 3223.37 | 2949.37 | 2679.08
G11 | 3417.83 | 3347.95 | 3019.9 | 2823.43 | 2677.1
G12 | 3569.61 | 3422.12 | 2946.14 | 1930.92 | 1479.56
G13 | 3582.82 | 3362.81 | 2868.72 | 1801.16 | 1380.18
G14 | 3544.7 | 3304.87 | 2821.82 | 1766.75 | 1294.43
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 001R2 | Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6588.32 | 336.56 | 1875.39 | 1917.33 | 1119.14 | 2529.17 | 2434.75 | 2293.58 | 3138.81 | 3128.76 | 3228.38 | 3411.22 | 3417.83 | 3569.61 | 3582.82 | 3544.7
35F | 6448.4607 | 508.78 | 2037 | 1902.77 | 1193.5 | 2542.45 | 2532.68 | 2177.56 | 3052.76 | 3066.64 | 3287.45 | 3329.04 | 3347.95 | 3422.12 | 3362.81 | 3304.87
45F | 6005.9953 | 1289.33 | 2119.27 | 2096.42 | 2046.54 | 2647.64 | 2597.08 | 2791.87 | 2966.89 | 2982.72 | 3222.75 | 3223.37 | 3019.9 | 2946.14 | 2868.72 | 2821.82
60F | 4949.4133 | 2388.06 | 2411.1 | 2426.34 | 2492.8 | 2508.89 | 2524.53 | 2644.96 | 2665.46 | 2690.26 | 2934.22 | 2949.37 | 2823.43 | 1930.92 | 1801.16 | 1766.75
70F | 4617.9807 | 2305.29 | 2325.71 | 2339.88 | 2345.9 | 2368.79 | 2384.74 | 2511.99 | 2536.37 | 2554.05 | 2732.14 | 2679.08 | 2677.1 | 1479.56 | 1380.18 | 1294.43

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 336.25 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.39 | -549.04 | -548.96 | 6568.55 | 336.56 | -383.22 | FULL
G1 | 1875.54 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -507.99 | -508.16 | 6548.82 | 1875.39 | -1267.64 | FULL
G2 | 1917.65 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -514.38 | -514.5 | 6559 | 1917.33 | -1270.97 | FULL
G3 | 1118.95 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.39 | -547.88 | -547.95 | 6581.75 | 1119.14 | -793.76 | FULL
G4 | 2528.66 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -515.44 | -515.36 | 6569.3 | 2529.17 | -1598.49 | FULL
G5 | 2435.03 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -504.53 | -504.6 | 6571.88 | 2434.75 | -1519.46 | FULL
G6 | 2293.82 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.39 | -548.33 | -548.28 | 6616.22 | 2293.58 | -1383.79 | FULL
G7 | 3139.28 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.25 | 536.78 | 536.78 | 6587.67 | 3138.81 | -1858.83 | CTG_FAIL_IN_FULL
G8 | 3127.57 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -512.52 | -512.31 | 6598.24 | 3128.76 | -1819.31 | FULL
G9 | 3228.11 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.25 | 536.32 | 536.14 | 6643.52 | 3228.38 | -1743.47 | CTG_FAIL_IN_FULL
G10 | 3412.52 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2703.31 | -2703.59 | 6580.44 | 3411.22 | -1825.89 | CTG_FAIL_IN_FULL
G11 | 3418.43 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2695.46 | -2695.49 | 6589.23 | 3417.83 | -1805.01 | CTG_FAIL_IN_FULL
G12 | 3570.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2692.02 | -2693.62 | 6650.22 | 3569.61 | -1811.1 | CTG_FAIL_IN_FULL
G13 | 3583.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -10.14 | -488.41 | -488.11 | 6576.77 | 3582.82 | -1792.5 | CTG_FAIL_IN_FULL
G14 | 3545.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -10.14 | -487.07 | -487.07 | 6583.19 | 3544.7 | -1746.22 | CTG_FAIL_IN_FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 509.9 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.39 | -535.87 | -535.78 | 6435.18 | 508.78 | -457.67 | FULL
G1 | 2037.22 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -496.45 | -496.23 | 6416.05 | 2037 | -1345.66 | FULL
G2 | 1902.94 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -490.3 | -490.09 | 6420.4 | 1902.77 | -1233.84 | FULL
G3 | 1193.52 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.39 | -533.32 | -533.38 | 6447.86 | 1193.5 | -802.73 | FULL
G4 | 2542.7 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -493.43 | -493.28 | 6430.84 | 2542.45 | -1580.86 | FULL
G5 | 2532.99 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -495.21 | -495.09 | 6438.98 | 2532.68 | -1550.91 | FULL
G6 | 2177.93 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -3.44 | -517.77 | -534.58 | 6478.61 | 2177.56 | -1293.04 | FULL
G7 | 3053.46 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2619.13 | -2619.2 | 6443.83 | 3052.76 | -1778.04 | CTG_FAIL_IN_FULL
G8 | 3067.07 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2618.34 | -2618.3 | 6452.02 | 3066.64 | -1756.55 | CTG_FAIL_IN_FULL
G9 | 3288.03 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.25 | 519.09 | 519.38 | 6508.83 | 3287.45 | -1754.99 | CTG_FAIL_IN_FULL
G10 | 3331.55 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2625.92 | -2627.76 | 6438.2 | 3329.04 | -1753.19 | CTG_FAIL_IN_FULL
G11 | 3348.51 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2629.63 | -2629.67 | 6447.8 | 3347.95 | -1739.58 | CTG_FAIL_IN_FULL
G12 | 3421.95 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -10.14 | -478.61 | -478.57 | 6505.06 | 3422.12 | -1702.87 | CTG_FAIL_IN_FULL
G13 | 3363.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -10.14 | -477.52 | -477.52 | 6428.4 | 3362.81 | -1642.23 | CTG_FAIL_IN_FULL
G14 | 3305.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -10.14 | -477.48 | -477.47 | 6434.85 | 3304.87 | -1568.4 | CTG_FAIL_IN_FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1289.03 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.39 | -520.73 | -520.81 | 6014.08 | 1289.33 | -901.3 | FULL
G1 | 2119.43 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -486.04 | -486.11 | 5975.51 | 2119.27 | -1361.06 | FULL
G2 | 2096.61 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -481.27 | -481.06 | 5982.64 | 2096.42 | -1308.51 | FULL
G3 | 2046.85 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -3.39 | -521.51 | -521.45 | 6035.96 | 2046.54 | -1290.88 | FULL
G4 | 2648.09 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -488.39 | -488.31 | 5993.18 | 2647.64 | -1625.48 | FULL
G5 | 2597.42 | Branch MURRAY (40767) TO SNOH S1 (41327) CKT 1 [230.00 - 230.00 kV] | N-2: Both - Samm - & Sedro - Both - HRanch 230kV | -7.76 | -482.3 | -482.24 | 5998.52 | 2597.08 | -1568.69 | FULL
G6 | 2792.24 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 10.25 | 504.46 | 504.42 | 6058.96 | 2791.87 | -1630.66 | CTG_FAIL_IN_FULL
G7 | 2967.29 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2532.02 | -2531.72 | 5995.53 | 2966.89 | -1707.26 | CTG_FAIL_IN_FULL
G8 | 2983.09 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2532.69 | -2532.55 | 6005.63 | 2982.72 | -1692.3 | CTG_FAIL_IN_FULL
G9 | 3223.9 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2540.02 | -2540.04 | 6063.41 | 3222.75 | -1702 | CTG_FAIL_IN_FULL
G10 | 3224.46 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2527.5 | -2527.47 | 5991.14 | 3223.37 | -1676.24 | CTG_FAIL_IN_FULL
G11 | 3020.36 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | N-1: Monroe - Custer #1 500kV | -71 | -2330.05 | -2329.02 | 5995.69 | 3019.9 | -1525.9 | FULL
G12 | 2946.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -10.68 | -443.34 | -443.35 | 6040.39 | 2946.14 | -1390.46 | FULL
G13 | 2869.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -10.68 | -443.14 | -443.21 | 5966.34 | 2868.72 | -1313.26 | FULL
G14 | 2822.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -10.68 | -442.14 | -442.41 | 5972.95 | 2821.82 | -1249.44 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2388.04 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | N-1: Monroe - Custer #1 500kV | -71 | -2198.24 | -2196.59 | 5004.37 | 2388.06 | -1450.85 | FULL
G1 | 2411.66 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2219.5 | -2217.95 | 4932.18 | 2411.1 | -1426.89 | FULL
G2 | 2426.68 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | N-1: Monroe - Custer #1 500kV | -71 | -2211.62 | -2210.27 | 4945.41 | 2426.34 | -1408.9 | FULL
G3 | 2492.91 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2215.26 | -2214.43 | 5001.38 | 2492.8 | -1450.46 | FULL
G4 | 2508.69 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2225.16 | -2224.14 | 4932.16 | 2508.89 | -1432.74 | FULL
G5 | 2524.93 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2229.87 | -2228.99 | 4942.27 | 2524.53 | -1418.11 | FULL
G6 | 2645.09 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2213.04 | -2214.7 | 4998.91 | 2644.96 | -1439.22 | FULL
G7 | 2666.55 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2219.46 | -2220.96 | 4928.6 | 2665.46 | -1423.43 | FULL
G8 | 2691.43 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2226.1 | -2225.22 | 4940.13 | 2690.26 | -1408.61 | FULL
G9 | 2936.8 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2240.93 | -2241.86 | 4999.09 | 2934.22 | -1419.46 | FULL
G10 | 2947.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2235.64 | -2233.73 | 4928.93 | 2949.37 | -1400.55 | FULL
G11 | 2823.1 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 3.25 | 113.61 | 113.56 | 4938.39 | 2823.43 | -1294.43 | FULL
G12 | 1931.15 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | 7.9 | 511.66 | 511.66 | 4959.46 | 1930.92 | -680.43 | FULL
G13 | 1800.96 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | 7.9 | 510.2 | 510.2 | 4888.69 | 1801.16 | -577.01 | FULL
G14 | 1766.57 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | 7.9 | 511.05 | 511.02 | 4901.23 | 1766.75 | -525.32 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2305.6 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2129.25 | -2130.64 | 4672.85 | 2305.29 | -1362.75 | FULL
G1 | 2325.91 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | -71.01 | -2116.49 | -2117.99 | 4601.3 | 2325.71 | -1350.41 | FULL
G2 | 2340.1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2124.97 | -2126.31 | 4615.69 | 2339.88 | -1324.29 | FULL
G3 | 2346.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -71 | -2136.09 | -2134.72 | 4668.42 | 2345.9 | -1334.94 | FULL
G4 | 2369.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -71 | -2141.67 | -2140.72 | 4598.81 | 2368.79 | -1319.48 | FULL
G5 | 2384.35 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -71 | -2145.86 | -2144.59 | 4610.54 | 2384.74 | -1304.04 | FULL
G6 | 2513.73 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -71 | -2131.43 | -2133.43 | 4666.72 | 2511.99 | -1330.48 | FULL
G7 | 2538.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -71 | -2138.34 | -2140.25 | 4597.16 | 2536.37 | -1315.36 | FULL
G8 | 2555.88 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4516 Cust-Mon #1 500kV & Mon Caps | -71 | -2138.4 | -2140.5 | 4609.77 | 2554.05 | -1294.58 | FULL
G9 | 2732.17 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 3.25 | 109.48 | 109.42 | 4664.66 | 2732.14 | -1271.07 | FULL
G10 | 2679.42 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 3.25 | 109.64 | 109.6 | 4593.36 | 2679.08 | -1213.24 | FULL
G11 | 2677.82 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 3.25 | 110.45 | 110.5 | 4604.69 | 2677.1 | -1183.2 | FULL
G12 | 1479.64 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | 7.9 | 500.47 | 500.41 | 4629.81 | 1479.56 | -380.35 | FULL
G13 | 1380.06 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | 7.9 | 499.83 | 499.75 | 4561.13 | 1380.18 | -293.1 | FULL
G14 | 1294.97 | Branch SEDRO (42100) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1246 Cust-Port Wy 230/115kV & Cust 500/230kV Bk#1 | 7.9 | 499.45 | 499.35 | 4574.8 | 1294.43 | -220.85 | FULL
001R2WINTER09v5SNH