## 25F nomo
Tacoma-Covington #2 230kV Line ***Includes Christopher Tap-O’Brien section of Tacoma-Covington #2 Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 047
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6612.538
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -1415.57 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | -203.52 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | -768.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 9.28 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | -203.52 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 318.98 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | -1138.81 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 914.24 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | -555.64 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1474.25 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 9.28 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | -768.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | -835.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | -555.64 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | -218.42 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | -218.42 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 318.98 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 395.07 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | -210.01 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 878.33 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 395.07 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -1415.57 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 914.24 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -1138.81 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 319.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -835.7 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 878.33 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | -210.01 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1474.25 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 319.9 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Tacoma-Covington #2 230kV Line ***Includes Christopher Tap-O’Brien section of Tacoma-Covington #2 Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 047
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6283.63
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -882.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 261.06 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | -300.86 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 493.36 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 261.06 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 796.46 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | -653.22 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1386.21 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | -48.93 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1933.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 493.36 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | -300.86 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | -298.92 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | -48.93 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 283.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 283.12 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 796.46 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 849.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 297.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1359.33 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 849.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -882.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1386.21 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -653.22 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 814.21 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -298.92 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1359.33 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 297.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1933.65 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 814.21 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Tacoma-Covington #2 230kV Line ***Includes Christopher Tap-O’Brien section of Tacoma-Covington #2 Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 047
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6005.7747
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -381.11 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 730.07 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 193.86 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 950.58 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 730.07 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1295.82 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 140 | -139.57 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1860.66 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 418.27 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 2350.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 950.58 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 193.86 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 200.13 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 418.27 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 738.5 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 738.5 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1295.82 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1309.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 767.78 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1829.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 1309.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -381.11 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1860.66 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -139.57 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1271.38 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 200.13 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1829.37 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 767.78 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2350.68 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1271.38 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Tacoma-Covington #2 230kV Line ***Includes Christopher Tap-O’Brien section of Tacoma-Covington #2 Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 047
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4962.4933
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1532.81 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2570.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
100 | 460 | 2090.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2918.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2570.41 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2864.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1755.85 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3305.78 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 460 | 2231.94 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1795.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2918.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2090.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2017.8 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2231.94 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2543.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2543.87 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2864.32 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3125.2 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2588.53 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1945.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3125.2 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1532.81 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3305.78 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1755.85 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2045.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2017.8 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1945.65 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2588.53 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1795.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2045.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Tacoma-Covington #2 230kV Line ***Includes Christopher Tap-O’Brien section of Tacoma-Covington #2 Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 047
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4630.5967
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1985.89 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2440.36 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2434 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2566.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2440.36 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2782.74 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2202.44 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3075.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2544.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1599.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2566.18 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2434 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2520.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2544.63 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2741.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2741.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2782.74 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3058.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3036.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1700.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3058.06 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1985.89 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3075.86 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2202.44 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1810.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2520.67 | N-2: Echo Lk-Maple VL/Rocky Rch-ML | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1700.53 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3036.27 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1599.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1810.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Tacoma-Covington #2 230kV Line ***Includes Christopher Tap-O’Brien section of Tacoma-Covington #2 Line (COV-CRES BYP @ COV)
G0 | -1415.57 | -882.37 | -381.11 | 1532.81 | 1985.89
G1 | -768.67 | -300.86 | 193.86 | 2090.67 | 2434 | Season/Year: | WINTER 2009
G2 | -203.52 | 261.06 | 730.07 | 2570.41 | 2440.36 | Direction: | South-to-North (SN)
G3 | -1138.81 | -653.22 | -139.57 | 1755.85 | 2202.44 | Case Loads: | Heavy Loads
G4 | -555.64 | -48.93 | 418.27 | 2231.94 | 2544.63 | Outage: | 047
G5 | 9.28 | 493.36 | 950.58 | 2918.48 | 2566.18 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | -835.7 | -298.92 | 200.13 | 2017.8 | 2520.67 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | -218.42 | 283.12 | 738.5 | 2543.87 | 2741.72 | Study Person: | FRP9899
G8 | 318.98 | 796.46 | 1295.82 | 2864.32 | 2782.74 | Source: | 047WINTER09v1SNH
G9 | -210.01 | 297.65 | 767.78 | 2588.53 | 3036.27
G10 | 395.07 | 849.67 | 1309.37 | 3125.2 | 3058.06
G11 | 914.24 | 1386.21 | 1860.66 | 3305.78 | 3075.86
G12 | 319.9 | 814.21 | 1271.38 | 2045.11 | 1810.23
G13 | 878.33 | 1359.33 | 1829.37 | 1945.65 | 1700.53
G14 | 1474.25 | 1933.65 | 2350.68 | 1795.56 | 1599.58
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 047 | Tacoma-Covington #2 230kV Line ***Includes Christopher Tap-O’Brien section of Tacoma-Covington #2 Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6612.538 | -1415.57 | -768.67 | -203.52 | -1138.81 | -555.64 | 9.28 | -835.7 | -218.42 | 318.98 | -210.01 | 395.07 | 914.24 | 319.9 | 878.33 | 1474.25
35F | 6283.63 | -882.37 | -300.86 | 261.06 | -653.22 | -48.93 | 493.36 | -298.92 | 283.12 | 796.46 | 297.65 | 849.67 | 1386.21 | 814.21 | 1359.33 | 1933.65
45F | 6005.7747 | -381.11 | 193.86 | 730.07 | -139.57 | 418.27 | 950.58 | 200.13 | 738.5 | 1295.82 | 767.78 | 1309.37 | 1860.66 | 1271.38 | 1829.37 | 2350.68
60F | 4962.4933 | 1532.81 | 2090.67 | 2570.41 | 1755.85 | 2231.94 | 2918.48 | 2017.8 | 2543.87 | 2864.32 | 2588.53 | 3125.2 | 3305.78 | 2045.11 | 1945.65 | 1795.56
70F | 4630.5967 | 1985.89 | 2434 | 2440.36 | 2202.44 | 2544.63 | 2566.18 | 2520.67 | 2741.72 | 2782.74 | 3036.27 | 3058.06 | 3075.86 | 1810.23 | 1700.53 | 1599.58

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -1414.09 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 521.83 | 521.79 | 6653.12 | -1415.57 | 604.18 | FULL
G1 | -769.08 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.49 | 522.53 | 6585.71 | -768.67 | 269.35 | FULL
G2 | -204.98 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.44 | 522.48 | 6598.21 | -203.52 | -17.62 | FULL
G3 | -1137.6 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.59 | 522.59 | 6650.93 | -1138.81 | 512.29 | FULL
G4 | -556.17 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.93 | 522.96 | 6583.74 | -555.64 | 217.23 | FULL
G5 | 7.99 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.38 | 522.41 | 6593.96 | 9.28 | -64.77 | FULL
G6 | -837.12 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.84 | 522.82 | 6650.44 | -835.7 | 464.08 | FULL
G7 | -219.43 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 523.33 | 523.36 | 6581.13 | -218.42 | 148.63 | FULL
G8 | 318.19 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.65 | 522.68 | 6594.74 | 318.98 | -122.77 | FULL
G9 | -210.88 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 523.42 | 523.43 | 6652.75 | -210.01 | 319.48 | FULL
G10 | 394.61 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 523.91 | 523.83 | 6584.06 | 395.07 | 10.4 | FULL
G11 | 914.08 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.72 | 522.74 | 6602.31 | 914.24 | -263.52 | FULL
G12 | 319.32 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 523.65 | 523.66 | 6655.63 | 319.9 | 176.63 | FULL
G13 | 876.85 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 523.35 | 523.39 | 6590.48 | 878.33 | -111.53 | FULL
G14 | 1473.76 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 522.13 | 522.15 | 6610.86 | 1474.25 | -424.66 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -882.19 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.25 | 507.28 | 6320.24 | -882.37 | 347.49 | FULL
G1 | -302.38 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.47 | 507.51 | 6254.57 | -300.86 | 48.16 | FULL
G2 | 259.5 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 506.99 | 506.94 | 6268.31 | 261.06 | -239.36 | FULL
G3 | -653.03 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.77 | 507.76 | 6318.79 | -653.22 | 281.65 | FULL
G4 | -50.16 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 508.18 | 508.16 | 6249.31 | -48.93 | -24.21 | FULL
G5 | 491.82 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.27 | 507.3 | 6268.49 | 493.36 | -309.02 | FULL
G6 | -299.92 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 508.11 | 508.09 | 6318.44 | -298.92 | 200.37 | FULL
G7 | 281.53 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 508.18 | 508.21 | 6249.96 | 283.12 | -93.24 | FULL
G8 | 795.48 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.13 | 507.19 | 6269.47 | 796.46 | -358.23 | FULL
G9 | 296.93 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 508.48 | 508.39 | 6321.05 | 297.65 | 74.3 | FULL
G10 | 849.4 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.81 | 507.83 | 6257.05 | 849.67 | -211.26 | FULL
G11 | 1384.11 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.01 | 507.02 | 6278.15 | 1386.21 | -496.73 | FULL
G12 | 812.54 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 508.52 | 508.52 | 6327.57 | 814.21 | -67.33 | FULL
G13 | 1359.18 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.73 | 507.61 | 6265.01 | 1359.33 | -350.12 | FULL
G14 | 1933.83 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 507.01 | 507.06 | 6288.04 | 1933.65 | -650.78 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -381.44 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 495.39 | 495.4 | 6039.19 | -381.11 | 78.77 | FULL
G1 | 193.05 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 495.23 | 495.29 | 5970.71 | 193.86 | -211.03 | FULL
G2 | 728.41 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 494.29 | 494.31 | 5992.82 | 730.07 | -495.68 | FULL
G3 | -140.81 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 495.84 | 495.85 | 6035.27 | -139.57 | 9.94 | FULL
G4 | 417.83 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 495.28 | 495.3 | 5970.69 | 418.27 | -275.13 | FULL
G5 | 949.92 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 494.57 | 494.59 | 5993.41 | 950.58 | -557.92 | FULL
G6 | 199.44 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 496.19 | 496.19 | 6034.22 | 200.13 | -61.14 | FULL
G7 | 738.19 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 495.36 | 495.34 | 5972.35 | 738.5 | -338.74 | FULL
G8 | 1296.01 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 494.98 | 495 | 5995.7 | 1295.82 | -633.3 | FULL
G9 | 767.14 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 495.93 | 495.95 | 6041.51 | 767.78 | -179.27 | FULL
G10 | 1309.26 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 495.1 | 495.04 | 5980.59 | 1309.37 | -460.21 | FULL
G11 | 1859.93 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 494.93 | 494.91 | 6004.7 | 1860.66 | -752.06 | FULL
G12 | 1271.47 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 495.62 | 495.49 | 6049.48 | 1271.38 | -314.6 | FULL
G13 | 1829.14 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 494.78 | 494.8 | 5990.3 | 1829.37 | -613.56 | FULL
G14 | 2351.02 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 494.28 | 494.36 | 6015.68 | 2350.68 | -883.61 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1533.06 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 475.18 | 475.22 | 4986.26 | 1532.81 | -903.72 | FULL
G1 | 2089.15 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 474.93 | 474.9 | 4935.98 | 2090.67 | -1197.21 | FULL
G2 | 2570.78 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 474.12 | 474.16 | 4969.56 | 2570.41 | -1450.94 | FULL
G3 | 1755.84 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 474.38 | 474.49 | 4989.42 | 1755.85 | -961.83 | FULL
G4 | 2233.92 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 474.24 | 474.18 | 4937.59 | 2231.94 | -1215.96 | FULL
G5 | 2918.95 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.05 | -2410.83 | -2410.1 | 4974.87 | 2918.48 | -1588.2 | CTG_FAIL_IN_FULL
G6 | 2017.43 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 474.45 | 474.52 | 4991.69 | 2017.8 | -1004.31 | FULL
G7 | 2543.69 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 474.03 | 473.95 | 4942.04 | 2543.87 | -1282.19 | FULL
G8 | 2864.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2240.6 | -2241.44 | 4966.25 | 2864.32 | -1434.78 | FULL
G9 | 2588.77 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 474.65 | 474.61 | 5002.98 | 2588.53 | -1124.52 | FULL
G10 | 3125.42 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 473.98 | 473.91 | 4955.29 | 3125.2 | -1412.77 | FULL
G11 | 3307.1 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3277.66 | 3274.74 | 4970.96 | 3305.78 | -1483.71 | FULL
G12 | 2045.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -425.41 | -425.35 | 4981.55 | 2045.11 | -650.36 | FULL
G13 | 1947.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -426.9 | -426.94 | 4910.89 | 1945.65 | -567.3 | FULL
G14 | 1795.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -421.7 | -421.62 | 4922.07 | 1795.56 | -444.26 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1987.62 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 459.3 | 459.27 | 4665.16 | 1985.89 | -1135.78 | FULL
G1 | 2435.96 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2144.54 | -2145.88 | 4615.18 | 2434 | -1370.71 | FULL
G2 | 2439.64 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2123.65 | -2124.66 | 4628.46 | 2440.36 | -1345.39 | FULL
G3 | 2202.48 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 459.33 | 459.44 | 4668.31 | 2202.44 | -1202.79 | FULL
G4 | 2544.94 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2137.42 | -2138.95 | 4615.25 | 2544.63 | -1362.29 | FULL
G5 | 2565.57 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2149.41 | -2150.39 | 4625.54 | 2566.18 | -1347.87 | FULL
G6 | 2520.96 | Branch COVINGTN (40303) TO CRESTON (46415) CKT 1 [230.00 - 230.00 kV] | N-2: Echo Lk-Maple VL/Rocky Rch-ML | 4.14 | 459.15 | 459.25 | 4672.14 | 2520.67 | -1264.39 | FULL
G7 | 2744.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2142.37 | -2142.99 | 4613.47 | 2741.72 | -1355.51 | FULL
G8 | 2785.18 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2167.22 | -2165.99 | 4625.68 | 2782.74 | -1355.85 | FULL
G9 | 3038.8 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2149.33 | -2147.85 | 4684.59 | 3036.27 | -1360.36 | FULL
G10 | 3058.48 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2151.85 | -2150.47 | 4615.13 | 3058.06 | -1340.94 | FULL
G11 | 3078.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.46 | -2145.02 | -2143.46 | 4628.45 | 3075.86 | -1311.8 | FULL
G12 | 1810.76 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -424.84 | -424.78 | 4642.58 | 1810.23 | -486.06 | FULL
G13 | 1700.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -422.7 | -422.74 | 4572.99 | 1700.53 | -382.92 | FULL
G14 | 1599.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.54 | -423.17 | -423.13 | 4586.02 | 1599.58 | -298.9 | FULL
047WINTER09v1SNH