## 25F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 027
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6646.0627
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 703.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 831.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 749.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1260.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 831.45 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2106.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1153.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2087.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1212.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1954.55 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1260.93 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 749.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2008.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1212.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2059.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2059.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2106.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2044.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 1979.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 2721.31 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 2044.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 703.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2087.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1153.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2838.94 | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2008.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2721.31 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1979.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 1954.55 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2838.94 | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 027
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6321.112
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 883.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 989.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 927.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1403.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 989.4 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2225.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1298.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2913.14 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1358.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2147.05 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1403.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 927.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2130.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1358.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2170.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2170.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2225.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2206.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2157.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 2776.35 | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2206.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 883.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2913.14 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1298.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2662.78 | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2130.01 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2776.35 | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2157.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 2147.05 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2662.78 | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 027
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6035.2113
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 735.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 837.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 764.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1243.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 837.34 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2077.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1153.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2289.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1196.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2429.78 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1243.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 764.42 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1979.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1196.89 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2035.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2035.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2077.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2242.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2198.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 2603.46 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2242.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 735.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2289.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1153.35 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2557.86 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1979.71 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2603.46 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2198.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 2429.78 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2557.86 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 027
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4973.3373
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1345.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1459.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1400.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1843.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1459.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2601.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 1744.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2597.33 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1797.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2138.69 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 1843.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1400.22 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2511.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1797.58 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2555.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2555.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2601.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2708.09 | BFR: 4684 Mon-Cust #2 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2697.99 | BFR: 4684 Mon-Cust #2 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2153.07 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2708.09 | BFR: 4684 Mon-Cust #2 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1345.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2597.33 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1744.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2105.3 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2511.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 2153.07 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2697.99 | BFR: 4684 Mon-Cust #2 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2138.69 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2105.3 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 027
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4632.9713
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1470.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1579.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1519.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1955.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1579.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2348.68 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 1857.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1803.74 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 1906.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1283.38 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 1955.28 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 1519.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2606.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1906.38 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2643.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2643.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 2348.68 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2386 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2612.89 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1845.42 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2386 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1470.2 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1803.74 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1857.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 1941.29 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2606.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 1845.42 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2612.89 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1283.38 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1941.29 | N-1: Murray - Sedro NT 230kV | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
G0 | 703.07 | 883.1 | 735.51 | 1345.82 | 1470.2
G1 | 749.06 | 927.02 | 764.42 | 1400.22 | 1519.24 | Season/Year: | WINTER 2009
G2 | 831.45 | 989.4 | 837.34 | 1459.24 | 1579.28 | Direction: | North-to-South (NS)
G3 | 1153.15 | 1298.71 | 1153.35 | 1744.62 | 1857.27 | Case Loads: | Heavy Loads
G4 | 1212.91 | 1358.1 | 1196.89 | 1797.58 | 1906.38 | Outage: | 027
G5 | 1260.93 | 1403.92 | 1243.38 | 1843.11 | 1955.28 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2008.19 | 2130.01 | 1979.71 | 2511.16 | 2606.7 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2059.56 | 2170.22 | 2035.33 | 2555.38 | 2643.51 | Study Person: | FRP9899
G8 | 2106.2 | 2225.22 | 2077.27 | 2601.13 | 2348.68 | Source: | 027WINTER09v2NSH
G9 | 1979.74 | 2157.02 | 2198.94 | 2697.99 | 2612.89
G10 | 2044.33 | 2206.33 | 2242.74 | 2708.09 | 2386
G11 | 2087.51 | 2913.14 | 2289.49 | 2597.33 | 1803.74
G12 | 2838.94 | 2662.78 | 2557.86 | 2105.3 | 1941.29
G13 | 2721.31 | 2776.35 | 2603.46 | 2153.07 | 1845.42
G14 | 1954.55 | 2147.05 | 2429.78 | 2138.69 | 1283.38
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 027 | Monroe-Custer #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6646.0627 | 703.07 | 749.06 | 831.45 | 1153.15 | 1212.91 | 1260.93 | 2008.19 | 2059.56 | 2106.2 | 1979.74 | 2044.33 | 2087.51 | 2838.94 | 2721.31 | 1954.55
35F | 6321.112 | 883.1 | 927.02 | 989.4 | 1298.71 | 1358.1 | 1403.92 | 2130.01 | 2170.22 | 2225.22 | 2157.02 | 2206.33 | 2913.14 | 2662.78 | 2776.35 | 2147.05
45F | 6035.2113 | 735.51 | 764.42 | 837.34 | 1153.35 | 1196.89 | 1243.38 | 1979.71 | 2035.33 | 2077.27 | 2198.94 | 2242.74 | 2289.49 | 2557.86 | 2603.46 | 2429.78
60F | 4973.3373 | 1345.82 | 1400.22 | 1459.24 | 1744.62 | 1797.58 | 1843.11 | 2511.16 | 2555.38 | 2601.13 | 2697.99 | 2708.09 | 2597.33 | 2105.3 | 2153.07 | 2138.69
70F | 4632.9713 | 1470.2 | 1519.24 | 1579.28 | 1857.27 | 1906.38 | 1955.28 | 2606.7 | 2643.51 | 2348.68 | 2612.89 | 2386 | 1803.74 | 1941.29 | 1845.42 | 1283.38

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 702.72 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 479.33 | 479.09 | 6654.06 | 703.07 | 269.82 | FULL
G1 | 748.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 479.67 | 479.43 | 6582.94 | 749.06 | 313.22 | FULL
G2 | 831.35 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 481.66 | 481.45 | 6595.12 | 831.45 | 378.23 | FULL
G3 | 1154.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 487.19 | 486.79 | 6649.61 | 1153.15 | 532.74 | FULL
G4 | 1215.08 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 487.49 | 487.06 | 6580.61 | 1212.91 | 592.46 | FULL
G5 | 1262.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 486.96 | 487.26 | 6593.64 | 1260.93 | 645.79 | FULL
G6 | 2014.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 492.48 | 492.16 | 6670.94 | 2008.19 | 1052.4 | FULL
G7 | 2067.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 492.5 | 492.37 | 6604.98 | 2059.56 | 1107.23 | FULL
G8 | 2115.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 492.3 | 492.02 | 6619.74 | 2106.2 | 1159.41 | FULL
G9 | 1989.11 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -4.95 | -96 | -137.9 | 6715.63 | 1979.74 | 1207.79 | FULL
G10 | 2053.67 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -4.95 | -96.24 | -137.94 | 6651.21 | 2044.33 | 1265.29 | FULL
G11 | 2096.11 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -4.95 | -96.04 | -137.91 | 6656.15 | 2087.51 | 1335.16 | FULL
G12 | 2851.34 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | -13.64 | -504.13 | -504.49 | 6767.5 | 2838.94 | 1752.65 | FULL
G13 | 2731.94 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.37 | 458.71 | 458.76 | 6691.59 | 2721.31 | 1744.12 | FULL
G14 | 1960.61 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.37 | 457.53 | 457.46 | 6657.22 | 1954.55 | 1403.82 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 882.9 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 474.8 | 474.33 | 6318.94 | 883.1 | 386.04 | FULL
G1 | 927.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 474.45 | 474.04 | 6249.25 | 927.02 | 430.37 | FULL
G2 | 991.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 475.69 | 475.22 | 6261.86 | 989.4 | 496.21 | FULL
G3 | 1301.33 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 479.36 | 479.55 | 6318.49 | 1298.71 | 638.64 | FULL
G4 | 1360.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 479.97 | 480.28 | 6250.77 | 1358.1 | 702.68 | FULL
G5 | 1407.79 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 479.62 | 480.03 | 6264.63 | 1403.92 | 751.4 | FULL
G6 | 2137.22 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 482.47 | 482.19 | 6345.31 | 2130.01 | 1146.45 | FULL
G7 | 2176.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 481.58 | 481.74 | 6279.87 | 2170.22 | 1194.56 | FULL
G8 | 2233.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 481.16 | 481.22 | 6296.73 | 2225.22 | 1249.73 | FULL
G9 | 2166.64 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -4.95 | -97.52 | -132.38 | 6392.5 | 2157.02 | 1336.23 | FULL
G10 | 2216.4 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -7.49 | -182.17 | -127 | 6329.03 | 2206.33 | 1388.56 | FULL
G11 | 2927.19 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.37 | 460.09 | 460.11 | 6368.87 | 2913.14 | 1756.95 | FULL
G12 | 2673.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | -13.64 | -494.18 | -494.37 | 6426.88 | 2662.78 | 1701.13 | FULL
G13 | 2788.49 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: A1428 Mon 230kV Bus & Mon-Snoh-HRanch 230kV | -13.64 | -493.31 | -493.36 | 6371.62 | 2776.35 | 1782.55 | FULL
G14 | 2152.91 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | 3.37 | 454.48 | 459 | 6341.93 | 2147.05 | 1524.77 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 735.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 441.53 | 441.07 | 6035.22 | 735.51 | 323.17 | FULL
G1 | 765.05 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 440.3 | 440.21 | 5965.62 | 764.42 | 360.77 | FULL
G2 | 838.32 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 441.7 | 441.37 | 5978.13 | 837.34 | 433.83 | FULL
G3 | 1154.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 445.23 | 445.63 | 6033.73 | 1153.35 | 578.89 | FULL
G4 | 1197.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 444.68 | 444.6 | 5965.55 | 1196.89 | 631.41 | FULL
G5 | 1244.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 444.54 | 444.8 | 5979.42 | 1243.38 | 684.34 | FULL
G6 | 1985.86 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 447.3 | 447.17 | 6057.08 | 1979.71 | 1082.83 | FULL
G7 | 2040.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 448.57 | 448.49 | 5991.62 | 2035.33 | 1140.52 | FULL
G8 | 2083.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 447.06 | 446.95 | 6008.47 | 2077.27 | 1190.35 | FULL
G9 | 2209.02 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -4.95 | -96.21 | -126.81 | 6110.1 | 2198.94 | 1370.52 | FULL
G10 | 2252.77 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -7.49 | -180.8 | -120.77 | 6046.7 | 2242.74 | 1420.18 | FULL
G11 | 2298.04 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -7.49 | -180.89 | -120.78 | 6060.34 | 2289.49 | 1475.78 | FULL
G12 | 2566.75 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-1: Murray - Sedro NT 230kV | -24.93 | -772.38 | -772.87 | 6138.31 | 2557.86 | 1657.32 | FULL
G13 | 2613.7 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-1: Murray - Sedro NT 230kV | -24.93 | -774.31 | -773.93 | 6078.12 | 2603.46 | 1705.96 | FULL
G14 | 2437.22 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 3.37 | 459.64 | 459.78 | 6079.76 | 2429.78 | 1668.87 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1347.4 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 444.32 | 444.77 | 4957.15 | 1345.82 | 723.34 | FULL
G1 | 1404.05 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 444.81 | 444.92 | 4891.71 | 1400.22 | 780.5 | FULL
G2 | 1462.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 445.68 | 445.89 | 4907.97 | 1459.24 | 842.84 | FULL
G3 | 1748.79 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 447.05 | 447.12 | 4968.2 | 1744.62 | 971.81 | FULL
G4 | 1802.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 447.25 | 447.32 | 4903.62 | 1797.58 | 1027.97 | FULL
G5 | 1848.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 447.08 | 447.54 | 4921.13 | 1843.11 | 1079.48 | FULL
G6 | 2520.17 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 445.27 | 445.18 | 5013.42 | 2511.16 | 1423.26 | FULL
G7 | 2564.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 444.78 | 444.63 | 4951.67 | 2555.38 | 1474.33 | FULL
G8 | 2611.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 444.23 | 444.31 | 4971.45 | 2601.13 | 1534.06 | FULL
G9 | 2709.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4684 Mon-Cust #2 500kV & Mon Caps | -38.68 | -475.75 | -474.94 | 5063.19 | 2697.99 | 1685.76 | FULL
G10 | 2719.42 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4684 Mon-Cust #2 500kV & Mon Caps | -38.68 | -475.71 | -474.92 | 4999.55 | 2708.09 | 1721.56 | FULL
G11 | 2608.16 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.87 | -190.71 | -190.7 | 5009.58 | 2597.33 | 1700.34 | FULL
G12 | 2112.84 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-1: Murray - Sedro NT 230kV | -24.94 | -733.86 | -734.13 | 5048.5 | 2105.3 | 1543.73 | FULL
G13 | 2160.69 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-1: Murray - Sedro NT 230kV | -24.94 | -733.25 | -733.75 | 4987.37 | 2153.07 | 1596.21 | FULL
G14 | 2146.58 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.87 | -194.55 | -194.54 | 5005.55 | 2138.69 | 1625.54 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1472.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 445.57 | 445.89 | 4626.52 | 1470.2 | 819.36 | FULL
G1 | 1522.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 446.08 | 445.96 | 4560.92 | 1519.24 | 869.65 | FULL
G2 | 1583 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 446.59 | 446.66 | 4578.84 | 1579.28 | 919.66 | FULL
G3 | 1861.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 447.51 | 447.89 | 4639.15 | 1857.27 | 1044.7 | FULL
G4 | 1913.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 447.79 | 448.11 | 4575.54 | 1906.38 | 1098.8 | FULL
G5 | 1960.35 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 448.26 | 447.82 | 4594.69 | 1955.28 | 1152.14 | FULL
G6 | 2616.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 443.79 | 444.05 | 4688.18 | 2606.7 | 1505.86 | FULL
G7 | 2654.1 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 15.9 | 443.1 | 443.19 | 4626.95 | 2643.51 | 1551.79 | FULL
G8 | 2356.16 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.87 | -172.93 | -172.87 | 4627.49 | 2348.68 | 1444.43 | FULL
G9 | 2623.21 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-1: Murray - Sedro NT 230kV | -24.94 | -692.31 | -692.95 | 4725.18 | 2612.89 | 1675.31 | FULL
G10 | 2394.1 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.87 | -173.54 | -173.56 | 4645.98 | 2386 | 1605.54 | FULL
G11 | 1810.47 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.87 | -175.96 | -175.95 | 4628.98 | 1803.74 | 1360.04 | FULL
G12 | 1947.42 | Branch HRNCHTAP (42321) TO SEDRO (42100) CKT 1 [230.00 - 230.00 kV] | N-1: Murray - Sedro NT 230kV | -24.94 | -700.22 | -700.32 | 4708.17 | 1941.29 | 1513.17 | FULL
G13 | 1849.66 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.87 | -173.59 | -173.58 | 4640.51 | 1845.42 | 1474.28 | FULL
G14 | 1285.83 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.87 | -172.96 | -172.95 | 4627.47 | 1283.38 | 1238.66 | FULL
027WINTER09v2NSH