## 25F nomo
Monroe-Snohomish-Horse Ranch Tap #1 230kV Line***Includes Horse Ranch Tap sect. of Sedro-Bothell-Horse Ranch 230kV Line(N>S GENERATION DROP ARMED AT 400MW) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 030
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6641.2293
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -191.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 82.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | -47.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1157.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 82.64 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3002.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 140 | 869.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2845.94 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1012.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2670.56 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1157.97 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | -47.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2060.35 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1012.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2896.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2896.46 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 775 | 3002.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2831.28 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2621.51 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2641.63 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2831.28 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -191.33 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2845.94 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 869.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2557.17 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2060.35 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2641.63 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2621.51 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2670.56 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2557.17 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Monroe-Snohomish-Horse Ranch Tap #1 230kV Line***Includes Horse Ranch Tap sect. of Sedro-Bothell-Horse Ranch 230kV Line(N>S GENERATION DROP ARMED AT 400MW) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 030
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6310.402
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 189.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 471.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 338.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1472.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 471.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 3057.3 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 1202.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2710.77 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1353.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2617.35 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1472.16 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 338.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2853.01 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1353.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2983.62 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2983.62 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 3057.3 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2716.87 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2645.46 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2495.81 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2716.87 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 189.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2710.77 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 1202.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2524.99 | BFR: Bothell 230kV Bus Sect #7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2853.01 | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2495.81 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2645.46 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2617.35 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2524.99 | BFR: Bothell 230kV Bus Sect #7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Monroe-Snohomish-Horse Ranch Tap #1 230kV Line***Includes Horse Ranch Tap sect. of Sedro-Bothell-Horse Ranch 230kV Line(N>S GENERATION DROP ARMED AT 400MW) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 030
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6024.7113
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -14.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 263.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 130.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1245.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 263.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2914.14 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 949.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2665.86 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 1103.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2574.82 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 1245.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 130.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2717.15 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1103.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2811.1 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2811.1 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2914.14 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2564.89 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2474.23 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2438.24 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2564.89 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -14.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2665.86 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 949.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2391.47 | BFR: Bothell 230kV Bus Sect #7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2717.15 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2438.24 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2474.23 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2574.82 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2391.47 | BFR: Bothell 230kV Bus Sect #7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Monroe-Snohomish-Horse Ranch Tap #1 230kV Line***Includes Horse Ranch Tap sect. of Sedro-Bothell-Horse Ranch 230kV Line(N>S GENERATION DROP ARMED AT 400MW) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 030
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4954.746
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1421.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1716.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1575.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2578.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1716.17 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2701.19 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2304.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2453.75 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
260 | 460 | 2443.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 2348.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 775 | 2578.41 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1575.72 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2557.7 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2443.48 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2621.96 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2621.96 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2701.19 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2286.05 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2295.05 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2191.7 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2286.05 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1421.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2453.75 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2304.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2101.4 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2557.7 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2191.7 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2295.05 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 2348.79 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 2101.4 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Monroe-Snohomish-Horse Ranch Tap #1 230kV Line***Includes Horse Ranch Tap sect. of Sedro-Bothell-Horse Ranch 230kV Line(N>S GENERATION DROP ARMED AT 400MW) (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 030
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4621.0173
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1705.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2003.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1865.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2733.12 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
100 | 775 | 2003.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2542.95 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
260 | 140 | 2561.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2193.38 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2625.39 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1599.27 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2733.12 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1865.39 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2418.63 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2625.39 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2459.04 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2459.04 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 2542.95 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2261.58 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 140 | 2167.33 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2149.11 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1000 | 460 | 2261.58 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 1705.52 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2193.38 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2561.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2008.21 | BFR: Bothell 230kV Bus Sect #7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2418.63 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2149.11 | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2167.33 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1599.27 | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2008.21 | BFR: Bothell 230kV Bus Sect #7 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Monroe-Snohomish-Horse Ranch Tap #1 230kV Line***Includes Horse Ranch Tap sect. of Sedro-Bothell-Horse Ranch 230kV Line(N>S GENERATION DROP ARMED AT 400MW) (COV-CRES BYP @ COV)
G0 | -191.33 | 189.25 | -14.29 | 1421.43 | 1705.52
G1 | -47.11 | 338.13 | 130.07 | 1575.72 | 1865.39 | Season/Year: | WINTER 2009
G2 | 82.64 | 471.74 | 263.36 | 1716.17 | 2003.47 | Direction: | North-to-South (NS)
G3 | 869.75 | 1202.81 | 949.6 | 2304.99 | 2561.07 | Case Loads: | Heavy Loads
G4 | 1012.04 | 1353.91 | 1103.85 | 2443.48 | 2625.39 | Outage: | 030
G5 | 1157.97 | 1472.16 | 1245.21 | 2578.41 | 2733.12 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2060.35 | 2853.01 | 2717.15 | 2557.7 | 2418.63 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2896.46 | 2983.62 | 2811.1 | 2621.96 | 2459.04 | Study Person: | JGO7470
G8 | 3002.69 | 3057.3 | 2914.14 | 2701.19 | 2542.95 | Source: | 030WINTER09v2NSH(NS GD @ 400MW)
G9 | 2621.51 | 2645.46 | 2474.23 | 2295.05 | 2167.33
G10 | 2831.28 | 2716.87 | 2564.89 | 2286.05 | 2261.58
G11 | 2845.94 | 2710.77 | 2665.86 | 2453.75 | 2193.38
G12 | 2557.17 | 2524.99 | 2391.47 | 2101.4 | 2008.21
G13 | 2641.63 | 2495.81 | 2438.24 | 2191.7 | 2149.11
G14 | 2670.56 | 2617.35 | 2574.82 | 2348.79 | 1599.27
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 030 | Monroe-Snohomish-Horse Ranch Tap #1 230kV Line***Includes Horse Ranch Tap sect. of Sedro-Bothell-Horse Ranch 230kV Line(N>S GENERATION DROP ARMED AT 400MW) (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6641.2293 | -191.33 | -47.11 | 82.64 | 869.75 | 1012.04 | 1157.97 | 2060.35 | 2896.46 | 3002.69 | 2621.51 | 2831.28 | 2845.94 | 2557.17 | 2641.63 | 2670.56
35F | 6310.402 | 189.25 | 338.13 | 471.74 | 1202.81 | 1353.91 | 1472.16 | 2853.01 | 2983.62 | 3057.3 | 2645.46 | 2716.87 | 2710.77 | 2524.99 | 2495.81 | 2617.35
45F | 6024.7113 | -14.29 | 130.07 | 263.36 | 949.6 | 1103.85 | 1245.21 | 2717.15 | 2811.1 | 2914.14 | 2474.23 | 2564.89 | 2665.86 | 2391.47 | 2438.24 | 2574.82
60F | 4954.746 | 1421.43 | 1575.72 | 1716.17 | 2304.99 | 2443.48 | 2578.41 | 2557.7 | 2621.96 | 2701.19 | 2295.05 | 2286.05 | 2453.75 | 2101.4 | 2191.7 | 2348.79
70F | 4621.0173 | 1705.52 | 1865.39 | 2003.47 | 2561.07 | 2625.39 | 2733.12 | 2418.63 | 2459.04 | 2542.95 | 2167.33 | 2261.58 | 2193.38 | 2008.21 | 2149.11 | 1599.27

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -192.08 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 470.56 | 470.51 | 6658.13 | -191.33 | -91.77 | FULL
G1 | -47.93 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 471.25 | 471.18 | 6587.8 | -47.11 | -8.29 | FULL
G2 | 81.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 471.08 | 470.87 | 6597.53 | 82.64 | 70.28 | FULL
G3 | 871.35 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 483.13 | 483.09 | 6649.11 | 869.75 | 588.2 | FULL
G4 | 1012.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 483.52 | 483.52 | 6580.08 | 1012.04 | 674.12 | FULL
G5 | 1160.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 484.31 | 484.05 | 6591.94 | 1157.97 | 762.42 | FULL
G6 | 2067.08 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.71 | 798.05 | 797.95 | 6672.2 | 2060.35 | 1386.43 | FULL
G7 | 2908.66 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 492 | 491.82 | 6619 | 2896.46 | 1882.57 | FULL
G8 | 3016.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 491.9 | 491.87 | 6636.37 | 3002.69 | 1933.67 | FULL
G9 | 2632.2 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 18.56 | 670.28 | 670.07 | 6700.3 | 2621.51 | 1906.54 | FULL
G10 | 2843.39 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.64 | 680.82 | 680.75 | 6638.34 | 2831.28 | 2021.39 | FULL
G11 | 2858.85 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 675.65 | 675.48 | 6655.99 | 2845.94 | 2030.25 | FULL
G12 | 2566.78 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 18.56 | 674.78 | 674.64 | 6713.86 | 2557.17 | 2010.55 | FULL
G13 | 2653.01 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 681.75 | 681.52 | 6650.43 | 2641.63 | 2057.86 | FULL
G14 | 2682.58 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 675.3 | 674.78 | 6667.36 | 2670.56 | 2069.9 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 188.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 466.82 | 466.62 | 6322.9 | 189.25 | 148.65 | FULL
G1 | 335.98 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 466.67 | 466.43 | 6250.97 | 338.13 | 239.99 | FULL
G2 | 471.05 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 466.47 | 466.57 | 6262.06 | 471.74 | 322.19 | FULL
G3 | 1205.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 476.8 | 476.67 | 6317.43 | 1202.81 | 803.63 | FULL
G4 | 1357.6 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 477.16 | 477.29 | 6249.49 | 1353.91 | 894.35 | FULL
G5 | 1474.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 476.35 | 476.44 | 6263.46 | 1472.16 | 965.99 | FULL
G6 | 2866.64 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 18.56 | 643.65 | 644.08 | 6356.47 | 2853.01 | 1863.95 | FULL
G7 | 2997.68 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 649.31 | 649.37 | 6293.24 | 2983.62 | 1942.5 | FULL
G8 | 3071.9 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 653.32 | 652.84 | 6310.86 | 3057.3 | 1986.71 | FULL
G9 | 2654.9 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 646.15 | 645.91 | 6368.86 | 2645.46 | 1938.89 | FULL
G10 | 2728.87 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 648.84 | 648.65 | 6304.98 | 2716.87 | 1976.38 | FULL
G11 | 2723.09 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5114 Rav-Echo Lk #1 & Mon-EchoLK-SnoK #1 500kV | 18.56 | 644.77 | 644.29 | 6321.87 | 2710.77 | 1974.92 | FULL
G12 | 2534.32 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -12.34 | -512.37 | -512.46 | 6380.39 | 2524.99 | 2003.62 | FULL
G13 | 2506.02 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 644.23 | 643.88 | 6316.29 | 2495.81 | 1994.84 | FULL
G14 | 2627.54 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.64 | 645.68 | 645.5 | 6336.76 | 2617.35 | 2055.03 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -15.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 433.63 | 433.49 | 6039.69 | -14.29 | 35.19 | FULL
G1 | 128.83 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 433.86 | 433.73 | 5968.07 | 130.07 | 123.51 | FULL
G2 | 262.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 433.9 | 433.75 | 5978.98 | 263.36 | 205.62 | FULL
G3 | 949.81 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 440.7 | 440.92 | 6032.25 | 949.6 | 661.93 | FULL
G4 | 1102.8 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 441.31 | 441.46 | 5964 | 1103.85 | 754.77 | FULL
G5 | 1246.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 441.88 | 441.96 | 5978.35 | 1245.21 | 840.01 | FULL
G6 | 2728.73 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 608.55 | 608.2 | 6068.87 | 2717.15 | 1791.66 | FULL
G7 | 2824.04 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 610.39 | 610.24 | 6004.99 | 2811.1 | 1846.41 | FULL
G8 | 2925.73 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 617.29 | 617.2 | 6023.23 | 2914.14 | 1908.7 | FULL
G9 | 2484.28 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 611.35 | 611.18 | 6080.44 | 2474.23 | 1843.05 | FULL
G10 | 2574.68 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 607.69 | 607.47 | 6018.06 | 2564.89 | 1896.62 | FULL
G11 | 2677.11 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 613.2 | 612.95 | 6036.03 | 2665.86 | 1956.74 | FULL
G12 | 2401.35 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -12.34 | -498.88 | -498.91 | 6094.36 | 2391.47 | 1926.4 | FULL
G13 | 2449.32 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.64 | 609.15 | 609.07 | 6031.62 | 2438.24 | 1954.09 | FULL
G14 | 2584.85 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.64 | 612.63 | 612.62 | 6051.73 | 2574.82 | 2040.08 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1425.61 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 441.97 | 442.02 | 4957 | 1421.43 | 942.26 | FULL
G1 | 1579.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 442.71 | 442.96 | 4891.94 | 1575.72 | 1034.15 | FULL
G2 | 1721.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 443.12 | 443.35 | 4909.69 | 1716.17 | 1117.88 | FULL
G3 | 2313.23 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 446.26 | 446.34 | 4974.99 | 2304.99 | 1507.9 | FULL
G4 | 2454 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 446.68 | 446.79 | 4912.51 | 2443.48 | 1588.79 | FULL
G5 | 2587.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 447.13 | 447.21 | 4933.35 | 2578.41 | 1663.47 | FULL
G6 | 2567.32 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 552.01 | 551.91 | 4991.95 | 2557.7 | 1755.72 | FULL
G7 | 2632.24 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 551.27 | 551.31 | 4928.93 | 2621.96 | 1799.69 | FULL
G8 | 2712.35 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 551.02 | 550.94 | 4948.76 | 2701.19 | 1846.69 | FULL
G9 | 2303.53 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 549.28 | 549.22 | 5005.72 | 2295.05 | 1797.07 | FULL
G10 | 2294.77 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 546.85 | 546.36 | 4942.25 | 2286.05 | 1800.62 | FULL
G11 | 2463.26 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 550.25 | 550.04 | 4963.97 | 2453.75 | 1895.68 | FULL
G12 | 2110.11 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 547.4 | 547.19 | 5019.04 | 2101.4 | 1820.87 | FULL
G13 | 2199.93 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 548.12 | 547.67 | 4959.25 | 2191.7 | 1880.71 | FULL
G14 | 2357.69 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 553.45 | 553.34 | 4981.84 | 2348.79 | 1971.45 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1710.06 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 443.39 | 443.5 | 4626.9 | 1705.52 | 1120.71 | FULL
G1 | 1869.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 444.27 | 444.41 | 4564.1 | 1865.39 | 1215.71 | FULL
G2 | 2010.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 444.81 | 444.58 | 4583.01 | 2003.47 | 1297.94 | FULL
G3 | 2570.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.71 | 446.92 | 447.02 | 4649.52 | 2561.07 | 1667.61 | FULL
G4 | 2636.21 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 509.96 | 509.75 | 4587.23 | 2625.39 | 1707.01 | FULL
G5 | 2744.67 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 509.15 | 509.03 | 4608.73 | 2733.12 | 1764.35 | FULL
G6 | 2427.36 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 511.26 | 511.13 | 4655.27 | 2418.63 | 1694.53 | FULL
G7 | 2469.01 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 509.49 | 509.25 | 4591.94 | 2459.04 | 1721.03 | FULL
G8 | 2552.73 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 512.68 | 512.4 | 4612.66 | 2542.95 | 1770.86 | FULL
G9 | 2175.25 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 18.63 | 509.83 | 509.47 | 4669.35 | 2167.33 | 1742.15 | FULL
G10 | 2269.79 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 511.28 | 510.88 | 4608.22 | 2261.58 | 1797.6 | FULL
G11 | 2201.04 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.46 | -172.88 | -172.83 | 4624.63 | 2193.38 | 1756.15 | FULL
G12 | 2015.03 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -12.34 | -463.94 | -463.93 | 4684.09 | 2008.21 | 1786.62 | FULL
G13 | 2156.76 | Branch NOVELTY (42304) TO SAMMAMSH (42300) CKT 1 [230.00 - 230.00 kV] | BFR: 5111 Monroe-EchoLK-SnoKing #1 500kV & Echo Lk Caps | 18.63 | 510.93 | 510.62 | 4625.84 | 2149.11 | 1863.26 | FULL
G14 | 1603.33 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | BFR: Maple Valley 230kV Bus Section #3 & Klahanie | -2.46 | -173.22 | -173.21 | 4623.77 | 1599.27 | 1559.08 | FULL
030WINTER09v2NSH(NS GD @ 400MW)