Notice of Availability of the Final Supplemental Environmental Impact Statement for the Interim Operation of the International Boundary and Water Commission International Wastewater Treatment Plant

The Draft Supplemental Environmental Impact Statement (SEIS) for Interim Operation of the International Wastewater Treatment Plant (IWTP) was prepared by the U.S. Environmental Protection Agency (EPA) and the International Boundary and Water Commission, U.S. Section (USIBWC).  Its( availability for review was noticed in the Federal Register on September 6, 1996.  Written comments were received through October 21, 1996.  A public hearing to receive comments to the Draft SEIS was held at Southwest High School in Imperial Beach, California on October 7, 1996.

EPA and USIBWC have reviewed and considered the oral and written comments submitted for the Draft SEIS.  EPA and USIBWC have concluded, based upon this review, that no additional alternatives need to be considered with respect to the proposed project and that no substantive new analysis or major revisions to the Draft SEIS are necessary.  The Final SEIS consists of copies of the letters of comment received, with responses; a transcript of the public hearing; an errata sheet and attachments to the Draft SEIS.

The Final SEIS will be available for public review and comment from December 6, 1996 to January 4, 1997.  Copies of the Final SEIS are available at San Diego main library and the Chula Vista, Imperial Beach, Otay Mesa and San Ysidro branch libraries.  Comments on the Final SEIS or requests for additional copies of the Final SEIS, Draft SEIS, or attachments may be addressed to:

Ms. Elizabeth Borowiec,

EPA Region IX, WTR-4,

75 Hawthorne Street,

San Francisco, CA 94105,

(415) 744-1165; or

Mr. Charles Fischer, USIBWC,

San Ysidro Office,

2225 Dairy Mart Road,

San Ysidro, CA (619) 662-7600.

The EPA and USIBWC will prepare a Record of Decision for the Interim Operation of the IWTP following the close of the public review period for the Final SEIS.

TABLE OF CONTENTS

1.1	Introduction	1

1.2	Comments Received and Responses	3

1.3	Public Hearing	161

1.4	Errata	224

1.5	Attachments	225

Introduction

The Draft Supplemental Environmental Impact Statement (SEIS) for Interim Operation of the International Wastewater Treatment Plant (IWTP) was prepared by the U.S. Environmental Protection Agency (EPA) and the International Boundary and Water Commission, U.S. Section (USIBWC).  Its availability for review was noticed in the Federal Register and the San Diego Union Tribune on September 6, 1996.  Written comments were received through October 21, 1996.  A public hearing to receive comments to the Draft SEIS was held at Southwest High School in Imperial Beach, California, on October 7, 1996.

EPA and USIBWC have reviewed and considered the oral and written comments submitted for the Draft SEIS.  EPA and USIBWC have concluded, based upon this review, that no additional alternatives need to be considered with respect to the proposed project and that no substantive new analysis or major revisions to the Draft SEIS are necessary.

Comments were received from the Surfrider Foundation that questioned the methodologies used in preparing the modeling and analysis of the effects of discharge of untreated sewage or treated effluent to the ocean shoreline in Mexico and through the South Bay Ocean Outfall, which was prepared by Parsons Engineering Science as a technical study for the SEIS.  The technical study was a key analytic component of the SEIS and was made available under separate cover to interested parties during the review period.  The Surfrider comments suggest that the modeling could not have been conducted as presented, based upon deficiencies in the base data and analytic models used, that the study was a (technical fraud,( and that previous current studies had indicated that there were no northerly trending currents along the shoreline south of the international border.

EPA, USIBWC, the State Water Quality Control Board, and the City of San Diego had reviewed the methodologies used by Parsons Engineering Science prior to release of the Draft SEIS.  The technical study was also independently reviewed for the National Marine Fisheries Service during the public review period.  EPA also contacted the author of one of the analytic models used in the study whose use was questioned by Surfriders for clarification.

After consideration of the challenges made to the adequacy of the Parsons Engineering Science study by the Surfrider Foundation, EPA and USIBWC have found that their comments were based upon misunderstanding of the data and methodologies used in the study and that the Parsons Engineering Science study is technically sound and appropriate in scope to evaluate the effects of the alternatives considered in the SEIS.  Specific responses to the alleged deficiencies are provided in the responses to comments from the Surfrider Foundation.

The Final SEIS consists of copies of the letters of comment received, with responses.  A transcript of the public hearing comments is provided. An errata sheet listing changes that should be made to the Draft SEIS for the Final SEIS is also provided.  Finally, several attachments providing clarification to issues raised in the letters of comment are provided.

The Final SEIS will be available for public review and comment from December 6, 1996 to January 6, 1997.  Comments on the Final SEIS or requests for additional copies of the Final SEIS, Draft SEIS, or attachments may be addressed to:

Ms. Elizabeth Borowiec, EPA Region IX, Water Management Division, 75 Hawthorne Street, San Francisco, CA 94105, (415) 744-1165; or to Mr. Charles Fisher, USIBWC, San Ysidro Office, 2225 Dairy Mart Road, San Ysidro, CA (619) 662-7600.

The EPA and USIBWC will prepare a Record of Decision for the Interim Operation of the IWTP following the close of the public review period for the Final SEIS.

Comments Received and Responses

Comments to the Draft SEIS were received from the following agencies, organizations, and individuals:

United States Department of Commerce, National Oceanic and Atmospheric Administration, National Marine Fisheries Service (NMFS)

United States Department of the Interior, Fish and Wildlife Service (USFWS)

United States Department of Health and Human Services, National Center for Environmental Health

Tijuana River National Estuarine Research Reserve, California Department of Parks and Recreation (CDPR)

County of San Diego Department of Environmental Health (DEH)

City of Imperial Beach, California

City of Coronado

City of San Diego Metropolitan Wastewater Department (MWWD)

Tia Juana Valley County Water District

Otay Water District

San Diego Audubon Society

Citizens Against Recreational Eviction (CARE)

Citizens Revolting Against Pollution

Environmental Health Coalition

Lev D. Rozman, Ph.D.

San Diego-Tijuana Sister Cities Society

Save Our Bay, Inc.

San Diego Chapter of the Sierra Club

Christopher Teng

Surfrider Foundation

The letters of comment are provided with numbers corresponding to comments responded to.  The responses follow each letter.

United States Department of Commerce, National Oceanic and Atmospheric Administration, National Marine Fisheries Service (NMFS)

Comment acknowledged.  USIBWC/EPA will continue to work with Mexico with respect to impacts to the marine environment from discharges to the marine environment.

The commentor is correct.  The SEIS evaluated each alternative as a stand alone solution for comparative purposes.  The preferred alternative would install detention basins to avoid discharges of treated effluent to the river, which would otherwise occur if Alternative 2 were carried through to the year 2001.

The intent of the document was to use (may( when there was some uncertainty about future conditions.  It was not intended to mislead the reader.

NMFS concurs with the conclusion of the SEIS and supports the discharge through the SBOO over other alternatives.

The statement in the SEIS is intended to advise readers that if conditions change, such as a more rapid increase in flows from Mexico being received prior to the completion of the ocean outfall, discharges to the Tijuana River could result.  These discharges would be unavoidable, as no other discharge option would be available.  USIBWC/EPA(s best estimate is that this circumstance would not occur.

The commentor is correct; the Draft SEIS is in error.  There is the potential for 0.7 mgd of flows during the wet weather season in the year 2000, as shown in Table 3 of Appendix A.

USIBWC/EPA is currently having a headworks analysis completed which will identify the maximum concentrations of constituent pollutants in sewage influent that could be treated and discharged to ocean plan standards through the SBOO.  This information will be given to Mexico to help to focus the industrial discharge source reduction program to address constituents of immediate concern, including PAHs.

It is anticipated that a detailed monitoring program will be required by the NPDES permit issued by the RWQCB; the permit will be available prior to issuance of the ROD for the project.

United States Department of the Interior, Fish and Wildlife Service (USFWS)

The USFWS supports the SEIS preferred Alternative 6, phased alternative.

The use of the South Bay Land Outfall has been considered by USIBWC but has not been evaluated as preferable to construction of the temporary earthen detention basins for various technical reasons.  These include requirements for additional conveyance lines to discharge stored effluent to the emergency connection, need for an additional temporary pumping station, concerns regarding safety of the workers constructing the SBOO tunnel adjacent to the SBLO if it is used for effluent storage and a failure of the pipe or seal occurs and sediment buildup in the SBLO from detention and settling of solids in the effluent.

Continued use of the emergency connection after the SBOO is completed would reduce impacts from discharges in Mexico.  However, the emergency connection may not be available on a long-term basis due to constraints in system capacities in the south San Diego sewers.

Although the preferred alternative is not anticipated to result in discharges of treated effluent to the Tijuana River, the RWQCB will set monitoring requirements for any discharges of treated effluent to the Tijuana River, which will include sediments.  If such discharges are to occur on a regular basis, EPA and USIBWC will consult with the USFWS, the Tijuana River National Estuarine Research Reserve, and California Department of Fish and Game with respect to monitoring of the effects of the discharge on plants and wildlife.

The USIBWC will consult with the County Department of Environmental Health and the USFWS regarding appropriate vector controls if the discharge of treated effluent results in ponding of waters in the river valley.

USIBWC is actively pursuing an industrial pretreatment and source reduction program with Mexico.

The EPA and USIBWC are preparing a second Supplemental EIS to consider alternatives to activated sludge.  The secondary treatment processes will be evaluated with respect to effectiveness at reducing these and other constituents of concern.  Reduction through industrial pretreatment and source control is also being pursued currently.

USIBWC and EPA are willing to provide technical guidance to Mexico in their design of a new pumping and conveyance system in Mexico; however, the development of this facility will be under the jurisdiction of Mexico.

United States Department of Health and Human Services, National Center for Environmental Health

The National Center for Environmental Health supports the ultimate construction of the South Bay Ocean Outfall and recognizes that the proposed interim phased approach (Alternative 6) is the most logical approach.

Tijuana River National Estuarine Research Reserve, California Department of Parks and Recreation (CDPR)

CDPR opposes any alternative that discharges freshwater effluents into the Tijuana River.  It is the intent of the preferred alternative to avoid such discharges.

CDPR opposes the chlorination of effluents and requests that the limits of total residual chlorine be given for river water.  Disinfection of any effluent discharged to the river is not proposed.  A probable standard of no trace residual chlorine in any effluent discharged to the river would be imposed by the RWQCB in its compliance order.

CDPR is concerned that exotic plant invasion (primarily Arundo donax) in the riparian channel should be addressed in the draft. The major source for exotic plant invasion is wet weather storm flows which the proposed action will not change.  Dry weather flows probably do not carry significant quantities of exotic plants in the river, though if established they may be maintained by year-round flows in the river.  The proposed action would reduce any effects of dry weather flows on invasive species in the river.

CDPR feels that impacts to the benthic communities and fish are underestimated in Section 2.2.2.4 and that the potential trapping of flows by tides are not addressed in Section 4.4.2.  The SEIS considers the potential impacts to the river, estuary, and nearshore coastal areas from dry weather discharges of treated effluent or untreated sewage as significant impacts.  The specific topics are addressed in Appendix B of the SEIS.

Comment acknowledged.  CDPR points out that the succession of events outlined in Section 2.2.1.4 is tenuous at best. They believe polluted flows decrease insect diversity and excess nutrients favor monocultures dominated by weedy species.

CDPR feels that Section 4.5.1.1 of the SEIS inadequately describes impacts to the plankton community.  They are concerned about excess nutrients in the outfall causing plankton blooms.  Eutrophication due to excess nutrients is identified as a significant impact of discharge to the river and estuary in the SEIS Sections 4.4.3 and 4.4.4).  Effects to plankton communities from SBOO discharge was considered in the SEIS under Marine Biology (Section 4.5.5.1) and in the ocean discharge modeling.  Adverse impacts are not anticipated.

County of San Diego Department of Environmental Health (DEH)

In the event that discharges must be made to the Tijuana River, Department of Environmental Health recommends that raw sewage should be treated before discharge.

Once the SBOO is on line, the DEH recommends that the peak flow capacity of IWTP (up to 75 mgd) be used with ocean discharge rather than allowing any discharges of raw sewage to the river.

DEH supports and encourages construction and use of the return to sender pump station and conveyance system. The City advocates the construction and operation of a new Mexican conveyance system.  EPA and USIBWC are providing funding and technical assistance to Commission Estatl de Servicios Publicos de Tijuana (CESPT), who will sponsor construction of the system through Border Environment Cooperation Commission (BECC).

The SEIS includes a requirement to submit a vector control plan to DEH prior to implementation of any of the alternatives.

Discharges to the river would occur if the capacity of the emergency connection is exceeded.  The required detention to equalize flows for maximum use of the emergency connection is approximately 5.5 million gallons.  While the SBLO has a greater storage capacity, there would be no way to discharge the excess effluent other than to the river.  Use of the SBLO would entail additional risks to workers constructing the SBOO if a failure were to occur, would require the design and construction of additional pumping and conveyance to discharge from SBLO to the emergency connection and may result in a build up of sediments from the effluent in the SBLO.  For these reasons, detention basins in the IWTP site is preferred.

Disinfection is not considered feasible for interim discharges because dechlorination to achieve removal of residual chlorine in the effluent is not feasible.  Other methods of disinfection would have to be designed and constructed but would only be needed for the period prior to discharge through the SBOO.  The SBOO discharge is not anticipated to require disinfection.

Page 37, 1.1.4.4.  The average daily flow of 174 mgd is increased to a peak of 333 mgd using a 1.9:1 peaking factor.  The siphon of the outfall cannot be cleaned, as such, but has been designed to minimize the accumulation of sediments.

The ocean and shoreline modeling studies used variable T90 rates to account for differences in temperature, light transmissivity, and salinity during a daily cycle, and assumed non-disinfected primary effluent.

All references to the San Diego County Department of Health Services should be changed in the Final SEIS to County of San Diego(s Department of Environmental Health.

City of Imperial Beach, California

The City of Imperial Beach supports the full construction of the IWTP and its operation as a secondary treatment facility as soon as possible but for the interim period it supports the phased operation of the IWTP as described in Alternative 6 of the SEIS.  The City opposes any discharges to the Tijuana River but also acknowledges that they could occur.  The City also supports the continued use of the emergency connection, construction of a parallel conveyance system in Mexico, and implementation of an industrial pretreatment program in Mexico.

USIBWC has notification procedures in existence for spills of sewage into the Tijuana River.  This notification will continue after the IWTP becomes operational.  The NPDES permit and compliance order to be issued by the RWQCB includes a monitoring program that should provide the City of Imperial Beach and other jurisdictions and agencies with updated information and timely notification of spills or discharges to the river and coastline.

City of Coronado

The City supports Alternative 6.

The City strongly advocates for the addition of secondary treatment at the IWTP.

The EPA and USIBWC agree that implementation of the IWTP and SBOO will not solve the City(s problem of dealing with wet weather seasonal beach contamination from Tijuana(s sewage.

The City advocates the construction and operation of a new Mexican conveyance system.  EPA and USIBWC are providing funding and technical assistance to CESPT, who will sponsor construction of the system through BECC.

City of San Diego Metropolitan Wastewater Department (MWWD)

Disinfection of treated effluent discharged to the river is not proposed or considered feasible, due to the lack of dechlorination facilities for the effluent if it were discharged to the river and the adverse consequences of trace residual chlorine.

MWWD supports the construction of a Mexican parallel conveyance system and industrial pretreatment program. EPA and USIBWC are providing funding and technical assistance to CESPT, who will sponsor construction of the system through BECC.

Interim operation alternatives other than discharge to SBOO assume some use of the connection to the Metropolitan Sewerage System; it should not be assumed that current capacities (13 mgd) will always be available.  MWWD and USIBWC must establish policies and procedures for its use during the period of interim operation.  EPA and USIBWC accepts MWWD(s recommendation for close coordination of flow capacity in the emergency connection.  As noted above, disinfection of effluent that may be discharged to the river is not proposed.

Changes to the City(s NPDES permit for discharges at Point Loma are not proposed by EPA or USIBWC as part of the interim operation of the IWTP.  The City has been accepting flows from Mexico since the 1960s and the flows are less than 7 percent of the total flows received.  This issue is within the oversight responsibility of the RWQCB, who permits the discharge from Point Loma.

MWWD recommends the development of operating procedures (especially washing of sides) to control odors if the earthen detention basin alternative is constructed.  The Draft SEIS proposes odor controls for the detention basins, as needed, to control nuisance odors, including covering of the basins, if required.  Washing down of the sides of the basins will be evaluated as an additional odor control practice.

USIBWC will consult with MWWD regarding operating procedures of the detention basin.  They are especially concerned that the diurnal wet weather flow may not drop off sufficiently fast to allow the combined flow from both the treatment process train and the detention basin to remain below 13 mgd and to be discharged to the emergency connection.

MWWD recommends that the NPDES permit for SBOO discharge should include an ocean monitoring program at least as stringent as that which exists for the Point Loma Wastewater Treatment Plant.  This monitoring has already been agreed to and will be included in the NPDES permit issued by the RWQCB.  Also, the USIBWC should be required to notify City of Imperial Beach officials of spills or plant overflows.

Minute No. 270 specified that Mexico construct, operate, and maintain a sanitary wastewater treatment and disposal facility for the city of Tijuana at a site known as San Antonio de los Buenos to prevent discharges of untreated sanitary and industrial wastewater across the international boundary in the San Diego-Tijuana area.  The design specified that the plant be constructed in two modules designed to treat an average discharge in the range of 17 to 25 mgd.  The first module of this facility was completed by Mexico and is in operation today.  The second module called for in Minute No. 270 was subsequently deleted by agreements of the two governments in Minute No. 283, which called for the construction of the international wastewater treatment plant, the first module capable of treating an average daily flow of 25 mgd.

Module No. 1 at San Antonio de los Buenos is operating at 17 mgd.  However, due to the fact that the IWTP and ocean outfall have not been completed, Mexico has continued to take flows to San Antonio de los Buenos that exceed the capacity of the plant.  Flows over the 17 mgd design capacity of the San Antonio de los Buenos are being discharged untreated to the surf.  This action by Mexico to continue to convey all flows up to the capacity of their conveyance system to San Antonio de los Buenos has prevented these discharges from crossing the international boundary into the United States.  This system is overloaded during the peak hours of the day.  These peak flows are presently diverted to the City of San Diego(s Point Loma Treatment Plant via the emergency connection.

It is recognized that a pretreatment program for industrial discharges to the IWTP is critical for the successful operation of the plant and the ability of the plant to produce an effluent that will meet the California Ocean Plan Standards.  The IBWC and EPA are actually working with the Mexican government to develop and institute such a program.  This program plans to utilize the services attended by the City of San Diego in the utilization of laboratory services, training protocols, and other appropriate technical services.

The federal agencies recognize that it is in the best interest of the local community to periodically report on the status of the program to the cognizant agencies in the San Diego region.  Future agreements between the two governments that could impact the operation of facilities identified in Minute Nos. 270 and 283 will receive proper review in the context of complying with the requirements of the minutes.

Tia Juana Valley County Water District

The District strongly supports Alternative 6 of the SEIS and encourages the quick completion and operation of the SBOO, the IWTP with detention basin and connection to the City of San Diego Point Loma Treatment Plant, and the completion of a new conveyance system in Mexico.

The District considers the parallel pumping and conveyance facilities in Mexico the most critical portion of the proposed project and should be started as quickly as possible.  EPA and USIBWC are providing funding and technical assistance to CESPT, who will sponsor construction of the system through BECC.

The District reluctantly supports the construction of the interim detention basins and urges that the basins be covered to avoid nuisance odors.

The District strongly recommends that the United States and Mexico develop and implement an effective sewage pretreatment program prior to the IWTP accepting untreated effluent.

Otay Water District

Comment in support of the project is acknowledged.

San Diego Audubon Society

The Audubon Society opposes any discharges of untreated or primary treated sewage from the IWTP into the Tijuana River.  The primary reasons for opposition is that discharge flows would encourage excessive growth of inappropriate vegetation, a change in the salinity of the estuary, and nutrient loading.  It is not the intent of the project to discharge to the river; the preferred alternative would be least likely of any of the alternatives to result in discharges during 1997 and 1998.

The Audubon Society supports use of the emergency connector, construction of the parallel conveyance, requiring industrial pretreatment of point source polluters in Mexico, and the construction of detention ponds for flow equalization.

It is the Society(s opinion that the predicted growth rate for Tijuana sewage (4.8 5 per annum) is unrealistically low and that the phased approach is too slow.  The growth rate was based upon the best available estimates at the time the flow projections were developed.  If the preferred alternative is selected, development of additional facilities will proceed as quickly as possible.

If the preferred alternative is selected and the flow estimates are correct, no discharges from the IWTP to the river or estuary would occur and mitigation would not be required.  If some discharges do result, the affected areas will be monitored, as indicated in the SEIS and according to a monitoring program included in the RWQCB(s compliance order.  The monitoring will provide data on the changes that have resulted from the discharges.  The EPA and USIBWC will then coordinate with the resource agencies as to appropriate mitigation for impacts from the discharges.

Citizens Against Recreational Eviction (CARE)

CARE supports the phased operation Alternative 6 of the SEIS and the construction of a parallel conveyance system in Mexico as a stand-alone project. EPA and USIBWC are providing funding and technical assistance to CESPT, who will sponsor construction of the system through BECC. CARE urges the implementation of an industrial source control program in Mexico and that planning for expansion of the IWTP stay ahead of potential future needs.

CARE notes that in the future, if Mexico asserts its rights to the IWTP effluent, the parallel conveyance system could be used to return the effluent to Mexico for reuse.

CARE argues for partial construction of the planned future primary sedimentation basins within the IWTP site as an alternative to excavating earthen detention basins, as described for Alternative 3 and Alternative 6.  This suggestion is made as a potential cost savings measure.  CARE notes there are additional areas within the site where the detention facilities could be sited and built to provide a greater holding capacity which could be used in future for flow equalization within the IWTP.  CARE notes, after observations of an equalization basin at an existing treatment works, several potential benefits including lack of objectionable odors, vectors and cleanliness.  USIBWC is evaluating these suggestions with respect to current and future need, and construction and operations cost savings.

Citizens Revolting Against Pollution

The comment supports the construction and operation of the IWTP.

The comment supports Alternative 3 of the SEIS, emphasizing that no effluent, treated or untreated, should be discharged to the river.

The comment recommends covering the proposed interim detention basin and that the area be returned to its original grade after its use.

Environmental Health Coalition

It is agreed that both domestic and industrial wastewaters have grown and are part of the overall problem being addressed.  IBWC Minute No. 283 addresses explicitly both domestic and industrial wastewaters.  The FEIS and SEIS included consideration of toxic constituents in its characterization of wastewater and modeling of the effects of effluent discharges.

Sewage discharges entering the U.S. have occurred during the past two years, although the chronic dry weather flows experienced in previous years have not occurred.

Comment noted, urban discharges refers more to non-point source discharges but could include persistent, bioaccumulative industrial toxics.

Comment noted; these have been added to the listing.

These facilities have been referred to as (defensive measures( in past documents, including the Water Quality Act of 1987, which authorized the project.

Growth is certainly a major factor in estimating future sewage flows.  However, as noted in the SEIS, Tijuana is not fully sewered; its existing pumping, conveyance and treatment capacity would not be adequate to serve existing residents and industry if fully sewered.

The San Antonio de los Buenos facility was designed as a secondary treatment works as identified in Minute No. 270.  There is no monitoring data available for the plant effluent.  The treated effluent is required to meet Mexican standards for discharge to national waters (appended to the SEIS) and U.S. standards at the international border, as specified in Minute No. 283.

Although chlorination and dechlorination facilities are part of the IWTP design, it is anticipated that chlorination of the effluent will not be necessary based on the results of the ocean modeling for both secondary and advanced primary discharge through the SBOO.  The dechlorination facilities would not be available for the interim discharge prior to the completion of SBOO.  As discussed in the SEIS, chlorination of the effluent for discharge other than to SBOO would probably not be feasible due to impacts to the river and estuary associated with trace residual chlorine.  Chlorination/dechlorination of effluent to be discharged through the SBOO would only be undertaken if needed to meet bacterial standards in receiving waters. It will be considered further if monitoring data of actual IWTP discharges indicates a need for disinfection.

The 1994 FEIS ROD would not be violated.  The ROD stated that no discharge other than secondary effluent through the outfall would occur until additional environmental review had taken place.  The SEIS provides the additional environmental review required by the ROD.

The proposed action seeks to avoid any discharges to the Tijuana River.  Discharge to the river is addressed because under certain flow conditions it could occur if the IWTP is operated prior to completion of SBOO.  The preferred Alternative 6, which includes using detention basins to store treated effluent for off-peak discharge to the emergency connection prior to completion of the SBOO, should avoid any discharges to the river.  Creating a larger temporary storage facility at the Imperial Beach Naval facility would require additional conveyance pipelines to be constructed, without additional benefit.  Closing the base is not an available option to the EPA/USIBWC.

The Regional Water Quality Control Board will be the permitting agency for any discharges from the IWTP and will set requirements for mitigation if any discharges to the river occur.  EPA and USIBWC will be responsible for ensuring that required mitigation is implemented.

The commentor is incorrect.  Construction at the IWTP is not ongoing on a 24-hour-a-day schedule; it is being completed on a normal workday schedule.  Portions of the SBOO construction are on a 24-hour schedule, due to construction requirements for tunneling.  Construction of the detention basins cannot begin until a ROD is signed for the SEIS.

Alternatives 3 and 6 maximize use of the emergency connection during the interim period.  As discussed in the SEIS, the emergency connection was not intended to be a permanent facility and its future availability will be constrained by sewage generated in the U.S.

Bioaccumulation of metals other than mercury (e.g., lead) in fish is addressed in Appendix C of the SEIS; lead in the effluent is not considered a potential human health risk as levels do not appear to increase in fish up the food chain.

Section 2.2.1.5 does not state that discharges in Mexico do not flow northward.  The effects of discharges in Mexico were modeled for the SEIS and are discussed in Section 4.2, including periods with northward current transport.

Table S-1 provides a summary of adverse impacts for each alternative.

The daily flow of sewage that can be sent via the emergency connection is limited by diurnal peaking factors, as is explained in the SEIS.  Under Alternative 2, the IWTP is initially providing additional storage of two million gallons that would otherwise exceed the hourly flow capacity of the emergency connection and flow to the Tijuana River.  The statements made at the scoping sessions summarized on page 320 refer to operating efficiency and not treatment performance.  Treating 10 mgd is more efficient and economical with respect to plant operations, but flows less than 10 mgd can be treated fully.

The SEIS outlines the anticipated flows to the river from increases in sewage given the existing facilities in Mexico and proposed new facilities in the U.S.  If circumstances change, such as the annual increases in flow from Mexico are greater than forecast, a failure of facilities occurs in Mexico, or there is otherwise a reduction in the flows Mexico handles with its system, then additional flows could occur in the Tijuana River.

No, for January 1997.  Table 2.3 provides estimates through 2001.

The SEIS provides flow estimates that will go to the IWTP.  The IWTP does not have to have a minimum of 10 mgd of flow to provide advanced primary treatment.

Costs for utilizing the emergency connection are based upon a flat rate per mgd of sewage.  Costs for treatment at the IWTP are variable, with the unit cost per mgd decreasing as the volume of sewage treated increases.

As explained above, the IWTP can treat flows less than 10 mgd.

The discussion on page 211 indicates that even though there would be a reduction in discharges of untreated sewage at the shoreline in Mexico, there would still be concern for coliform levels for treated effluent discharges.  For coliforms, primary treatment only reduces coliform levels by approximately 20 percent.  Therefore, there is little difference in health risks from bacterial pathogens between the discharge of untreated sewage or primary treated effluent.

The SBOO is scheduled to be operational in June 1998 and the Final SEIS text on page 82 is revised.

The data requested on industrial discharges in Mexico is not available at this time.  Minute No. 283, the 1994 FEIS, and ROD for the project have recognized the need for pretreatment and source reduction for industrial dischargers in Mexico and current steps to implement and expand the Mexican program are described in the SEIS in Section 1.3.1.10.  USIBWC is conducting a headworks analysis to identify effluent limitations for industrial wastewaters directed to the IWTP.

The purpose of the project is to avoid discharge of dry weather sewage or IWTP effluent to the river and estuary.  It is anticipated that with selection of the preferred alternative, no discharges of treated effluent from the IWTP to the river or estuary would occur.  There are uncertainties, however, and the SEIS seeks to disclose the potential effects if discharges do occur.  The RWQCB will require monitoring of the river and estuary if discharges should occur so that the effects of the discharges can be measured.  The responsible resource agencies have been consulted during the scoping of the project and have reviewed the SEIS.  No specific mitigation for the contingency if discharges do occur has been recommended at this time.  EPA and USIBWC will reopen consultation with the agencies if discharges to the river become unavoidable.

For purposes of comparison of the alternatives, including using the SBOO for discharge of effluent, each alternative was evaluated as a stand-alone alternative through the planning horizon period of 2001.  If SBOO were not used for discharge, there could be discharges to the river between 1998 and 2001 for several of the alternatives.

Effluent concentrations were estimated by the IWTP design engineering consultant, Malcolm Pirnie Engineers.  Effluent concentrations were not provided for certain constituents for a variety of reasons, including lack of influent concentration data or specific treatment efficiencies.  The IWTP will be test operated for several months once completed, at which time additional data will be available.

Covering the basins to reduce nuisance odor impacts is included as potential mitigation for the detention basins in the SEIS.

EPA and USIBWC recognize that monitoring is not mitigation.  However, monitoring to assess whether there are impacts from river discharges and to what extent the river or estuary habitats are impacted is a necessary precondition to providing appropriate mitigation.

We are sorry for the inconvenience; these omissions were a reproduction error in some copies.  The Minutes were appended to the 1994 FEIS and USIBWC can make full copies available upon request.

This is a typographical error in the original memo; Mr. Gold is a City of San Diego attorney.

By agreement, Mexico will be responsible for the disposition of sludge, which for the interim operations period will go to the Tijuana landfill in Mexico.  As the landfill is not in a north-draining canyon to the Tijuana River, no impacts to the U.S. are anticipated.

The SEIS discusses the prior international agreements with Mexico, U.S. environmental laws, and Executive Orders, and summarizes environmental laws of Mexico.  Air emissions from the IWTP operation were assessed in the 1994 SEIS and have been subject to additional review by the APCD in issuing permits to construct and operate.

Lev D. Rozman, Ph.D.

The commentor suggests that more evaluation be done in order to optimize the location of the outfall terminus with respect to initial dilution and subsequent mixing.  The type of effort described was completed early on in the project (1990) and led to the determination of the length of the outfall and its discharge location.  It was found that a 14,100 foot long outfall would be sufficient to meet regulatory standards.  In view of the potential for re-entrainment in the area, Engineering Science (the outfall designer) investigated the effects of the currents on initial dilution and determined that a longer outfall would be needed to meet the intent of the standards.  This issue was presented in the 1994 FEIS for the project.  It is possible that other sites might exhibit higher diffusivities than the selected location; however, the location must satisfy several other criteria, including conditions of poor circulation or prevailing conditions during periods of unfavorable water movements.  In evaluating the performance of the outfall with computer modeling, Engineering Science used conservative values for diffusivity for the South Bay, resulting in lower estimates of the total dilution that may actually be achieved.

San Diego-Tijuana Sister Cities Society

Comment in support of the parallel conveyance in Mexico is acknowledged. EPA and USIBWC are providing funding and technical assistance to CESPT, who will sponsor construction of the system through BECC.

Save Our Bay, Inc.

Rainfall data and river flow data are available, but EPA or USIBWC do not have any studies that correlate rainfall events and flows in the river reaching the shoreline.  The FEIS and SEIS discussions of hydrology provide evidence of the variability in river flows (annual median 659 acre-feet; annual average 33,000 acre-feet and annual maximum of 586,000 acre-feet).  The wet weather flows typically occur December through March, which is also the period when most rainfall is received.  The frequency and severity of storms as well as the annual total rainfall all contribute to river flows and flow volumes.  The Tijuana River watershed includes three reservoirs, and portions of the river in urban Tijuana have been channelized, which are complicating factors.  The goal of the IWTP is to minimize the potential for dry weather flows of sewage contaminating the U.S.  Unfortunately, conditions that would allow runoff in the Tijuana River to be contaminated with sewage still exist and the potential for wet weather contamination of beaches will continue.

The FEIS and SEIS both indicated that wet weather flows in the Tijuana River would not be intercepted and could be contaminated with sewage.

SBOO is an acronym for South Bay Ocean Outfall.

Apparently there were no flows in the river at the time.  The flow estimates are forecasts based upon conservative estimates of various factors contributing to sewage in Mexico.  They were developed to evaluate the various alternatives under consideration.

The State Water Resources Control Board provided funding to the City of San Diego for the SBLO.  The Regional Water Quality Control Board is responsible for the permitting of any discharges.  Both agencies serve on the policy and technical oversight committees for this project.

The potential for discharges in Mexico impacting U.S. waters was modeled for the SEIS and is discussed in Chapter 4.2.  The body contact standards for U.S. waters have the potential to be out of compliance June-August and during November, according to the modeling.

See response to comment #3.

Sewage from western Tijuana was estimated at approximately 10 percent of the sewage generated in eastern and central Tijuana.  Sewage from Playas de Tijuana does not flow into the U.S.  Spills from the canyon areas west of pump station one have varied in size over the years.

Wet weather and storm flows refer to periods when the Tijuana River has runoff flows.  Dry weather flows refers to periods when flows occur in the river that are not related to rainfall or fresh water releases of water from reservoirs in the watershed.

The IWTP has a peaking factor of 3:1 so hourly flow rates in excess of 1 million gallon can be accommodated.

Comment noted; the word maximum should be deleted from the text.

Comment noted; the syntax in the SEIS text is confusing.

The planning horizon year of 2001 is used to account for the completion of the SBOO and the re-evaluation and completion of secondary treatment process components for the IWTP.

There have been dry weather discharges of sewage to the river during 1996, although they fortunately have not met the forecast volumes estimated in the EPA/USIBWC flow memo.

Although Mexico has made a number of improvements to prevent sewage from entering the river, conditions still exist which would make it likely that wet weather season river runoff entering the U.S. would be contaminated with sewage.  Mexico has planned additional improvements to the Tijuana River which will reduce the likelihood of sewage contamination.  The flow memo forecasts address the potential for dry season contamination.

SBOO is still scheduled to be completed in 1998.

No modeling of the frequency of wet weather flows in the Tijuana River was conducted for the SEIS.

San Diego Chapter of the Sierra Club

The Sierra Club expresses concerns that any discharges to the Tijuana River would have adverse impacts on the environment.  This conclusion is consistent with the SEIS analysis.  The Sierra Club supports only the (return to sender( and (emergency connection( alternatives offered in the SEIS.  It should be noted that the preferred alternative would utilize the emergency connection and additional pumping and conveyance facilities in Mexico if they are available to avoid discharges to the Tijuana River until SBOO is available.

The EPA and USIBWC have been working with the appropriate parties since 1994 to create a (return to sender( connection to transport IWTP effluent to the Punta Banderas facility for discharge with other Tijuana sewage flows.  The (return to sender( option could be used to transport-treated effluent for reclamation and reuse in Tijuana as well as untreated sewage.  Federal agencies are concerned about impacts to U.S. waters if additional facilities are used to transport and discharge untreated sewage to the shoreline in Mexico.  These facilities would have to be agreed to and operated by Mexico, and cannot be assured by actions by U.S. agencies.

The IWTP effluent is not the equivalent of Point Loma effluent.  According to the NPDES permit application to the RWQCB, BOD levels (204 mg/l vs. 273 mg/l at Point Loma) and suspended solids (88 mg/l vs. 289 mg/l at Point Loma) are substantially less; other constituents vary.

Comment noted.  This is acknowledged in the SEIS.

The preferred alternative in the SEIS seeks to avoid discharge of effluent to the Tijuana River.  The SEIS discusses recent actions by the sponsoring federal agencies to assist Mexico in the development of an industrial pretreatment and source reduction program.  Development of this program is under the jurisdiction of Mexico according to its laws.

Chlorination and dechlorination of the IWTP effluent is not proposed, although it could be done in the future to disinfect effluent discharged through the SBOO.  Potential effects to the environment from trace residuals from chlorination are addressed in Section 4.1.1.3 of the SEIS.

Discharge to the Tijuana River is possible under the preferred alternative, although all reasonable measures to avoid the discharges will be taken..  Discharges of untreated sewage or treated effluent could occur if the capacity of the emergency connection is exceeded prior to SBOO being completed.  This would be more likely to occur if no action is taken.

EPA and IBWC have been pursuing the implementation of the (return to sender( facilities with the appropriate agencies in Mexico. EPA and USIBWC have made funding and technical assistance available to CEPT, who will sponsor the project through BECC.

Effluent from the IWTP would not be chlorinated prior to discharge to the river.  The effluent from the IWTP discharged to SBOO is not proposed to be chlorinated unless it is necessary to achieve a reduction in pathogens.  Provision has been made for this as a contingency and the RWQCB will require monitoring of the discharge through the NPDES permit.  The EPA and USIBWC do not want to commit to this decision until the IWTP has been test operated.

It is the intent of the proposed project (preferred alternative) to avoid any discharge to the Tijuana River; however, because flow projections are only estimates, the possibility exists that Mexican flows will exceed the discharge capacity before the SBOO facilities are available.  If that occurs, discharge of either untreated sewage or treated effluent into the Tijuana River will be unavoidable.  The SEIS acknowledges that the discharge would not be consistent with the federal Clean Water Act.  It may meet State Ocean Plan requirements, however.

Additional studies and assessments of Mexican sewage flows for heavy metals and other toxics will be conducted once the IWTP is operated.  Both influent and effluent will be monitored.

Whatever flow conditions prevail, sewage flows that exceed the capacity of the Mexican system and the emergency connection would be discharged to the Tijuana River as either untreated sewage or advanced primary treated effluent.

Christopher Teng

The cost of construction and operations and maintenance specified in Minute No. 270 is the obligation of the Mexican government.  Mexico is to operate the San Antonio de los Buenos treatment facility in such a manner that the quality of the coastal receiving wastes at the international boundary comply with the water quality criteria established for primary contact recreation uses.  Monitoring of the surf conditions at the international boundary is performed for this U.S. section of the IBWC and this data is available to the public.

Mexico will participate in the cost of constructing and operation and maintenance of the IWTP in accordance with provisions in Minute No. 283.  Specifically, this cost contribution will be in the negotiated amount of what it would have cost Mexico to build a 25 mgd secondary treatment plant at the Rio El Alamar that would have produced an effluent that meets Mexican standards for discharge to rivers and streams.  Additionally, Mexico will participate in the annual operation and maintenance cost in an amount equivalent to what it would have cost Mexico to operate a 25 mgd treatment facility at the Rio El Alamar.  The construction, operation, and maintenance at the outfall for ocean disposal is at the sole expense of the United States.

Monitoring of the discharge from the IWTP will be in compliance with the NPDES permit issued to the IBWC from the RWQCB and will be available to the public.

The funding for (various environmental cooperation mechanisms( (page 30 of the SEIS) to meet required pretreatment of industrial discharges in Mexico is not specifically identified.  The Department of Ecology, Baja, California, Mexico; EPA; USIBWC; SWRCB; and the City of San Diego are assisting U.S. cooperative actions under various grant programs.

Peak flows in excess of 100 mgd would flow untreated to the Tijuana River.  The emergency connection to Point Loma is the only discharge option other than the Tijuana River.

The time frame for implementing various secondary treatment options will be assessed in the Alternatives to Activated Sludge Supplemental EIS.

Section 1.6 of the SEIS acknowledges that Tijuana(s sewer improvements are an (unknown factor( in evaluating the potential impacts of the proposed interim operation of the IWTP.  The EPA/USIBWC continue to communicate on a regular basis with Mexican officials regarding sewerage improvements on both sides of the border.

The commentor is correct and this inconsistency is acknowledged in the SEIS.

The least Bell(s vireo is migratory but breeds in southern California(s freshwater riparian habitats.  The proposed capture of dry weather, periodic sewage flows, will not adversely affect this habitat.  This issue was considered in the Biological Assessment and 1994 FEIS prepared for the construction of the IWTP and SBOO.

Page 155, Section 3.4.5 of the SEIS addresses estuarine biology and not terrestrial biology where the least Bell(s vireo is discussed.  Please see page 146, Section 3.3.3 of the SEIS.

Surfrider Foundation

The intent of the project is to keep untreated sewage out of the Tijuana River, not to discharge treated effluent to the river.  The IWTP would treat those flows that cannot be handled by Mexico.  Mexico has agreed, to the best of their ability, to retain sewage flows at their current levels until the SBOO is built (see Attachment 1); and the City of San Diego has agreed to continue to accept sewage through the emergency connection.  The flow projections used for the SEIS (Appendix A) are based upon these agreements, and 1995 flow measurements and a 4.8 percent annual growth rate.  Based on the estimated flows, the preferred alternative would avoid discharges of untreated sewage or treated IWTP effluent to the Tijuana River in the U.S. during the dry weather season.  If the following were to occur: (a) sewage flows in Mexico increase sooner than expected; or (b) Mexico reduces the volume of sewage it retains in its existing system; or (c) failures occur in the pumping or conveyance system in Mexico; then untreated sewage would enter the U.S. via Stewart(s drain or other locations.  If the IWTP is operated, flows that otherwise would enter the river untreated could be treated at the IWTP prior to discharge.  There is no basis to assume that the volume of flows from Mexico would be different with or without the IWTP.

The Final EIS and ROD for the project disclosed that interim operation of the IWTP as an advanced primary treatment plant may occur prior to the SBOO or secondary treatment facilities being available.  However, this could not occur unless additional environmental documentation were performed. This SEIS satisfies that requirement.  This NEPA process was agreed to by Surfriders in a Settlement Decree (San Diego Chapter of the Sierra Club et al. vs. International Boundary and Water Commission, United States Section et al.) (see Attachment 2) and Surfriders and all the other parties participating in the settlement was aware of the approach prior to release of the SEIS.

Criticisms of the modeling performed by Parsons Engineering Science are responded to in more detail below. At the request of the Surfrider Foundation, EPA solicited an independent review of the modeling.  It was reviewed by A. J. Mearns for the National Oceanographic and Atmospheric Administration (NOAA); his review comments are attached to NOAA(s letter of comment to the SEIS.  It was also reviewed by EPA, USIBWC, U.S. Army Corps of Engineers, the State Water Resources Control Board, and City of San Diego.  EPA and USIBWC support the modeling as a reasonable and technically valid approach to assessing environmental impacts of the interim operation of the IWTP.  EPA and USIBWC do not concur that the 1988 TOES supports the assumption that there are no, or rarely, northward flows from the shoreline discharge point in Mexico.  The 1988 TOES found that upcoast (north-trending) currents predominate about 27 percent of the time.  There is also evidence of north-trending currents from satellite imagery data and bacteriological sampling along the shoreline both in Mexico and the U.S.  It should also be noted that Minute 270 was predicated upon protecting U.S. waters from discharges of effluent or sewage in Mexico along the coastline.

IBWC is a binational commission empowered by both governments to address border issues.  Collaboration with the Mexican section of IBWC has been ongoing throughout the project.  EPA and USIBWC acknowledge the difficulties in sharing information between the two countries; and have and will continue to take steps to improve communication.  EPA and USIBWC support the CALBECC (with the Direccion General de Ecologia and Secretaria de Asentamietos Humanos y Obras Publicas for Baja, California and the Commission Estatl de Servicios Publicos de Tijuana) and other initiatives.  The operations minute is identified as a needed agreement to be negotiated with Mexico in the SEIS, and will be completed before the IWTP is operated.

As a statement of purpose and need, many technical details contained in other sections of the document (e.g., Chapter 2) are not presented in this section of the SEIS.

The commentor(s reference to the EPA, USIBWC, and SWRCB investigative team or its findings is unclear to those agencies.  Real time recording meters are being installed by IBWC and more closely monitored data will be available in the future.

All the assumptions regarding flows in Mexico are stated in the Flow Memorandum, Appendix A to the SEIS.

The flows through the conveyance canal and treated at San Antonio de los Buenos are based upon estimates by Mexico, the USIBWC and Minute No. 283.  These estimates were confirmed by a representative of CESPT in 1996.

The commenter is incorrect, there is ample evidence of northerly nearshore currents at the shoreline discharge point in Mexico based upon the TOES I and II current studies, satellite imagery data, and bacteriological concentration data as is summarized in the Parsons Engineering Science shoreline discharge model study.  EPA and USIBWC have not been able to confirm the accuracy of the reference to a 0.06 percent probability in the TOES study.  If treated effluent were discharged to the Tijuana River, there would certainly be significant impacts to the river, estuary, and nearshore coastal areas.

That the project addresses the problem of dry weather flows is stated throughout the SEIS.  It is clearly stated that wet weather river flows would not be intercepted. If contaminated with sewage, these flows would continue to affect the river valley, estuary, and coastal areas.

As indicated in the SEIS, Mexico has agreed to continue to convey and treat sewage at current levels until the SBOO is completed. Given this assumption, flows of 25 mgd will not be discharged to the river valley.  See response to comment #1.  If operating the plant would result in the need to treat and discharge sewage to the Tijuana River that Mexico is currently able to convey and treat, there would be a negative impact.  However, the SEIS does not address this scenario since it would be inconsistent with existing agreements.

Both the FEIS and SEIS include summaries of the past problems with border sewage contamination, and the numerous treaties, minutes, declarations, and agreements made in response.

Point Loma, as a primary treatment works with ocean discharge was permitted by the state of California, along with treatment works at Encina, San Elijo, and Goleta.

The characterization of IWTP effluent as equivalent to Point Loma influent is misleading.  According to data presented to the RWQCB for the IWTP NPDES permit, the IWTP effluent will have reduced levels of BOD5 (204 mg/l vs. 273 mg/l at Point Loma) and suspended solids (88 mg/l vs. 289 mg/l at Point Loma) compared with levels of Point Loma influent.

The Interim Operation proposal would not import sewage from Tijuana.  Mexico has agreed to continue to handle the current volume of flows until SBOO is operational.  Only flows from Tijuana that would otherwise enter the U.S. untreated and flow through the Tijuana River would be treated at the IWTP until the SBOO is operational.  There is no basis for assuming that the IWTP would treat 25 mgd of sewage once it is operational.  The IWTP has a design capacity of 25 mgd.  Because sewage flows vary diurnally, a peaking factor of 3:1 (75 mgd hourly flow equivalent) was provided to accommodate peak hourly flows.  Mexico generates approximately 42 mgd of sewage currently; which is expected to rise to approximately 51 mgd on the highest flow days by the year 2001.  The scenario of the IWTP taking 75 mgd from Tijuana is not realistic.

Potential limitations on the future availability of the emergency connection are explained in the SEIS.  The City has indicated its willingness to continue to accept sewage from Mexico to avoid discharge to the river as long as it has capacity in its conveyance system.

IWTP effluent will not be equivalent to Point Loma influent.  Modeling conducted for the SEIS indicates that non-disinfected IWTP effluent discharged through the SBOO has a very low probability of impacting any beaches or recreational areas near the coastline.  Discharge of treated effluent to the river would represent a health risk, however.

The Final EIS and ROD for the project disclosed that Interim Operation of the IWTP as an advanced primary treatment plant may occur prior to the SBOO or secondary treatment facilities being available.  However, this could not occur unless additional environmental documentation were performed.  This SEIS satisfies that requirement.  Secondary treatment options are currently being evaluated and will be addressed in a subsequent SEIS, along with the alternative of continued operation as an advanced primary treatment works.  Surfriders agreed to this approach in a settlement agreement with the EPA prior to release of the SEIS.  No decision has been made by EPA or USIBWC to operate the IWTP as an advanced primary treatment works for a term longer than five years, the interim operation planning horizon.

Pond-based treatment is not a reasonable alternative to the interim operation of the IWTP considered in the SEIS and the panel study results are not relevant to the decisions being made.  Pond-based treatment systems will be evaluated in the Alternatives to Activated Sludge SEIS which is in preparation.  Detention basins discussed in the Interim Operations SEIS would be temporary (cycled daily) storage basins for flow equalization to the emergency connection and would not function as treatment ponds.  The current interim operations SEIS does not eliminate any secondary treatment options that would otherwise be considered, including ponds, activated sludge, or other means.

EPA/USIBWC used the most up to date flow information available to them at the time the forecasts were made (data were collected in Mexico in 1995 from the collection system with the cooperation of Mexico).  They are consistent with previous estimates, although there is a range of variation.  The prior FEIS discussed a range of future flow estimates and their basis.

The No Action alternative would result in significant environmental pollution and human health risk; and the resulting water quality in the river would violate federal and state water quality standards.  Since there would be no authorized discharge, there would be no possibility of enforcement of water quality standards.  The SEIS indicates that the discharge of less than secondary treated effluent is not authorized by the federal Clean Water Act.  Discharge of advanced primary effluent to the Tijuana River would not meet Basin Plan objectives for surface- or groundwaters.  Discharge of advanced primary effluent through the SBOO may or may not meet the California Ocean Plan (the modeling indicates PAHs and HCH limits may be exceeded).  The No Action alternative would not minimize public health and environmental impacts relative to other alternatives under consideration.

Section 1.3.1 of the SEIS does not discuss the capacities of the Mexican system.  Minute No. 270 states that the peak capacity of the force main is 62 mgd.  The reliable peak capacity of Pump Station One is approximately 36 mgd and the effective capacity of the conveyance canal is approximately 48 mgd.  Note that the conveyance canal has to carry additional flows from western Tijuana in addition to flows from Pump Station One.  The flow memo is based on these capacities.

A detention basin is not intended to provide treatment and would be filled and emptied within a daily cycle to provide flow equalization for discharge through the emergency connection.  They are not equivalent in function to treatment ponds.  The size of the detention basins are based upon the daily volume needed to maximize use of the emergency connection, estimated at 5.5 million gallons.  The basins have been sized and sited to minimize pumping requirements and allow gravity flow to the emergency connection.  Feasibility studies are being conducted for use of treatment ponds for long-term use and will be considered in a Supplemental EIS.

The commentor is correct; treated effluent would not meet health standards for discharge to the river.  The discharge modeling suggests that health standards would be met for the SBOO discharge, however.  The 1,000 minimum probaby number (mpn) coliforms standard is not applied at the point of discharge.  It applies at the 30 feet water depths or within 1,000 feet of the shoreline or nearshore recreation areas.  Bacterial die off and dilution of the effluent would reduce concentrations below the standard.  It is not agreed treatment will increase mass loading of coliforms or suspended solids to the environment relative to untreated effluent, as only equivalent volumes would be discharged.

Mexico chose a capacity of 50 mgd to match the capacity of their current force main and conveyance canal capacities.  The EPA and USIBWC support the construction of a parallel pumping and conveyance system in Mexico to reduce the risks of failure of the Mexican system causing adverse consequences in the U.S.  Mexico has stated its opposition to such a system being used in lieu of the SBOO, however.  Its ultimate construction and operation is at the discretion of Mexico.

Effluent dispersion for the SBOO has been modeled for both secondary and advanced primary effluent based upon samples of Tijuana sewage without an industrial pretreatment program.  The concerns raised about a counter current gyre dumping effluent back to beaches in Imperial Beach and Coronado is not supported by the ocean discharge modeling in the 1994 FEIS and current SEIS.

The ocean discharge modeling has shown that discharge through the SBOO would have the least impact on the environment and threat to public health.  The model results will be verifiable through the NPDES permit monitoring program that will be required by the RWQCB for the discharge.

The preferred Interim IWTP operation evaluated in the SEIS would allow advanced primary operation of the plant through the year 2001 with discharge through the emergency connection.  The phased alternative would initially utilize the detention capabilities of some of the primary treatment facilities to provide additional flow equalization and limited treatment (screening, degritting, and settling) of about 2 million gallons prior to discharge to the emergency connection.  Once the 5.5-million-gallon detention basins were constructed, the IWTP would be operated with discharge through the emergency connection to its maximum of 13 mgd.  Flow volumes would be as shown in Table 2-3 through 1997 and Table 2-4 for 1998, and Table 2-6 to the year 2001.  Costs for discharge to the emergency connection are a fixed unit cost per million gallons of sewage.  Costs to operate the IWTP have both a fixed operational cost and a variable cost for chemicals and energy usage.

Once the SBOO is on-line no additional discharge capacity is needed to supplement the SBOO.  It has been designed for up to 174 mgd average, 333 mgd peak flows.  These flow volumes are not needed for interim IWTP operation; but are valuable as a facilities improvement for the discharge system for reliability.

Again, Mexico construction of additional pumping and conveyance in Mexico is at the discretion of Mexico.  While EPA and USIBWC have been in active negotiations, they cannot unilaterally construct these facilities.  CESPT has only recently agreed to sponsor the construction of the facilities through the BECC, with funding and technical support from USIBWC and EPA.

The preferred alternative maximizes use of Mexico(s existing facilities and the emergency connection until SBOO is available.  It is expected that no discharge to the river would result.  Discharge of treated effluent with respect to the Clean Water Act, State Ocean Plan, and Basin Plan are discussed in the SEIS.  EPA and USIBWC believe that it best meets project(s stated purpose.

The consideration of interim operation of the IWTP prior to secondary treatment processes or the SBOO was disclosed in the 1994 SEIS and the SEIS process and alternatives considered was agreed to in the settlement agreement by Surfriders.

Mexico has taken the position that additional pumping and conveyance facilities are not acceptable as an alternative to the SBOO.  This alternative is not available to EPA and USIBWC.

Section 4.2 of the SEIS details the effects of SBOO discharge.  There are less adverse impacts to U.S. waters from the SBOO discharge than the discharge of untreated sewage to the shoreline in Mexico.

The commentor is correct, discharge of secondary effluent through the SBOO with industrial pretreatment or source reduction in Mexico is the preferred alternative, as indicated in the 1994 EIS and ROD for the project.  Secondary treatment options for the IWTP will be evaluated in an SEIS, as agreed to by Surfriders.  However, in the interim period the decision to be made is whether No Action is preferable to operating the IWTP as an advanced primary plant.  In that case, discharge through SBOO is preferable to other discharge options, and avoiding discharge to the river of effluent from the IWTP is imperative.

EPA and USIBWC disagree with two fundamental assumptions made by Surfriders in their amendments to Table S-1: that the IWTP would immediately treat and discharge 25 mgd to 75 mgd of sewage from Tijuana and that no evaluation of the effects of discharge through the SBOO is available.  The flow estimates prepared by EPA and USIBWC are considered the best available forecasts.  For reasons explained in response #1, EPA and USIBWC reject the assumption that 25 mgd flow would be directed to the IWTP.  The entire volume of Tijuana sewage that would be generated through the year 2001 is not forecast to exceed 52 mgd, even during wet weather high flow days; the 75 mgd figure could only occur as a peak hourly flow rate.  Discharge through the SBOO has been demonstrated through detailed modeling to be superior to shoreline or river discharge (Chapters 4.1 and 4.2 of the SEIS).  By Surfrider(s own analysis, the No Action alternative has significant unavoidable adverse impacts under each issue except Geology.  EPA and USIBWC do not find that No Action is an environmentally superior alternative.

EPA and USIBWC do not agree with the commentor(s statements regarding flows.

Minute No. 270 outlined improvements to Pump Station One which included providing a 62 mgd peak capacity, with 34 mgd average capacity.  However, as designed and built, the pump station currently has a peak capacity of 50 mgd with all four pumps operating.  As stated in the SEIS, one pump is used as a backup.  The reliable peak operating capacity with three pumps is approximately 36 mgd.

As indicated in section 2.1.1.1 of the SEIS, although the conveyance canal has a peak design capacity of 62 mgd, because of accumulations of debris in the canal and siphons and the lack of opportunities to perform regular maintenance, the usable capacity of the canal is estimated at 48 mgd.

This section of the SEIS clearly states that the activated sludge portion of the IWTP (. . . has been designed, but construction has been postponed until an additional SEIS has been finalized.(  All other major elements of the IWTP are either completed or currently under construction.

The SEIS does not state that the flows cannot be disinfected, but that chlorination/dechlorination may not allow the flows to meet standards for trace residual chlorine.  Dechlorination of effluent at the IWTP would require additional facilities as well.

The supplemental EA was circulated for public and agency review, and is referenced in the SEIS (U.S. Army Corps of Engineers 1996).  Bacterial levels for treated effluent and their transport and fate if discharged to the shoreline in Mexico or through SBOO were modeled for the SEIS.  Adverse effects from chlorination were also identified.

Please see attached letter from Commissioner Solis of the Mexican Section USIBWC (Attachment 1).  Mexico will continue to convey a total of approximately 42-45 mgd to San Antonio de los Buenos, of which 17 mgd will be treated and the remainder discharged to the ocean untreated.  Pump Station One peak design capacity is 50 mgd, with an approximately 36 mgd reliable peak capacity.  Peak design capacity of the conveyance canal is 62 mgd, but due to debris accumulation, the effective capacity is estimated at 48 mgd.

It is standard convention to express flow rates in millions of gallons per day (mgd).  However, peak hourly flows are not sustained for a 24-hour period.  A peak flow rate of 73.4 mgd is equivalent to approximately 3 million gallons per hour; 91.8 mgd peak flow is approximately 3.8 million gallons per hour.  Total throughput through the system is expressed as the average flow in mgd, and takes into account the predicted peak and low flows throughout the day.

These considerations relating to treatment ponds are outside the scope of the Interim Operations SEIS.

There is ample evidence to support the basic findings of the EPA/IWBC flow memo.  The Mexican section of IBWC has reviewed the flow memo.  Mexico(s estimate of the current capacity of the San Antonio de los Buenos treatment works is 17 mgd.  It is estimated that by the year 2001 total flows to the plant would reach 39.9 mgd such that 22.9 mgd of raw sewage would bypass the treatment works and be discharged directly to the shoreline.  The effects of shoreline discharge in Mexico to U.S. waters are included in the modeling for the SEIS.

The SEIS characterizes the current setting as untreated flows to the Tijuana River estimated to average 1.1 mgd in 1996 and are expected to reach 5.6 mgd average by the year 2001.

The SEIS does not state that the peak capacity of Pump Station One is 62 mgd nor 48 mgd.  The peak capacity of Pump Station One is 50 mgd with all four pumps operating.  However, only three pumps operate resulting in a peak reliable capacity of approximately 36 mgd; the fourth pump being reserved as a backup in the event of equipment failure.  Pump stations in the U.S. would also be rated this way, with one pump held as a reserve.

Alternative 3 in the SEIS incorporates a detention basin for flow equalization and storage during interim operation.  The use of ponds for secondary treatment, including the results of previous studies, is currently under evaluation and will be addressed in a second SEIS.

Comment acknowledged.  If these data were available at the time the SEIS was prepared, they would have been included in the Draft.

The final Construction and Operations Minute has not been finalized at this time; it will be finalized before the plant is operated.

Yes, it will reduce the potential for discharge to the river and estuary.

Yes.

No, as discussed in the SEIS.

The modeling results of discharge through SBOO indicates that the effluent may not meet two criteria pollutant concentration at the zone of initial dilution.

Yes.

Not applicable.

Because interim operation limits the amount of untreated sewage discharged to the river, yes.

Majority of commentors to the SEIS support the preferred alternative (i.e., USFWS, NMFS, Center for Disease Control, City of San Diego, City of Imperial Beach, City of Coronado, Tijuana Valley County Water District, Citizens Revolting Against Pollution, Citizens Against Recreational Eviction).

No response required.

No response required.

Surfriders are a party to the settlement agreement which laid out the scope of the supplemental SEISs that are being prepared for the project.

Congress authorized this with the original funding for the project.

The RWQCB will make this determination.

The concentration is 1.6 x 108 total coliform MPN/100 ml.  The State Health Standards referenced are for the shoreline at 30 feet water depth or within 1,000 feet of the shoreline or coastal recreation area.  Taking into account bacterial die off and dilution, the effluent is expected to meet the standard.

As coliform bacteria are subject to relatively rapid die off, (a 90 percent reduction in 4 hours) mass loading of coliforms is not considered to be as critical as the diurnal changes in the rate of reduction, which was analyzed in the discharge modeling for SBOO and coastal waters.

The difference between a primary or secondary effluent discharge to receiving waters is not whether a discharge occurs or its volume; but the constituent concentrations of the discharge.  The effects of discharge to the river, estuary, or ocean was considered in the SEIS, whether the effects should be considered direct or indirect effects.

EPA and USIBWC disagree for reasons stated in response to #1.

To the extent that discharges in Mexico adversely affect U.S. waters, shoreline discharges are relevant to the purpose and need and goals of the action.  Modeling of the transport of discharges in Mexico conducted for the project and historical records of coliforms at the international border indicate that such discharges are relevant.

The IWTP will not discharge 25 to 75 mgd.

Effects to riparian habitat and wildlife are considered in Section 4.3 of the SEIS.

This and other hydrographs in Chapter 2 were prepared by Boyle Engineering who are technical advisors to the project.  Flows are based upon best available information.  The SEIS clearly states the assumptions for the flow analysis and Mexico(s current system capacities.  The conveyance canal is labeled on Figure 2-1.

See response #72.

See response #72.

A comparison of the relative pollutant loadings between each of the alternatives is discussed for each alternative in Section 2.2 (Comparison of Alternatives( of the SEIS.  While it is obvious that 25 mgd of treated effluent would have greater mass loadings than 1 mgd of untreated effluent, it is irrelevant to evaluating the alternatives in the SEIS.

Basing a comparison of IWTP effluent with Point Loma influent on the basis of BOD alone is misleading.  BOD would be somewhat lower than Point Loma effluent, suspended solids substantially lower.  Other constituents vary with treatment efficiencies.

The SEIS acknowledges adverse health impacts from coliforms for discharges of advanced primary effluent to the river and coastline.

The SEIS does address nutrient loading and eutrophication in its impacts to the river and estuary in its assessment of terrestrial, estuarine, and marine biology (Sections 4.3-4.6) and finds the impacts significant.

As noted above, discharges to the shoreline in Mexico may effect U.S. waters, which is relevant to the purpose and need and goals of the action.

A functional capacity of 36.6 mgd is used for pump station one for reasons cited in the SEIS.  See response #72.

Mexico does not utilize all four pumps at one time, as explained in the text of the SEIS.  See response #72.

The IWTP would provide 2 mgd of flow equalization to assist in preventing flows of sewage to the river, as explained in the SEIS.

A functional capacity of 36.6 mgd is used for pump station one for reasons cited in the SEIS.

A HEC model of the discharges was provided in the SEIS and discussed under hydrology and estuarine biology (Sections 4.1 and 4.4).  No significant impacts to the hydrology of the river would result from flows of 1.1 mgd to 5.6 mgd.  Flows of 25 mgd are not expected.  The SEIS identifies adverse consequences to water quality.

For reasons noted above, 25 mgd to 75 mgd discharges are not anticipated and were not evaluated for the SEIS.

For discharge to the Tijuana River, effluent from the IWTP could be chlorinated but not dechlorinated.  At comparable volumes, the discharge of treated effluent would result in less mass loading than raw sewage.  EPA and USIBWC do not agree that IWTP effluent is roughly equivalent to Point Loma influent.

Flows of 25 to 75 mgd are not anticipated.  Mass loadings from treated effluent would be somewhat reduced relative to discharges of untreated sewage, as the flows would be equivalent.

A discussion of chlorination/dechlorination is provided in Section 4.1.1.3 of the SEIS.  Alternative 2 will result in less pollutant loading to the river and estuary than would the No Action alternative.  It would not meet body contact standards, as acknowledged in the SEIS.

If the same volumes of flow are compared, the mass loadings for treated effluent are less but not below a level to eliminate ecological and human health and safety concerns.  However, it has been repeatedly expressed by the public that taking action by treating sewage that would otherwise be discharged to the river would be a positive step.

BOD, solids, and other constituents have been lowered through detention in an odor controlled environment and ferric chloride has been added to reduce hydrogen sulfide emissions.  That odors may still be objectionable is agreed.

EPA and USIBWC do not agree with the comment and based upon the SEIS conclude that Alternative 2 is preferable to No Action, although it is not the preferred alternative.

EPA and USIBWC cannot confirm the northward drift probability figure cited in the comment as accurately reflecting the conclusions of the 1988 TOES.  Based upon the current modeling, untreated discharges in Mexico appear to have adverse consequences for waters in the U.S.

The commentor is incorrect; there is no undisclosed (maximization( for the pumping or conveyance capacities in Mexico.

As noted above, the sizing of the detention basin is based upon its functioning as a flow equalization for the emergency connection.  If sized above this use, treated effluent would be stored in the basins, which is undesirable.

As noted above, there is no basis to anticipate flows of 25 mgd to the IWTP on a regular basis.

The SEIS discloses that effluent from the IWTP would not meet health or safety standards if discharged to the river.

IWTP effluent is not equivalent to raw sewage.  Riparian habitats in the valley have been exposed to continuous years with dry weather sewage flows prior to 1992.  The effects of these discharges were considered in the 1994 EIS.  It does not appear that dry weather sewage flows adversely impact riparian habitat.

Alternative 3 will not result in discharge of 25 to 75 mgd to the river.  The claimed potential impacts are not realistic.

This comment misstates the analysis presented in Sections 4.1.1 and 4.1.2 of the SEIS.  Adverse impacts are identified in these sections.  Effects of discharge to the shoreline in Mexico to marine biota cannot readily be quantified, but are qualitatively assessed as adverse.

The comment is inaccurate.  The effects of discharge of sewage to the shoreline in Mexico has been modeled for the SEIS by Parsons Engineering Science.

There is no basis for assuming 25 to 75 mgd would be flushed through the Tijuana Estuary from the project.

Total pollutant loadings would be reduced under Alternative 2 relative to the No Action alternative.

Primary treated effluent has a lower BOD and total solids content than untreated raw sewage and, therefore, will have a lower odor D/T value than raw sewage.  However, these values have not been quantified.  Additionally, Alternative 2 will result in lower discharges to the river than the No Action alternative.  The SEIS discloses that treated effluent discharged to the river will not meet coliform standards.

Under Alternative 3, there would only be discharges to the river under high flow conditions in the years 2000 and 2001. The SEIS concludes that discharge of primary treated effluent would not be consistent with the federal and state water quality plans and policies.

Mexico has chosen these capacities, consistent with its existing facilities.  They would be temporary in the sense of their use for interim discharge considered in the SEIS.

The new pumping and conveyance facilities will not be operational until 1998; discharges of untreated sewage could occur before then.  A (Return to Sender( alternative was considered in the 1994 EIS for the IWTP and SBOO.  These alternatives result in discharge of untreated sewage to the shoreline in Mexico, which may adversely impact U.S. waters.  Mexico will not agree to use of the new pumping and conveyance system as a substitute for the SBOO.

(Mixed flows( refers to untreated sewage and San Antonio de los Buenos effluent discharged at the same point to the shoreline.  There is not a significant difference in the two flows relative to coliform concentrations, and this was considered in the shoreline discharge modeling.  The purpose of the IBWC Minutes and the project is to reduce impacts to U.S. waters, which shoreline discharges in Mexico could result in.

The commentor is incorrect; there would be discharges to the river prior to the completion of the new conveyance system if the IWTP is not operated.

See response #72.

However, IWTP effluent is preferable to untreated sewage if it is discharged to the shoreline in Mexico.

EPA/USIBWC cannot confirm the 0.06 percent probability figure.

The dilution stated is an order of magnitude estimate.

Impacts to marine environment and biota are presented in Section 4.5 of the SEIS, based upon modeling by Parsons Engineering Science.

See comment numbers 110-113.

Statement is based upon the results of the shoreline discharge modeling.  The chlorination is recent change in operations at the facility.  Data has not been made available as to the effectiveness of the chlorination at San Antonio de los Buenos.

Section 4.2 of the SEIS presents the shoreline discharge modeling results.

Mexico has the rights to the effluent from the IWTP per Minute No. 283.  As a discharge to a national water, the Mexican federal standards apply, which were appended to the SEIS.  Compliance with the appropriate laws is Mexico(s responsibility.

The 75 mgd flow rate is the reliable peaking factor for the IWTP, not a flow figure for IWTP interim operation.  Operating the IWTP at 25 mgd is included in Minute No. 283 and will be formalized in the Operations and Maintenance Minute.

This is discussed in Section 4.2 of the SEIS.

While a waiver from secondary treatment standards was authorized by congress in the enabling legislation for the project, no decision will be made until the Alternatives to Activated Sludge Supplemental EIS has been completed.

The alternatives considered in the SEIS and the environmental process was formalized in the settlement agreement agreed to by Surfriders (Attachment 2).

As discharges to the shoreline in Mexico may result in impacts to U.S. waters, there is no conflict in the purpose and goals.

Table 3.1-2 was developed as an example to show mass loads of various pollutants based on sampling results at a given flow rate.  The actual flow rate varies on a daily basis, but as indicated in the SEIS is expected to average 1.1 mgd in 1996 for the No Action alternative.  Mass loadings at flow rates other than 10 mgd can be determined simply by multiplying the indicated mass loads by the ratio of the flow rates.

Table 3.1-2 presents the results of samples taken in the Tijuana River; Table 3.1-3 presents the results of samples taken from the sewage stream at Pump Station One.

As part of the Interim Operation SEIS, one of the alternatives considered was the construction of a new pump station and conveyance pipeline for discharge in Mexico near the San Antonio de Los Buenos Treatment Plant in Mexico. In order to accurately assess the impacts of short-term discharge of unchlorinated primary treated effluent to the surf zone near the San Antonio plant, Parsons Engineering Science was requested by EPA/USIBWC to develop a computer model, later known as the Shore Discharge Model, to illustrate the migration of treated effluent discharged in Mexico and its possible impacts to the U.S. coastline.

The commentor is suggesting that there is no evidence of northerly moving currents which could transport the discharge near San Antonio de Los Buenos.  However, the existence of northerly currents along the surf zone is amply documented by the abundant bacterial samples taken over the years by different agencies, including sampling conducted by the IBWC, the City of San Diego, and San Diego County Department of Environmental Health.  The sampling demonstrates that at certain times of the year the bacterial plume discharged from the wastewater treatment plant near Punta Banderas diminishes in concentration as it travels northward.  In addition, current monitoring (metering) carried out for the TOES I and II studies also substantiates the presence of north-moving currents along the nearshore zone near the international border.  The 1988 TOES study found northerly currents trending upcoast 27 percent of the time, including the nearshore zone (Attachment 3).

Parsons Engineering Science contacted Dr. O(Reilly when wave data, not current data discussed above, obtained from the 1986 TOES study model was found not to be suitable as input to the Shore Discharge Model.  Parsons was concerned that the wave data available from the TOES study was not representative of the waves in the general area.  Parsons contacted Dr. O(Reilly to enlist his services in providing the required wave data to be used as input to the shoreline discharge model.  In his conversation with Parsons, Dr. O(Reilly did express some concerns about the quality of the bathymetric data available for the extreme southern portion of the area to be modeled, as well as possible limitations on the data available for the waves in the area.  Modifying the available bathymetry would have required a substantial amount of time in view of his current work at U.C. Berkeley, and his existing commitments with the state of California.

Parsons Engineering Science then contacted Pacific Weather Analysis to assist Parsons with this effort.  Pacific Weather Analysis was able to obtain the necessary data for two locations: one at the border between the U.S. and Mexico and a second approximately midway between the border and the discharge near Punta Banderas. Parsons informed Pacific Weather Analysis of Dr. O(Reilly(s concerns.  They concluded that because of the location of the stations, the known deficiencies in the bathymetry data base would not affect the predicted wave data because the modeled waves reaching the specific sites would propagate through the area with sufficient overall bathymetric information.  In total, Parsons obtained from Pacific Weather Analysis the follow information:

a)	Twenty years of hindcast wave records in southern California which classified sources of the wave and fetch characteristics;

b)	A Monte Carlo simulation developed by Noble Consultants in order to generate an annual wave climate by season given the probabilities of each wave pattern obtained; and

c)	A modification of directional wave spectra in deep water to select shallow water sites, utilizing the O(Reilly-Guza spectral wave refraction model from Nicholas Graham of Scripps.  (More information regarding the services provided by Pacific Weather Analysis is included as Attachment 4 to the Response to Comments.)

Finally, in a conversation with EPA on November 20, 1996, Dr. O(Reilly indicated that the O(Reilly-Guza spectral wave refraction model used did transform the wave heights and that Dr. Nicolas Graham at Scripps Institute of Oceanography was authorized to use the model.

In order to develop the Shore Discharge Model, typical wave and current conditions had to be developed only using available data in order to meet the schedule and practical constraints of the preparation of the SEIS.  The wave data available to match current data was not considered suitable and Parsons Engineering Science had to obtain wave data for a different time period.

However, not obtaining wave and current data from the same time period was not considered critical for the development of the Shore Discharge Model.  In general, wave and current characteristics are virtually unrelated and act independently of each other.  Furthermore, because of variability in the wave and current characteristics, there is an advantage in using a much larger (representing 20 years) data base which could result in a more representative sample.

The scope of the description of the SDM model included in the report was designed to inform the lay reader about the general approach of the model, the most important assumption and approximations, and the sources of the data used to drive the model.  In general, the key computational algorithms was found in the article by Press et al. (1992).  The model does contain the elements referred to by Dr. Jenkins except there is no nested grid, nor is there any reference to a nested grid in the report.  The equations used to qualify the relationship between the wave characteristics and the wave-induced advective transport model parameters were obtained by estimates from Inman et al. (1968).  Calculations of the wastewater transport and concentrations in this area were obtained from Jirka (1990) as the oceanic eddy diffusivities for the offshore region were estimated from characteristic(s cross-shore length scales of the wastefield and the work of Okubo (1974).  Wave-induced eddy diffusivities at the boundary of the surf zone were computed by Jirka (1990).

In order to test the Shore Discharge Model, the report provided a comparison between bacterial concentrations predicted by the model with various historical sampling events at several monitoring stations obtained by the IBWC, City of San Diego, and San Diego County Health Department at stations between the Punta Banderas discharge area and northern San Diego.

One factor considered in the Shore Discharge Model was the presence of rip currents as part of the overall ocean characterization.  The modeling of rip currents was significant since it illustrates the cross-shore transport between the surf zone and the off shore zone, as well as illustrates the movement between the transition zone and the surf zone.  Rip currents are observed to both migrate or remain stationary.  Rip currents are typically found between the surf zone and outer transition zones.  Their effects are computed in terms of volume fluxes.  The rip current speed was shown in Figure N-1 of the Ocean Modeling Report.  The speed was determined by the computational model contained in Inman et al. (1968) combined with information about the actual rip current area.

Furthermore, a fixed rip current length was selected for the model.  The length of each rip current was chosen to be comparable to the average rip current spacing as described in Inman et al. (1968) and the average wave conditions. Sensitivity studies carried out with the model indicated that variations in the rip current parameters had relatively small effects on the concentrations predicted far upcoast from the point of discharge.  This characteristic supports the use of fixed length rip currents.

As stated in the above comments, a Surf Discharge Model was developed to examine the impacts of a short-term ocean discharge of unchlorinated advanced primary treated effluent from a discharge near Punta Banderas.  A three-dimensional model as referenced by the commentor would not be capable of predicting accurately the coastal mixing and transport occurring in the surf, since the primary driving mechanism for this area is waves.  A second ocean modeling was also conducted by Parsons Engineering Science to examine the short-term discharge from the South Bay Ocean Outfall three miles in the Pacific Ocean.  For this modeling effort, a three-dimensional model was considered.

Dr. Ralph T. Cheng of the U.S.G.S. in Menlo Park and Dr. Vincenzo Casulli, of the University of Trento in Italy, the developer of the most recent three-dimensional model, as well as Dr. Craig Swanson of Applied Science Associates of Rhode Island, the developer of a Princeton model, were contacted about the modeling for the interim discharge of advanced primary effluent through the South Bay Ocean Outfall.  After several conference calls between Parsons Engineering Science and the individual three-dimensional modelors, it was concluded that with the time constraints of the SEIS and input data available, only qualitative results could be expected.

Parsons Engineering Science proceeded to model four ocean layers for the discharge, obtaining a discrete quasi-three-dimensional representation of the water quality in the area.

EPA and USIBWC have reviewed the Parsons Engineering Science Modeling study, have received independent agency review of the study, and have consulted with some of the principals cited in the Surfrider(s letter of comment.  EPA and USIBWC believe that the study is technically sound and appropriate as a model to approximate the effects of ocean discharge through SBOO and shoreline discharge in Mexico for the Interim Operations SEIS.  EPA and USIBWC find that the objections raised are based upon misinformation about the Parsons Engineering Science study and the federal agencies do not agree with the comments by Surfriders Foundation.

See response #131.

Table 4.1-1 was not based upon the Parsons Engineering Science modeling study; it was based upon estimates from Malcolm Pirnie Engineers, as cited in the table.

Public Hearing

A noticed public hearing was held at Southwest High School on October 7, 1996 for which a transcript of questions, comments, and responses by the federal agencies is provided. As portions of the hearing were conducted as a question and answer format with the sponsoring federal agencies, and that any substantive issues raised were responded to at the hearing, no additional specific responses to the transcript are provided.  Most speakers at the public hearing also provided written versions which are responded to in the letters of comment.

Errata

The following changes to the Draft SEIS are made for the Final SEIS:

Section 1.3.2.2, page xiv, paragraph 5, should be changed to read:

The outfall is designed to carry an maximum average daily flow of 174 mgd . . . .

Section 1.4, page xv, paragraph 1 should be revised as follows:

EPA and USIBWC are considering operating the IWTP as an advanced primary treatment works prior to the completion of the ocean outfall and the secondary treatment process trains to minimize the risk of discharges of raw sewage or treated effluent into the Tijuana River.

Figure 1-5	The scale shown is in miles, not feet.

Section 2.2.3, page 81, paragraph 3; Section 4.1.4.1 page 210, Paragraph 2; Section 4.2.5, page 231, paragraph 2; Section 4.5.3, page 275, paragraph 2; modify sentence as follows:

There could be episodic discharges of up to 0.7 mgd (31 lps) and 2.0 mgd (88 lps) on seasonal high flow days in the years 2000 and 2001 . . . .

Section 1.1.1.5.page 12, paragraph 1; add as indicated:

Manufacturing industries of Tijuana include televisions, computers, metal products . . . .

Section 1.4.10.1, page xxii, paragraph 2; Section 3.2.1.4, page 140, Bacterial Contamination, paragraph 2; Section 3.7.2, page 182, paragraph 5; Section 3.7.3.1, page 184, paragraph 1; Section 5.1.1, page 305, paragraph 1; Section 5.4.1, page 306, paragraph 1:

County Department of Health Services should be changed to County Department of Environmental Health.

Section 2.2.3.1, page 82, paragraph 1 should be revised as follows:

The discharge of treated effluent to the Tijuana River would not occur until the year 20001, when 0.7 2.0 mgd (31 88 lps) would be discharged during seasonal high flow days. If the SBOO becomes operational by June 1998-1999 as scheduled, all discharges to the river of untreated sewage or treated effluent could be avoided.

Attachments

1.	Letter from Commissioner J. Arturo Herrera Solis, Commissioner of the Mexican Section of the IBWC to John M. Bernal, Commissioner, U.S. Section of the IBWC.  This letter recites basic issues with respect to sewage facilities in Mexico and Mexico(s best disposition to continue to accept flows through Pump Station One until the SBOO is operational.

2.	Settlement Agreement between the EPA and USIBWC and the San Diego Chapter of the Sierra Club, Chaparral Green and Surfrider Foundation, dated July 19, 1995.  This Settlement Agreement [Case No. 94-920-J(RBB), U.S. District Court Southern District of California] was concluded after the 1994 Final EIS and Record of Decision was signed for the project.  It outlines the agreed to process for preparing additional NEPA documentation for the project and the scope of the documents.

3.	Memorandum from Terry Hendricks (11/25/96) with respect to current meter information collected during the TOES study indicating northerly transport.

4.	Letter from Pacific Weather Analysis, signed by R. Rea Strange to Dr. Luciano Meiorin of Parsons Engineering Science, dated November 7, 1996; clarifying data sources and wave records used as input for the shoreline discharge model.