## 25F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 021
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6619.8527
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 151.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 375.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 265.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1380.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 375.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2010.69 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1031 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1413 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1267.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 875.78 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1380.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 265.26 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1175.7 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1267.09 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2549.78 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2549.78 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
525 | 775 | 2010.69 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2123.02 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 140 | 1660.38 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1503.23 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 2123.02 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 151.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1413 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1031 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2306.84 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1175.7 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1503.23 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1660.38 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 875.78 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2306.84 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 021
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6296.4973
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 522.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 792.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 621.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1677.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 792.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2190.83 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1428.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1619.35 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1560.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1223.81 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1677.15 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 621.95 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1734.52 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1560.07 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2761.81 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2761.81 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
525 | 775 | 2190.83 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2310.76 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 140 | 2926.42 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1791.32 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 2310.76 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 522.68 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1619.35 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1428.49 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2564.14 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1734.52 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1791.32 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2926.42 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1223.81 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2564.14 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 021
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6017.738
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 269.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 492.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 388.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1422.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 492.74 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2438.63 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1188.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1889.78 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1312.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1345.5 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1422.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 388.25 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2945.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1312.57 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3029.47 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3029.47 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
525 | 775 | 2438.63 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2405.09 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 140 | 3030.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1881.9 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 2405.09 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 269.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1889.78 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1188.7 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2723.75 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2945.61 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 1881.9 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3030.71 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1345.5 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2723.75 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 021
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4957.1733
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1626.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1877.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1753.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2695.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1877.79 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2603.17 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2471.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2032.11 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2582.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1530.12 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2695.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1753.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3236.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2582.1 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3213.91 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3213.91 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 2603.17 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2621.15 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2826.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2125.14 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2621.15 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1626.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2032.11 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2471.81 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2603.37 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3236.85 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2125.14 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2826.21 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1530.12 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2603.37 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 021
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4611.6947
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1895.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2136.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2022.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2115.11 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
100 | 775 | 2136.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1799.02 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2720.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1235.91 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2735.98 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 719.1 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2115.11 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2022.76 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3044.35 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 2735.98 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
525 | 460 | 2410.81 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2410.81 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 1799.02 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 1835.19 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2469.3 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 1304.13 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 1835.19 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1895.9 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1235.91 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2720.77 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 1948.18 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3044.35 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1400 | 460 | 1304.13 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2469.3 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 719.1 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1948.18 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2
G0 | 151.63 | 522.68 | 269.85 | 1626.75 | 1895.9
G1 | 265.26 | 621.95 | 388.25 | 1753.86 | 2022.76 | Season/Year: | WINTER 2009
G2 | 375.94 | 792.43 | 492.74 | 1877.79 | 2136.36 | Direction: | North-to-South (NS)
G3 | 1031 | 1428.49 | 1188.7 | 2471.81 | 2720.77 | Case Loads: | Heavy Loads
G4 | 1267.09 | 1560.07 | 1312.57 | 2582.1 | 2735.98 | Outage: | 021
G5 | 1380.69 | 1677.15 | 1422.63 | 2695.88 | 2115.11 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1175.7 | 1734.52 | 2945.61 | 3236.85 | 3044.35 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2549.78 | 2761.81 | 3029.47 | 3213.91 | 2410.81 | Study Person: | JGO7470
G8 | 2010.69 | 2190.83 | 2438.63 | 2603.17 | 1799.02 | Source: | 021WINTER09v2NSH
G9 | 1660.38 | 2926.42 | 3030.71 | 2826.21 | 2469.3
G10 | 2123.02 | 2310.76 | 2405.09 | 2621.15 | 1835.19
G11 | 1413 | 1619.35 | 1889.78 | 2032.11 | 1235.91
G12 | 2306.84 | 2564.14 | 2723.75 | 2603.37 | 1948.18
G13 | 1503.23 | 1791.32 | 1881.9 | 2125.14 | 1304.13
G14 | 875.78 | 1223.81 | 1345.5 | 1530.12 | 719.1
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 021 | Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6619.8527 | 151.63 | 265.26 | 375.94 | 1031 | 1267.09 | 1380.69 | 1175.7 | 2549.78 | 2010.69 | 1660.38 | 2123.02 | 1413 | 2306.84 | 1503.23 | 875.78
35F | 6296.4973 | 522.68 | 621.95 | 792.43 | 1428.49 | 1560.07 | 1677.15 | 1734.52 | 2761.81 | 2190.83 | 2926.42 | 2310.76 | 1619.35 | 2564.14 | 1791.32 | 1223.81
45F | 6017.738 | 269.85 | 388.25 | 492.74 | 1188.7 | 1312.57 | 1422.63 | 2945.61 | 3029.47 | 2438.63 | 3030.71 | 2405.09 | 1889.78 | 2723.75 | 1881.9 | 1345.5
60F | 4957.1733 | 1626.75 | 1753.86 | 1877.79 | 2471.81 | 2582.1 | 2695.88 | 3236.85 | 3213.91 | 2603.17 | 2826.21 | 2621.15 | 2032.11 | 2603.37 | 2125.14 | 1530.12
70F | 4611.6947 | 1895.9 | 2022.76 | 2136.36 | 2720.77 | 2735.98 | 2115.11 | 3044.35 | 2410.81 | 1799.02 | 2469.3 | 1835.19 | 1235.91 | 1948.18 | 1304.13 | 719.1

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 150.38 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 472.88 | 472.82 | 6651.27 | 151.63 | -252.27 | FULL
G1 | 264.04 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 473.19 | 473.24 | 6581.24 | 265.26 | -153.23 | FULL
G2 | 374.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 473.49 | 473.42 | 6592.05 | 375.94 | -46.29 | FULL
G3 | 1032.14 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 808.78 | 808.74 | 6644.73 | 1031 | 319.2 | FULL
G4 | 1268.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 484.84 | 484.88 | 6577.85 | 1267.09 | 489.4 | FULL
G5 | 1384.71 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 485.18 | 484.98 | 6592.05 | 1380.69 | 590.68 | FULL
G6 | 1176.35 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 807.03 | 807.01 | 6648.2 | 1175.7 | 520.4 | FULL
G7 | 2559.58 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.91 | 458.94 | 6605.87 | 2549.78 | 1326.81 | FULL
G8 | 2017.45 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.18 | 459.67 | 6606.27 | 2010.69 | 1062.68 | FULL
G9 | 1663.18 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 805.19 | 805.26 | 6666.09 | 1660.38 | 1000.69 | FULL
G10 | 2129.29 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.58 | 459.62 | 6611.05 | 2123.02 | 1293.55 | FULL
G11 | 1414.37 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.15 | 459.13 | 6606.99 | 1413 | 933.24 | FULL
G12 | 2314.93 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.64 | 459.68 | 6698.69 | 2306.84 | 1511.25 | FULL
G13 | 1507.2 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.88 | 458.87 | 6607.63 | 1503.23 | 1106.63 | FULL
G14 | 876.39 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.87 | 458.91 | 6607.81 | 875.78 | 786.36 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 521.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 468.72 | 468.56 | 6315.51 | 522.68 | 10.83 | FULL
G1 | 621.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 468.85 | 468.63 | 6246.27 | 621.95 | 101.46 | FULL
G2 | 792.31 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 470.6 | 470.45 | 6258.62 | 792.43 | 244.05 | FULL
G3 | 1432.2 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 476.26 | 476.2 | 6316.03 | 1428.49 | 587.73 | FULL
G4 | 1565.08 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 477.22 | 476.99 | 6249.17 | 1560.07 | 698.24 | FULL
G5 | 1681.5 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 477.6 | 477.43 | 6264.69 | 1677.15 | 799.94 | FULL
G6 | 1741.4 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 807.7 | 807.65 | 6328.2 | 1734.52 | 882.91 | FULL
G7 | 2775.05 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.51 | 458.46 | 6283.79 | 2761.81 | 1486.04 | FULL
G8 | 2199.02 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.16 | 459.09 | 6281.04 | 2190.83 | 1210.35 | FULL
G9 | 2940.2 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 807.01 | 807.02 | 6377.69 | 2926.42 | 1738.78 | FULL
G10 | 2319.12 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.03 | 459.05 | 6287.32 | 2310.76 | 1440.53 | FULL
G11 | 1624.98 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | 2.98 | 458.67 | 458.65 | 6283.46 | 1619.35 | 1088.92 | FULL
G12 | 2573.54 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.86 | 459.9 | 6381.72 | 2564.14 | 1679.92 | FULL
G13 | 1796.99 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.89 | 458.96 | 6286.79 | 1791.32 | 1304.79 | FULL
G14 | 1224.29 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.74 | 459.82 | 6287.16 | 1223.81 | 1022.37 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 267.96 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 435.36 | 435.25 | 6031.76 | 269.85 | -113.74 | FULL
G1 | 385.97 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 435.67 | 435.55 | 5961.7 | 388.25 | -9.22 | FULL
G2 | 494.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 435.76 | 435.63 | 5974.12 | 492.74 | 84.77 | FULL
G3 | 1191.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.29 | 442.24 | 6029.58 | 1188.7 | 474.5 | FULL
G4 | 1312.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.51 | 442.69 | 5962.54 | 1312.57 | 580.84 | FULL
G5 | 1426.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.87 | 442.99 | 5977.88 | 1422.63 | 677.52 | FULL
G6 | 2958.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 448.5 | 448.36 | 6072.41 | 2945.61 | 1575.25 | FULL
G7 | 3044.24 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.31 | 459.38 | 6010.05 | 3029.47 | 1655.41 | FULL
G8 | 2446.91 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | 2.98 | 461.88 | 458.85 | 6005.26 | 2438.63 | 1362.33 | FULL
G9 | 3045.61 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -492.53 | -492.12 | 6100.8 | 3030.71 | 1829.94 | FULL
G10 | 2413.13 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.95 | 458.92 | 6009.22 | 2405.09 | 1516.02 | FULL
G11 | 1894.37 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 460.03 | 460.06 | 6008.01 | 1889.78 | 1261.28 | FULL
G12 | 2734.17 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.87 | 459.9 | 6106.21 | 2723.75 | 1803.43 | FULL
G13 | 1887.08 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.74 | 458.73 | 6008.58 | 1881.9 | 1379.05 | FULL
G14 | 1347.39 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.66 | 459.74 | 6007.95 | 1345.5 | 1111.76 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1631.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.43 | 442.53 | 4956.1 | 1626.75 | 796.82 | FULL
G1 | 1759.61 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.97 | 443.1 | 4892.11 | 1753.86 | 903.98 | FULL
G2 | 1884.49 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.83 | 443.94 | 4909.62 | 1877.79 | 1008.74 | FULL
G3 | 2483.13 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 446.86 | 446.97 | 4976.97 | 2471.81 | 1331.49 | FULL
G4 | 2592.62 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.27 | 447.19 | 4914.91 | 2582.1 | 1427.57 | FULL
G5 | 2707.75 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.39 | 447.64 | 4934.9 | 2695.88 | 1524.14 | FULL
G6 | 3253.97 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -471.3 | -471.67 | 5018.17 | 3236.85 | 1871.56 | FULL
G7 | 3230.61 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -194.87 | -194.83 | 4950.61 | 3213.91 | 1871.88 | FULL
G8 | 2613.99 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -195.17 | -195.15 | 4942.03 | 2603.17 | 1575.55 | FULL
G9 | 2836.68 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -477.86 | -477.13 | 5025.76 | 2826.21 | 1849 | FULL
G10 | 2631.01 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -196.81 | -196.81 | 4950.87 | 2621.15 | 1773.36 | FULL
G11 | 2038.27 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -195.26 | -195.26 | 4945.92 | 2032.11 | 1462.29 | FULL
G12 | 2613.75 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -12.82 | -458.2 | -458.17 | 5038.91 | 2603.37 | 1876.47 | FULL
G13 | 2132.82 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -193.16 | -193.15 | 4952.25 | 2125.14 | 1641.82 | FULL
G14 | 1534.02 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -194.87 | -194.94 | 4948.47 | 1530.12 | 1350.26 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1900.59 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.92 | 444.01 | 4627.31 | 1895.9 | 986.62 | FULL
G1 | 2031.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.88 | 444.75 | 4563.89 | 2022.76 | 1080.73 | FULL
G2 | 2143.6 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.4 | 445.47 | 4583.17 | 2136.36 | 1178.92 | FULL
G3 | 2732.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.49 | 447.54 | 4651.79 | 2720.77 | 1501.54 | FULL
G4 | 2747.29 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.36 | -176.37 | 4587.88 | 2735.98 | 1546.03 | FULL
G5 | 2122.88 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -175.88 | -175.91 | 4585.93 | 2115.11 | 1230.23 | FULL
G6 | 3058.63 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -175.82 | -175.8 | 4675.49 | 3044.35 | 1793.35 | FULL
G7 | 2419.29 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.95 | -176.98 | 4586.69 | 2410.81 | 1482.18 | FULL
G8 | 1804.79 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.33 | -176.33 | 4585.9 | 1799.02 | 1171 | FULL
G9 | 2479.28 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.23 | -176.22 | 4677.32 | 2469.3 | 1680.58 | FULL
G10 | 1839.47 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.92 | -176.98 | 4590.5 | 1835.19 | 1366.39 | FULL
G11 | 1237.35 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -175.78 | -175.81 | 4591.17 | 1235.91 | 1072.47 | FULL
G12 | 1954.99 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.15 | -176.13 | 4678.95 | 1948.18 | 1544.48 | FULL
G13 | 1306.08 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.43 | -176.5 | 4593.41 | 1304.13 | 1216.11 | FULL
G14 | 719.26 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.09 | -176.07 | 4596.02 | 719.1 | 937.28 | FULL
021WINTER09v2NSH