## 25F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 022
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6620.3047
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 151.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 375.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 265.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1380.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 375.87 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2015.94 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1029.52 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1412.42 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1267.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 875.33 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1380.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 265.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1177.93 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1267.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2549.28 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2549.28 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
525 | 775 | 2015.94 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2122.53 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 140 | 1659.18 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1502.69 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 2122.53 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 151.55 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1412.42 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1029.52 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2306.16 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1177.93 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1502.69 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1659.18 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 875.33 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2306.16 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 35F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 022
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6297.0173
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 522.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 792.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 620.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1676.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 792.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2198.3 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1428.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1618.84 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1559.98 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1220.73 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1676.02 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 620.56 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 1732.84 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1559.98 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 2751.19 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2751.19 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
525 | 775 | 2198.3 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2310.24 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 140 | 2923.13 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1801.92 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 2310.24 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 522.62 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1618.84 | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1428.43 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2563.58 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1732.84 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1801.92 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2923.13 | BFR: Sno-King 230kV North Bus | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1220.73 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2563.58 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 022
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6018.21
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 269.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 492.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 388.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 1422.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 492.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2441.82 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 140 | 1188.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1889.36 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 460 | 1312.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1345.92 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
260 | 775 | 1422.6 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 388.19 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2942.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 1312.51 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3028.91 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3028.91 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
525 | 775 | 2441.82 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2404.57 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 140 | 3030.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1881.39 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
1000 | 460 | 2404.57 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 269.78 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1889.36 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 1188.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2723.13 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2942.92 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 460 | 1881.39 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3030.68 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1345.92 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2723.13 | BFR: Sammamish 230kV East Bus | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 022
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4957.6113
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1626.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 1877.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 1753.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2695.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 775 | 1877.86 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 2602.56 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2471.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 2031.48 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2582.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 1529.54 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2695.82 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G2 | 100 | 460 | 1753.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3236.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2582.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 460 | 3213.3 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3213.3 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 2602.56 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2620.51 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2826.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 2124.01 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 2620.51 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1626.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 2031.48 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2471.75 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 2603.35 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 3236.88 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 2124.01 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2826.2 | N-2: Monroe - Custer #1&2 500kV | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1529.54 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2603.35 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Heavy Loads
Outage: |  | 022
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4612.1253
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1895.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2136.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2022.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G6 | 260 | 775 | 2114.5 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
100 | 775 | 2136.3 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G9 | 525 | 775 | 1798.42 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2720.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G12 | 1000 | 775 | 1235.29 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 460 | 2735.35 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G15 | 1400 | 775 | 718.49 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
260 | 775 | 2114.5 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G2 | 100 | 465 | 2022.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 3043.74 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 2735.35 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
525 | 460 | 2410.19 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2410.19 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 1798.42 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 1834.58 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 140 | 2468.68 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 1303.51 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1000 | 460 | 1834.58 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 1895.85 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1235.29 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2720.69 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 140 | 1947.55 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3043.74 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1400 | 460 | 1303.51 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2468.68 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
1400 | 775 | 718.49 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1947.55 | N-2: Maple Valley - Sno-King #1&2 230kV | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
G0 | 151.55 | 522.62 | 269.78 | 1626.69 | 1895.85
G1 | 265.19 | 620.56 | 388.19 | 1753.83 | 2022.73 | Season/Year: | WINTER 2009
G2 | 375.87 | 792.36 | 492.69 | 1877.86 | 2136.3 | Direction: | North-to-South (NS)
G3 | 1029.52 | 1428.43 | 1188.63 | 2471.75 | 2720.69 | Case Loads: | Heavy Loads
G4 | 1267.05 | 1559.98 | 1312.51 | 2582.04 | 2735.35 | Outage: | 022
G5 | 1380.63 | 1676.02 | 1422.6 | 2695.82 | 2114.5 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 1177.93 | 1732.84 | 2942.92 | 3236.88 | 3043.74 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2549.28 | 2751.19 | 3028.91 | 3213.3 | 2410.19 | Study Person: | JGO7470
G8 | 2015.94 | 2198.3 | 2441.82 | 2602.56 | 1798.42 | Source: | 022WINTER09v2NSH
G9 | 1659.18 | 2923.13 | 3030.68 | 2826.2 | 2468.68
G10 | 2122.53 | 2310.24 | 2404.57 | 2620.51 | 1834.58
G11 | 1412.42 | 1618.84 | 1889.36 | 2031.48 | 1235.29
G12 | 2306.16 | 2563.58 | 2723.13 | 2603.35 | 1947.55
G13 | 1502.69 | 1801.92 | 1881.39 | 2124.01 | 1303.51
G14 | 875.33 | 1220.73 | 1345.92 | 1529.54 | 718.49
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Heavy Loads |  |  | 022 | Echo Lake-Maple Valley #1&2 500kV Line ***Includes Maple Valley 500/230kV Transformer Bank #2 (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6620.3047 | 151.55 | 265.19 | 375.87 | 1029.52 | 1267.05 | 1380.63 | 1177.93 | 2549.28 | 2015.94 | 1659.18 | 2122.53 | 1412.42 | 2306.16 | 1502.69 | 875.33
35F | 6297.0173 | 522.62 | 620.56 | 792.36 | 1428.43 | 1559.98 | 1676.02 | 1732.84 | 2751.19 | 2198.3 | 2923.13 | 2310.24 | 1618.84 | 2563.58 | 1801.92 | 1220.73
45F | 6018.21 | 269.78 | 388.19 | 492.69 | 1188.63 | 1312.51 | 1422.6 | 2942.92 | 3028.91 | 2441.82 | 3030.68 | 2404.57 | 1889.36 | 2723.13 | 1881.39 | 1345.92
60F | 4957.6113 | 1626.69 | 1753.83 | 1877.86 | 2471.75 | 2582.04 | 2695.82 | 3236.88 | 3213.3 | 2602.56 | 2826.2 | 2620.51 | 2031.48 | 2603.35 | 2124.01 | 1529.54
70F | 4612.1253 | 1895.85 | 2022.73 | 2136.3 | 2720.69 | 2735.35 | 2114.5 | 3043.74 | 2410.19 | 1798.42 | 2468.68 | 1834.58 | 1235.29 | 1947.55 | 1303.51 | 718.49

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 150.3 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 472.88 | 472.82 | 6651.73 | 151.55 | -252.31 | FULL
G1 | 263.96 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 473.19 | 473.24 | 6581.69 | 265.19 | -153.27 | FULL
G2 | 374.8 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 473.49 | 473.42 | 6592.5 | 375.87 | -46.34 | FULL
G3 | 1030.64 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 808.77 | 808.73 | 6645.18 | 1029.52 | 318.36 | FULL
G4 | 1268.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 484.84 | 484.88 | 6578.3 | 1267.05 | 489.37 | FULL
G5 | 1384.64 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 485.18 | 484.98 | 6592.5 | 1380.63 | 590.65 | FULL
G6 | 1178.84 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 807.14 | 807.02 | 6648.64 | 1177.93 | 521.67 | FULL
G7 | 2559.05 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.91 | 458.94 | 6606.31 | 2549.28 | 1326.54 | FULL
G8 | 2021.76 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.66 | 459.53 | 6606.86 | 2015.94 | 1065.62 | FULL
G9 | 1661.88 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 805.18 | 805.27 | 6666.51 | 1659.18 | 1000.02 | FULL
G10 | 2128.79 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.58 | 459.62 | 6611.48 | 2122.53 | 1293.28 | FULL
G11 | 1413.88 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.15 | 459.13 | 6607.43 | 1412.42 | 932.91 | FULL
G12 | 2314.38 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.65 | 459.68 | 6699.12 | 2306.16 | 1510.88 | FULL
G13 | 1506.7 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.88 | 458.87 | 6608.07 | 1502.69 | 1106.33 | FULL
G14 | 875.94 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.87 | 458.91 | 6608.25 | 875.33 | 786.1 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 521.7 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 468.72 | 468.56 | 6315.96 | 522.62 | 10.79 | FULL
G1 | 621.41 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 468.85 | 468.63 | 6246.71 | 620.56 | 100.65 | FULL
G2 | 792.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 470.6 | 470.45 | 6259.08 | 792.36 | 244.01 | FULL
G3 | 1432.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 476.26 | 476.2 | 6316.48 | 1428.43 | 587.69 | FULL
G4 | 1565.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 477.22 | 476.99 | 6249.62 | 1559.98 | 698.19 | FULL
G5 | 1681.77 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 477.63 | 477.43 | 6265.12 | 1676.02 | 799.28 | FULL
G6 | 1739.75 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 807.69 | 807.65 | 6328.62 | 1732.84 | 881.97 | FULL
G7 | 2763.31 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.42 | 458.36 | 6283.95 | 2751.19 | 1480.15 | FULL
G8 | 2206.05 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.18 | 459.19 | 6281.92 | 2198.3 | 1214.29 | FULL
G9 | 2935.47 | Branch SNOK S2 (41006) TO SNOK S3 (41008) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV North Bus | 4.02 | 806.91 | 806.94 | 6378.03 | 2923.13 | 1737.03 | FULL
G10 | 2318.59 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.03 | 459.05 | 6287.75 | 2310.24 | 1440.25 | FULL
G11 | 1624.48 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus & Klahanie 230kV Bus | 2.98 | 458.67 | 458.65 | 6283.89 | 1618.84 | 1088.64 | FULL
G12 | 2572.98 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.86 | 459.9 | 6382.15 | 2563.58 | 1679.62 | FULL
G13 | 1806.23 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.27 | 459.28 | 6288.43 | 1801.92 | 1314.37 | FULL
G14 | 1223.82 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.73 | 459.82 | 6287.55 | 1220.73 | 1020.62 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 267.89 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 435.36 | 435.25 | 6032.21 | 269.78 | -113.78 | FULL
G1 | 385.91 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 435.67 | 435.55 | 5962.15 | 388.19 | -9.26 | FULL
G2 | 494.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 435.76 | 435.63 | 5974.57 | 492.69 | 84.74 | FULL
G3 | 1191.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.29 | 442.24 | 6030.03 | 1188.63 | 474.46 | FULL
G4 | 1312.69 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.51 | 442.69 | 5962.99 | 1312.51 | 580.81 | FULL
G5 | 1426.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.87 | 442.99 | 5978.32 | 1422.6 | 677.5 | FULL
G6 | 2955.72 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.44 | 447.54 | 6073.18 | 2942.92 | 1573.49 | FULL
G7 | 3043.67 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.31 | 459.38 | 6010.48 | 3028.91 | 1655.1 | FULL
G8 | 2449.54 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 462.48 | 458.86 | 6005.83 | 2441.82 | 1364.04 | FULL
G9 | 3045.58 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -492.52 | -492.12 | 6101.24 | 3030.68 | 1829.94 | FULL
G10 | 2412.61 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.95 | 458.92 | 6009.65 | 2404.57 | 1515.74 | FULL
G11 | 1893.88 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 460.03 | 460.05 | 6008.45 | 1889.36 | 1261.05 | FULL
G12 | 2733.62 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.87 | 459.9 | 6106.63 | 2723.13 | 1803.1 | FULL
G13 | 1886.57 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 458.74 | 458.73 | 6009.01 | 1881.39 | 1378.77 | FULL
G14 | 1346.92 | Branch SAMMAMSH (42300) TO SAMMAMSH (42301) CKT 2 [230.00 - 115.00 kV] | BFR: Sammamish 230kV East Bus | 2.98 | 459.66 | 459.74 | 6008.41 | 1345.92 | 1112.01 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1631.11 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.43 | 442.53 | 4956.55 | 1626.69 | 796.79 | FULL
G1 | 1759.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 442.97 | 443.1 | 4892.56 | 1753.83 | 903.97 | FULL
G2 | 1884.56 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.86 | 443.94 | 4910.07 | 1877.86 | 1008.78 | FULL
G3 | 2483.07 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 446.86 | 446.97 | 4977.41 | 2471.75 | 1331.46 | FULL
G4 | 2592.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.27 | 447.18 | 4915.36 | 2582.04 | 1427.54 | FULL
G5 | 2707.7 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.39 | 447.64 | 4935.35 | 2695.82 | 1524.1 | FULL
G6 | 3254 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.94 | -471.31 | -471.67 | 5018.63 | 3236.88 | 1871.58 | FULL
G7 | 3229.98 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -194.87 | -194.84 | 4951.03 | 3213.3 | 1871.56 | FULL
G8 | 2613.37 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -195.17 | -195.15 | 4942.45 | 2602.56 | 1575.22 | FULL
G9 | 2836.67 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | N-2: Monroe - Custer #1&2 500kV | -38.69 | -477.86 | -477.13 | 5026.21 | 2826.2 | 1848.99 | FULL
G10 | 2630.37 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -196.81 | -196.81 | 4951.29 | 2620.51 | 1773.02 | FULL
G11 | 2037.65 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -195.26 | -195.26 | 4946.34 | 2031.48 | 1461.95 | FULL
G12 | 2613.73 | Branch MURRAY (40767) TO SEDRO NT (42103) CKT 1 [230.00 - 230.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | -12.82 | -458.2 | -458.17 | 5039.36 | 2603.35 | 1876.46 | FULL
G13 | 2131.59 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -193.15 | -193.15 | 4952.66 | 2124.01 | 1641.21 | FULL
G14 | 1533.41 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -194.87 | -194.94 | 4948.9 | 1529.54 | 1349.95 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1900.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 443.92 | 444.01 | 4627.75 | 1895.85 | 986.59 | FULL
G1 | 2030.96 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 444.88 | 444.75 | 4564.34 | 2022.73 | 1080.71 | FULL
G2 | 2143.55 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 445.4 | 445.47 | 4583.62 | 2136.3 | 1178.89 | FULL
G3 | 2732.19 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 8.57 | 447.49 | 447.54 | 4652.23 | 2720.69 | 1501.49 | FULL
G4 | 2746.66 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.36 | -176.37 | 4588.3 | 2735.35 | 1545.68 | FULL
G5 | 2122.24 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -175.88 | -175.91 | 4586.36 | 2114.5 | 1229.89 | FULL
G6 | 3058 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -175.82 | -175.8 | 4675.91 | 3043.74 | 1793.02 | FULL
G7 | 2418.66 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.95 | -176.98 | 4587.11 | 2410.19 | 1481.84 | FULL
G8 | 1804.17 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.33 | -176.33 | 4586.33 | 1798.42 | 1170.67 | FULL
G9 | 2478.64 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.23 | -176.22 | 4677.74 | 2468.68 | 1680.24 | FULL
G10 | 1838.84 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.92 | -176.98 | 4590.92 | 1834.58 | 1366.06 | FULL
G11 | 1236.72 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -175.78 | -175.81 | 4591.61 | 1235.29 | 1072.13 | FULL
G12 | 1954.35 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.15 | -176.13 | 4679.37 | 1947.55 | 1544.14 | FULL
G13 | 1305.45 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.43 | -176.51 | 4593.84 | 1303.51 | 1215.77 | FULL
G14 | 718.63 | Branch BROAD ST (46409) TO UNIVERSY (46453) CKT 1 [115.00 - 115.00 kV] | N-2: Maple Valley - Sno-King #1&2 230kV | -2.92 | -176.09 | -176.07 | 4596.45 | 718.49 | 936.94 | FULL
022WINTER09v2NSH