## 25F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 012
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6665.3967
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -2367.55 | BFR: Bothell 230kV Bus Sect #7 & Sed-Both-HRanch 230kV | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2423.39 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 863.19 | BFR: Sno-King 230kV South Bus | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2606.12 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2423.39 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2868.86 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
260 | 140 | -691.3 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3427.09 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1191.56 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3626.45 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2606.12 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 863.19 | BFR: Sno-King 230kV South Bus | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV]
525 | 140 | -28.45 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1191.56 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1986.75 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1986.75 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2868.86 | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2896.01 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 967.58 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3459.36 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 2896.01 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -2367.55 | BFR: Bothell 230kV Bus Sect #7 & Sed-Both-HRanch 230kV | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 3427.09 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -691.3 | BFR: Bothell 230kV Bus Sect #7 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 2064.71 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -28.45 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3459.36 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 967.58 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3626.45 | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 2064.71 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 012
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6338.384
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -596.81 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2562.69 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1233.59 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2745.16 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2562.69 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 2997.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
260 | 140 | -210.46 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3500.01 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 1908.77 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3534.81 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
260 | 775 | 2745.16 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1233.59 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 424.48 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1908.77 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2554.43 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2554.43 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2997.15 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3124.96 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1680.15 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3539.69 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
1000 | 460 | 3124.96 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -596.81 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3500.01 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | -210.46 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 2576.32 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 424.48 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3539.69 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G10 | 1000 | 140 | 1680.15 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3534.81 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G13 | 1400 | 140 | 2576.32 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 012
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6053.7927
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -403.4 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2573.53 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 1779.46 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2755.72 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2573.53 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 3046.63 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 84.9 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3404.6 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2208.68 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 3148.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2755.72 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 1779.46 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 711.59 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2208.68 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2649.59 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2649.59 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 3046.63 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 3138.62 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1736.43 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 3242.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3138.62 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -403.4 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3404.6 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 84.9 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 2916.38 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 711.59 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 3242.47 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1736.43 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 3148.05 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2916.38 | 3TM: Monroe-Echo LK-SnoK 500kV | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 012
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4973.4413
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1319.64 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2793.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2766.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2891.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2793.64 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2828.78 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 1545.43 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3147.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2846.78 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1934.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2891.84 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2766.49 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2236.21 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2846.78 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2808.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2808.92 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2828.78 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3107.95 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3302.4 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 2056.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3107.95 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1319.64 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3147.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 1545.43 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 2181.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2236.21 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 2056.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3302.4 | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV]
1400 | 775 | 1934.04 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 2181.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 012
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4634.6087
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 1850.74 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2417.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2402.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2766.76 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2417.61 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2744.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 2215.56 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 3066.6 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 460 | 2517.77 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 1716.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2766.76 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2402.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2705.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 2517.77 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2725.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 2725.48 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 2744.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 3037.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 140 | 3014.6 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G14 | 1400 | 460 | 1827.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 3037.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G1 | 100 | 140 | 1850.74 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 3066.6 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G4 | 260 | 140 | 2215.56 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1907.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2705.16 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 1827.13 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 3014.6 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 775 | 1716.63 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1907.12 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
G0 | -2367.55 | -596.81 | -403.4 | 1319.64 | 1850.74
G1 | 863.19 | 1233.59 | 1779.46 | 2766.49 | 2402.33 | Season/Year: | WINTER 2009
G2 | 2423.39 | 2562.69 | 2573.53 | 2793.64 | 2417.61 | Direction: | South-to-North (SN)
G3 | -691.3 | -210.46 | 84.9 | 1545.43 | 2215.56 | Case Loads: | Heavy Loads
G4 | 1191.56 | 1908.77 | 2208.68 | 2846.78 | 2517.77 | Outage: | 012
G5 | 2606.12 | 2745.16 | 2755.72 | 2891.84 | 2766.76 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | -28.45 | 424.48 | 711.59 | 2236.21 | 2705.16 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 1986.75 | 2554.43 | 2649.59 | 2808.92 | 2725.48 | Study Person: | FRP9899
G8 | 2868.86 | 2997.15 | 3046.63 | 2828.78 | 2744.66 | Source: | 012WINTER09v1SNH
G9 | 967.58 | 1680.15 | 1736.43 | 3302.4 | 3014.6
G10 | 2896.01 | 3124.96 | 3138.62 | 3107.95 | 3037.11
G11 | 3427.09 | 3500.01 | 3404.6 | 3147.61 | 3066.6
G12 | 2064.71 | 2576.32 | 2916.38 | 2181.24 | 1907.12
G13 | 3459.36 | 3539.69 | 3242.47 | 2056.13 | 1827.13
G14 | 3626.45 | 3534.81 | 3148.05 | 1934.04 | 1716.63
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | CTG_FAIL_IN_FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 012 | Chief Joseph-Snohomish #3 or #4 345kV Line ***Includes corresponding Chief Joseph & Snohomish 345/230kV Banks (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6665.3967 | -2367.55 | 863.19 | 2423.39 | -691.3 | 1191.56 | 2606.12 | -28.45 | 1986.75 | 2868.86 | 967.58 | 2896.01 | 3427.09 | 2064.71 | 3459.36 | 3626.45
35F | 6338.384 | -596.81 | 1233.59 | 2562.69 | -210.46 | 1908.77 | 2745.16 | 424.48 | 2554.43 | 2997.15 | 1680.15 | 3124.96 | 3500.01 | 2576.32 | 3539.69 | 3534.81
45F | 6053.7927 | -403.4 | 1779.46 | 2573.53 | 84.9 | 2208.68 | 2755.72 | 711.59 | 2649.59 | 3046.63 | 1736.43 | 3138.62 | 3404.6 | 2916.38 | 3242.47 | 3148.05
60F | 4973.4413 | 1319.64 | 2766.49 | 2793.64 | 1545.43 | 2846.78 | 2891.84 | 2236.21 | 2808.92 | 2828.78 | 3302.4 | 3107.95 | 3147.61 | 2181.24 | 2056.13 | 1934.04
70F | 4634.6087 | 1850.74 | 2402.33 | 2417.61 | 2215.56 | 2517.77 | 2766.76 | 2705.16 | 2725.48 | 2744.66 | 3014.6 | 3037.11 | 3066.6 | 1907.12 | 1827.13 | 1716.63

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -2367.65 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 & Sed-Both-HRanch 230kV | -2.88 | -551.08 | -550.74 | 6669.93 | -2367.55 | 1134.32 | FULL
G1 | 863 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] | BFR: Sno-King 230kV South Bus | -3.61 | -517.55 | -543.81 | 6612.08 | 863.19 | -686.96 | FULL
G2 | 2423.69 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 535.26 | 535.22 | 6685.44 | 2423.39 | -1569.74 | CTG_FAIL_IN_FULL
G3 | -691.13 | Branch BOTHELL (46403) TO SNOK S1 (41004) CKT 1 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #7 | -4.52 | -553.74 | -553.74 | 6653.32 | -691.3 | 239.72 | FULL
G4 | 1191.35 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -545.78 | -545.71 | 6616.1 | 1191.56 | -802.4 | FULL
G5 | 2605.92 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 535.49 | 535.43 | 6686.06 | 2606.12 | -1610.27 | CTG_FAIL_IN_FULL
G6 | -30.65 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -553.5 | -553.54 | 6655.96 | -28.45 | -20.41 | FULL
G7 | 1986.77 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -548.73 | -548.61 | 6633.46 | 1986.75 | -1151.87 | FULL
G8 | 2869.4 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4522 Echo Lk-Mon-SnoK #1 500kV & Mon Caps | 13.69 | 625.57 | 628.69 | 6684.76 | 2868.86 | -1632.87 | CTG_FAIL_IN_FULL
G9 | 967.42 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -550.61 | -550.57 | 6667.81 | 967.58 | -380.27 | FULL
G10 | 2896.8 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -546.31 | -546.37 | 6660.05 | 2896.01 | -1477.09 | FULL
G11 | 3427.75 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 536.27 | 536.59 | 6695.71 | 3427.09 | -1760.73 | CTG_FAIL_IN_FULL
G12 | 2065.1 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -548.35 | -548.3 | 6689.84 | 2064.71 | -852.58 | FULL
G13 | 3459.49 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 537.02 | 536.97 | 6675.05 | 3459.36 | -1658.14 | CTG_FAIL_IN_FULL
G14 | 3626.61 | Branch CUST BNK1 (95008) TO CUST ING2 (95009) CKT 1 [500.00 - 500.00 kV] | BFR: 4276 Cust-Ing #1 500kV & Cust 500/230kV Bk#2 | 100 | 3588.78 | 3587.13 | 6695.38 | 3626.45 | -1721.43 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -596.62 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -540.74 | -540.67 | 6322.59 | -596.81 | 161.39 | FULL
G1 | 1233.79 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -5.77 | -525.59 | -525.64 | 6287.68 | 1233.59 | -866.68 | FULL
G2 | 2563.95 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 518.9 | 518.9 | 6354.16 | 2562.69 | -1607.97 | CTG_FAIL_IN_FULL
G3 | -210.99 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -535.89 | -535.85 | 6323.15 | -210.46 | 10.13 | FULL
G4 | 1908.69 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -535.96 | -535.87 | 6305.34 | 1908.77 | -1190.66 | FULL
G5 | 2745.44 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 518.83 | 518.77 | 6354.65 | 2745.16 | -1647.79 | CTG_FAIL_IN_FULL
G6 | 423.06 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -535.6 | -535.66 | 6327.41 | 424.48 | -234.8 | FULL
G7 | 2555.69 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -536.3 | -536.26 | 6322.27 | 2554.43 | -1464.07 | FULL
G8 | 2997.49 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 517.89 | 517.81 | 6359.05 | 2997.15 | -1676.67 | CTG_FAIL_IN_FULL
G9 | 1682.18 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -537.88 | -537.8 | 6348.81 | 1680.15 | -759.76 | FULL
G10 | 3125.43 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 518.25 | 518.22 | 6333.99 | 3124.96 | -1573.31 | CTG_FAIL_IN_FULL
G11 | 3500.65 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.24 | -2599.73 | -2599.86 | 6364.07 | 3500.01 | -1758.35 | CTG_FAIL_IN_FULL
G12 | 2576.82 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -535.07 | -537.25 | 6372.66 | 2576.32 | -1128.06 | FULL
G13 | 3540.41 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3504.12 | -3506.36 | 6344.6 | 3539.69 | -1657.75 | FULL
G14 | 3535.39 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3499.31 | -3501.61 | 6355.33 | 3534.81 | -1625.93 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -403.24 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -522.33 | -522.26 | 6039.12 | -403.4 | 72.71 | FULL
G1 | 1779.43 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -521.09 | -521.25 | 6021.41 | 1779.46 | -1169.67 | FULL
G2 | 2574.74 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 14.27 | 567.68 | 525.74 | 6068.06 | 2573.53 | -1604.97 | CTG_FAIL_IN_FULL
G3 | 84.12 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -522.53 | -522.48 | 6040.93 | 84.9 | -142.84 | FULL
G4 | 2208.96 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -522.72 | -522.88 | 6032.16 | 2208.68 | -1357.51 | FULL
G5 | 2755.96 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 504.23 | 504.18 | 6069.74 | 2755.72 | -1645.88 | CTG_FAIL_IN_FULL
G6 | 711.43 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -524.23 | -524.21 | 6046.81 | 711.59 | -384.26 | FULL
G7 | 2650.04 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 504.61 | 504.59 | 6039.58 | 2649.59 | -1504.4 | CTG_FAIL_IN_FULL
G8 | 3046.97 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 504.11 | 504.06 | 6071.2 | 3046.63 | -1693.64 | CTG_FAIL_IN_FULL
G9 | 1737.38 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -522.28 | -522.25 | 6065.89 | 1736.43 | -766.93 | FULL
G10 | 3139.23 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 11.53 | 504.18 | 504.14 | 6049.91 | 3138.62 | -1566.5 | CTG_FAIL_IN_FULL
G11 | 3405.04 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.24 | -2524.17 | -2524.1 | 6070.72 | 3404.6 | -1693.78 | CTG_FAIL_IN_FULL
G12 | 2916.98 | Branch MAPLE VL (40689) TO SNOK S1 (41004) CKT 2 [230.00 - 230.00 kV] | 3TM: Monroe-Echo LK-SnoK 500kV | 11.81 | 487.71 | 488.05 | 6103.05 | 2916.38 | -1314.23 | FULL
G13 | 3242.97 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.46 | -436.74 | -436.71 | 6042.65 | 3242.47 | -1485.7 | FULL
G14 | 3148.43 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.46 | -436.21 | -436.01 | 6045.66 | 3148.05 | -1381.79 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1319.51 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -498.12 | -498.15 | 4983.83 | 1319.64 | -812.68 | FULL
G1 | 2766.78 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.24 | -2406 | -2405.72 | 4971.61 | 2766.49 | -1621.86 | CTG_FAIL_IN_FULL
G2 | 2794.17 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.24 | -2409.81 | -2409.51 | 4982.09 | 2793.64 | -1609.54 | CTG_FAIL_IN_FULL
G3 | 1547.65 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | -5.77 | -490.63 | -491.28 | 4987.68 | 1545.43 | -877.56 | FULL
G4 | 2846.55 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.24 | -2395.31 | -2394.99 | 4968.68 | 2846.78 | -1619.48 | CTG_FAIL_IN_FULL
G5 | 2892.27 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.24 | -2411.7 | -2411.09 | 4978.79 | 2891.84 | -1596.78 | CTG_FAIL_IN_FULL
G6 | 2235.82 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -494.28 | -494.35 | 5002.62 | 2236.21 | -1154.35 | FULL
G7 | 2808.83 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2231.17 | -2232.22 | 4959.56 | 2808.92 | -1460.95 | FULL
G8 | 2829.12 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2233.15 | -2234.48 | 4969.8 | 2828.78 | -1440.52 | FULL
G9 | 3302.7 | Branch CUST ING1 (95012) TO CUSTER W (40323) CKT 1 [500.00 - 500.00 kV] | BFR: 4486 Cust-Ing #2 500kV & Cust 500/230kV Bk#2 | -100 | -3272.44 | -3270.65 | 5036.11 | 3302.4 | -1588.57 | FULL
G10 | 3109.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2210.87 | -2209.74 | 4960.35 | 3107.95 | -1429.79 | FULL
G11 | 3148.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2237.4 | -2238.49 | 4971.74 | 3147.61 | -1421.45 | FULL
G12 | 2181.28 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.46 | -425.85 | -425.79 | 4988.26 | 2181.24 | -755.27 | FULL
G13 | 2059.09 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.46 | -424.24 | -424.15 | 4915.2 | 2056.13 | -647.94 | FULL
G14 | 1934.15 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.46 | -424.43 | -424.37 | 4925.3 | 1934.04 | -547.44 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 1849.14 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -479.96 | -480 | 4664.41 | 1850.74 | -1093.85 | FULL
G1 | 2402.55 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2127.29 | -2126.26 | 4619.43 | 2402.33 | -1374.71 | FULL
G2 | 2419.14 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2132.03 | -2133.97 | 4630.82 | 2417.61 | -1357.77 | FULL
G3 | 2215.51 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | -5.71 | -484.95 | -484.91 | 4672.81 | 2215.56 | -1232.4 | FULL
G4 | 2519.81 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2143.82 | -2144.77 | 4618.26 | 2517.77 | -1381.3 | FULL
G5 | 2767.29 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -65.24 | -2299.05 | -2298.74 | 4635.91 | 2766.76 | -1479.89 | CTG_FAIL_IN_FULL
G6 | 2704.71 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2158.02 | -2156.08 | 4685.89 | 2705.16 | -1397.98 | FULL
G7 | 2724.96 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2158.7 | -2157.24 | 4616.08 | 2725.48 | -1376.8 | FULL
G8 | 2746.99 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2150.69 | -2149 | 4628.53 | 2744.66 | -1363 | FULL
G9 | 3014.73 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2156.33 | -2155.06 | 4688.26 | 3014.6 | -1371.63 | FULL
G10 | 3039.08 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2159.78 | -2158.59 | 4617.76 | 3037.11 | -1352.84 | FULL
G11 | 3068.81 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.68 | -2162.75 | -2161.52 | 4630.13 | 3066.6 | -1339.05 | FULL
G12 | 1907.09 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.46 | -422.9 | -422.84 | 4646.9 | 1907.12 | -567.72 | FULL
G13 | 1827.05 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.46 | -425.24 | -425.18 | 4576.17 | 1827.13 | -487.22 | FULL
G14 | 1716.7 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.46 | -424.41 | -424.36 | 4587.77 | 1716.63 | -390.32 | FULL
012WINTER09v1SNH