<!DOCTYPE HTML PUBLIC "-//W3C//DTD HTML 4.0 Transitional//EN"><!-- saved from url=(0051)http://emergencyservices.bnl.gov/annualr/cy_98.html -->

Annual Summary of Fire and Other Related Property

Damage Experience Report for Calendar Year 2000

Brookhaven National Laboratory

Emergency Services Division

Prepared by J. Levesque

February, 2001

This report summarizes the fire and other property damage experience of Brookhaven National Laboratory for the 2000 Calendar Year.  The information in this report is in the format requested in "Environment, Safety and Health Reporting," Manual for DOE Order 231.1-1”, Appendix F, dated 1-28-2000.

1. Fire Related Deaths and Injuries.

None.

2. BNL Property Loss Experience for the Calendar Year.

Fire Loss1         $70,200

Damage or loss sustained as a consequence of, and following the outbreak of fire, shall be classified as a fire loss.

Other Loss2         None

Damage or loss sustained as a consequence of the following events shall be classified as another loss: explosions, natural cause events, electrical malfunctions, transportation (cargo) losses, mechanical malfunctions, radiation releases or other nuclear accidents, and miscellaneous (i.e., thermal) accidents.

1 Summation of fire losses as detailed in section 3A and in Attachment A. 
2 Summation of other losses as detailed in Attachment A.

3. Summary of Fire and Other Property Loss Incidents.

A. Details of Losses of $5,000 or More.

Date:    March 11, 2000

Type of Loss: Fire

Incident Report Number: 00-058 (3-11-00 fire), 00-059 (3-12-00 rekindle), 00-060 (3-12-00 rekindle)

DOE Occurrence Report: Yes

Loss Estimate: $70,200

On March 11, 2000 a fire occurred at a waste-staging area associated with the Chemical/Glass Holes Project at Brookhaven National Laboratory. The waste included low level radioactive soil and processed (shredded) debris, which was stored in “Soft Sided Lift Liner” containers.  Thirty-two lift liner containers, made of light density polypropylene, containing these wastes were involved in the fire.  The plastic lift liner containers and the polyethylene coverings were the primary fuel.  The plastic sacks most likely were ignited by burning pieces of straw.  The warm spring day in March accelerated bacterial action within the straw, generating sufficient heat to spontaneously combust.  Combustible straw had been allowed to enter the waste stream without the hazards being identified and controls implemented.

Direct property loss (sacks, polyethylene cover) is estimated at under $17,200.  The costs of the repackaging and analysis were $10,000.  Investigation costs are estimated at $10,000.  The costs of emergency response (Radiological Control Technician, Fire/Rescue, and Analytical Services) is estimated at $33,000.

B. Summary of Losses Less than $5,000.

See Attachment A to this report for a list of minor fires and losses for CY00.

See Attachment B to this report for a list of miscellaneous electrical and other smoke related incidents for CY00.

4. Incidents Actuating Automatic Fire Suppression Systems.

None occurred for CY 2000.

5. Halon Reduction Activities.

A. Halon 1301:

| 1. | Number of Fixed Systems | 37 Systems |
| --- | --- | --- |
| 2. | Total Quantity of Halon 1301 at Site |  |
|  | a. Active (including reserve) | 10,690 Lbs. |
|  | b. Inventoried | 4,984 Lbs. |
| 3. | Fixed Systems Deactivated Within Past Year |
|  | a. Total Number | 1 Systems |
|  | b. Total Quantity | 590 Lbs. |
| 4. | Fixed Systems Converted to Manual Operation Within the Past Year |
|  | a. Total Number | None |
|  | b. Total Quantity | N/A |
| Note: Due to a change in the tracking system from Dbase IV to a Barcode system, present cylinder inventories do not include weights. Actions are underway to track weights accurately. |  |  |

B. Halon 1211:

| 1. | Total Quantity of Halon 1211 at Site |  |
| --- | --- | --- |
|  | a. Active | 9690 Lbs. (570 17# units) |
|  | b. Inventoried | 63 Lbs. (B599recovery tank) |
| 2. | Quantity Replaced by Other Agents Within the Past Year | None |
| Note: Due to a change in the tracking system from Dbase IV to a Barcode system, present cylinder inventories do not include weights. Actions are underway to track weights accurately. |  |  |

6. Fire Protection Inspection, Testing, and Maintenance Activities.

BNL has an active fire protection inspection, testing, and maintenance program.  The program includes the inspection and testing of over 220 fire alarm panels, monitoring over 6000 alarm points in 250 facilities.  Inspection, testing and maintenance is done in general accordance with NFPA codes and standards.  The annual report format requests information on failure rates of equipment included in the fire protection inspection, testing, and maintenance activities.  While BNL has a vigorous inspection, testing, and maintenance program, the ability to accurately capture failure rates of equipment has not previously existed.  With Plant Engineering’s recent acquisition of new maintenance management software, the possibility to capture this information is possible.   An implementation plan is being developed.

7. Fire Department Activities.

| A. Number of Responses: | CY00 | CY99 | CY98 | CY97 |
| --- | --- | --- | --- | --- |
| 1. Fire | 16 | 5 | 32 | 25 |
| 2. HAZMAT Response | 58 | 63 | 58 | 63 |
| 3. Other Emergency | 51 | 12 | 65 | 58 |
| 4. Other Non-Emergency1 | 154 | 311 | 233 | 248 |
| 5. Medical | 92 | 117 | 106 | 87 |
| 1 Includes false alarms, non-emergency responses, drills, and miscellaneous. |

B. Major Equipment Purchases:

Placed an order for a replacement Rescue Truck ($250K). To be in service 1st quarter of 2001.

Formed Ambulance Committee to develop plans and specifications for replacement ambulance.  To be in service 4th quarter of 2001.

C. Noteworthy Activity.

Installed a residential type sprinkler system in Bldg. 257 Guest Dormitory ($200K).

Installed Inergen Clean Agent Fire Suppression System in Bldg. 515’s Network Backbone Room ($250K).

Established a Fire Protection System Planning Committee to provide long range planning for the aging infrastructure associated with fire systems.

See Attachment C to this report for a list of mutual aid responses to surrounding communities for CY00.

8. Recurring Fire Protection Program Costs.

# Fire Department Costs

|  |  | FY00 | FY99 | FY98 | FY97 |
| --- | --- | --- | --- | --- | --- |
| 1. | Staffing1,2,4 | $2,306K 2 | $2,419K6 | $2,196K5 | $2,231K |
| 2. | Equipment (MST) | $178K8 | $133K | $130K | $143K |
| 3. | Inspection & Testing Program3 | N/A | N/A | N/A | N/A |
| 4. | Emergency Medical Response Program3 | N/A | N/A | N/A | N/A |
| 5. | Training Program3 | N/A | N/A | N/A | N/A |

# Inspection & Testing Program By Others4

|  | $1,280K | $828K | $801K | $979K |
| --- | --- | --- | --- | --- |

# Fire Protection Engineering (FPE)

|  | $249K7 | $292K | $266K | $198K |
| --- | --- | --- | --- | --- |

1 Costs reflect salary, wage, and fringe for uniform firefighters.

2 Reduction in cost reflects loss of Deputy Chief’s position in 2000.
3 These programs are integral to Fire Department operations. Costs are included in 1 and 2, above. 
4 Costs include salary and benefits and other Plant Engineering fire system maintenance costs (fire alarm electricians, plumber, etc.).   Source documents is Activity Data Sheet A92D0133.
5 Change in numbers from FY97 to FY98 reflects shift of one FTE from Fire Department budget to FPE budget.

6 Costs include a new organizational burden added to overhead operations at BNL.

7 Costs reflect a reduction of one Fire Protection Engineer in 2000

8 Does not include $210k for FY00 building space charges, heat, electric, and repair of the firehouse.

ATTACHMENT A

Summary of Fires and Losses of Less than $5,000

for Calendar Year 2000

| Date: 03/04/00 | Type of Loss: Fire |
| --- | --- |
| Incident Report Number: 000050 | Government Loss Estimate: $ 100 |
| Description: Cutting operation ignited Trane chiller filter. Operation conducted under permit 00-1490. Fire watch extinguished filter with Halon 1211 extinguisher. Only the filter was damaged. |

| Date: 03/31/00 | Type of Loss: Brush Fire |
| --- | --- |
| Incident Report Number: 000070 | Government Loss Estimate: $ 0 |
| Description: Wildland fire by National Weather Service Building. Reported by lunchtime passerby. Less than 1/8 acre involved. |

| Date: 04/07/00 | Type of Loss: Brush Fire |
| --- | --- |
| Incident Report Number: 000079 | Government Loss Estimate: $ 0 |
| Description: Wildland fire by Princeton and Grove Streets. Reported by lunchtime jogger. Less than 1/8 acre involved. |

| Date: 05/01/00 | Type of Loss: Fire |
| --- | --- |
| Incident Report Number: 000099 | Government Loss Estimate: $ 0 |
| Description: Outside contractor torch cutting railroad cars for salvage. Welding permit issued and area was wetted down with fire hose. Sparks traveled to fence line 30 to 50 feet away. Ignited brush growing under fence. No real property damage. |

| Date: 05/24/00 | Type of Loss: Electrical Over Voltage |
| --- | --- |
| Incident Report Number: 000126 | Government Loss Estimate: $5K |
| Description: During a test of an emergency generator, the voltage controller failed. Voltage above design was supplied to the building, causing various electrical components to smoke. |

| Date: 08/16/00 | Type of Loss: Fire |
| --- | --- |
| Incident Report Number: 000243 | Government Loss Estimate: $10.00 |
| Description: Smell of smoke report for Bldg. 479. Found unit heater smoking. Used CO2 extinguisher to put out smoldering materials (flexible duct joint). |

| Date: 10/04/00 | Type of Loss: Electrical Fire |
| --- | --- |
| Incident Report Number: 000302 | Government Loss Estimate: $500. |
| Description: Building occupant (AGS operator) smelled smoke. Pulled fire alarm box. Fire Alarm Panel failed. Operator pulled a Halon discharge station, discharging 590 pounds of halon. Still no alarm was transmitted, so a call was placed to 911. The fire origin was found the next day at an electrical motor control panel. A short in the panel caused an overload. Sparks from the overload ignited a 55-gallon bag of garbage in front of the motor control center. No further damage occurred. |

| Date: 10/09/00 | Type of Loss: Wildland Fire |
| --- | --- |
| Incident Report Number: 000309 | Government Loss Estimate: $0 |
| Description: 100’ by 100’ wildland fire burned by the northeast firebreak. |

| Date: Various after 10/31/00 | Type of Loss: Wildland Fire |
| --- | --- |
| Incident Report Number: 000322, 23, 24, 29, 30, 31, 34, 36 | Government Loss Estimate: $0 |
| Description: Wildland fire burned approximately 12.6 acres of undeveloped land by the northeast firebreak. Likely origin was the wildland fire from Incident 000309. The fire rekindled several times due to the heavy organic ground cover. |

| Date: 12/12/00 | Type of Loss: Fire |
| --- | --- |
| Incident Report Number: 000375 | Government Loss Estimate: 200 |
| Description: Responded to a report of smoke. Cooking pot left on stove unattended. No extension of fire. |

ATTACHMENT B

Summary of Miscellaneous Electrical and Other Smoke Related Incidents

for Calendar Year 2000

See Attachment A, Incident numbers 000126, 000243 and 000302.

ATTACHMENT C

Summary of Mutual Aid Responses to Surrounding Communities

for Calendar Year 2000

Date: 01/10/00
Incident Report Number: 000005
Mutual Aid To: Heavy rescue and transport provided to Ridge Fire Department for a vehicle accident.  Transported on patient.

Date: 04/29/00
Incident Report Number: 000096
Mutual Aid To: To Ridge Fire Department for vehicle accident.  Transported one patient.

Date: 04/30/00
Incident Report Number: 000097
Mutual Aid To: To Ridge Fire Department for vehicle accident.  Transported two injured to BMH.

Date: 05/24/00
Incident Report Number: 000127
Mutual Aid To: Ridge Fire Department for three car accident.  Transported one injured.

Date: 06/14/00
Incident Report Number: 000150
Mutual Aid To: Ridge Fire Department for ambulance service related to school bus accident.  Transported two injured.