# CDF SVXII Cables	10/01/99

Remote sensor

### Cable

0.025" Pleated Foil Shielded Cable, 30 AWG Solid, TPE Primary, Halogen-free Cover

3M Part #: 90201/26

### Description

Manufacturer:  3M

Cable Type:     Shielded and jacketed high density flat cable.

Part Number:   3M 90201/26

Function:          Provides remote sensing to SVXII power supplies to enable dynamic voltage adjustment

Length:             60ft

Location_1:      Power/supply/FIB racks mounted on collision hall walls

Location_2:      Just inside ISL spaceframe

### Fire Safety

Flame test rating: Rated for 105 C @ 150V

Insulation material: Thermoplastic Elastomer(TPE)

Jacket material: Thermoplastic Elastomer(TPE)

### Electrical Considerations

Power conductor ampacity: 1Amp(estimated as this is a power limited cable)

Power conductor overcurrent protection: sense lines are connected to load using (50 () current-limiting resistors.  This would limit current to 160mA in the event of a short in the sensing circuitry on the power supply.

High voltage conductor rating: 150V

## Connector 1: At CAEN Crate

0.050" Mini D Ribbon (MDR) Connector, IDC Wiremount Plug --- Shielded.

3M Part #:  10136-6000EC

Metal Junction Shell Part #: 10336-1230-00

## Connector 2: At the Junction Board

0.050" Mini D Ribbon (MDR) Connector, IDC Wiremount Plug --- Shielded.

3M Part #: 10126-6000EC

Metal Junction Shell Part #: 10326-1230-00

Connector pin-out assignments:

| PIN @ CAEN | PIN @ JB1 | Conductor Number | Description | CAEN Designation | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | - | - | Enable | Enable | Connected to PIN 19 in the Connector at CAEN |
| 19 | - | - | Enable 1 | En 1 | See pin 19 |
| 2 | - | - | No Connection |  | not/connected |
| 20 | - | - | No Connection |  | n/c |
| 3 | - | - | No Connection |  | n/c |
| 21 | - | - | No Connection |  | n/c |
| 4 | - | - | DTERM POS. | DTERMSP | n/c |
| 22 | - | - | DTERM NEG. | DTERMSN | n/c |
| 5 | 1 | 2 | 5VDOIM POS. | 5VDOIMSP |  |
| 23 | 14 | 1 | 5VDOIM NEG. | 5VDOIMSN |  |
| 6 | 2 | 4 | 2VDOIM POS. | 2VDOIMSP |  |
| 24 | 15 | 3 | 2VDOIM NEG. | 2VDOIMSN |  |
| 7 | 3 | 6 | Digital layer 0 pos. | DSPLY0 |  |
| 25 | 16 | 5 | Digital layer 0 neg. | DSNLY0 |  |
| 8 | 4 | 8 | Analog layer 0 pos. | ASPLY0 |  |
| 26 | 17 | 7 | Analog layer 0 neg. | ASNLY0 |  |
| 9 | 5 | 10 | Digital layer 1 pos. | DSPLY1 |  |
| 27 | 18 | 9 | Digital layer 1 neg. | DSNLY1 |  |
| 10 | 6 | 12 | Analog layer 1 pos. | ASPLY1 |  |
| 28 | 19 | 11 | Analog layer 1 neg. | ASNLY1 |  |
| 11 | 7 | 14 | Digital layer 2 pos. | DSPLY2 |  |
| 29 | 20 | 13 | Digital layer 2 neg. | DSNLY2 |  |
| 12 | 8 | 16 | Analog layer 2 pos. | ASPLY2 |  |
| 30 | 21 | 15 | Analog layer 2 neg. | ASNLY2 |  |
| 13 | 9 | 18 | Digital layer 3 pos. | DSPLY3 |  |
| 31 | 22 | 17 | Digital layer 3 neg. | DSNLY3 |  |
| 14 | 10 | 20 | Analog layer 3 pos. | ASPLY3 |  |
| 32 | 23 | 19 | Analog layer 3 neg. | ASNLY3 |  |
| 15 | 11 | 22 | Digital layer 4 pos. | DSPLY4 |  |
| 33 | 24 | 21 | Digital layer 4 neg. | DSNLY4 |  |
| 16 | 12 | 24 | Analog layer 4 pos. | ASPLY4 |  |
| 34 | 25 | 23 | Analog layer 4 neg. | ASNLY4 |  |
| 17 | - | - | GROUND | EARTH | n/c |
| 35 | - | - | GROUND | EARTH | n/c |
| 18 | - | - | SHIELD | SHIELD | The shield pin on the CAEN supply should be attached to the shield of the cable. The cable shield will attach to the connector at the junction board and to the board through the connector |
| 36 | - | - | SHIELD | SHIELD | n/c |
| - | 13 | - |  |  | n/c |
| - | 26 | - |  |  | n/c |
| - | - | 26 |  |  | n/c |
| - | - | 25 |  |  | n/c |

1 Junction Board

### Contact person

Matthew Herndon, x8619, herndon@fnal.gov

Low Voltage Connection

### Cable

30 Conductor, 22 AWG Spectra-Bond parallel conductor ribbon cable.

Amphenol Spectra-Strip Part #: 843-111-2214-030.

NOTE:  Using two cables per assembly.

### Description

Manufacturer:  Amphenol

Cable Type:     Flat ribbon cable.

Part Number:   843-111-2214-030

Function:         Supplies low voltages to SVXII port card and SVX3 IC.

Length:             60ft

Location_1:      Power/supply/FIB racks mounted on collision hall walls

Location_2:      Just inside ISL spaceframe

### Fire Safety

Flame test rating: Rated for 105 C @ 300V

Insulation material: Flame-retardant PVC

### Electrical Considerations

Power conductor ampacity: 3.3Amps.  In addition connector pin current has been reduced by 2 to 5 times on high current lines by using multiple conductors.

Power conductor overcurrent protection: Fused at power supply.  Also hardware and software trip control.  As the maximum current for any supply is below the rated maximum of the cable assembly, fusing of individual lines is not necessary.  In addition connector pin current has been reduced by 2 to 5 times on high current lines by using multiple conductors.

High voltage conductor rating: 300V

## Connector 1: At the CAEN Power Supply

Plug connector, Size 5, 78 position, Amplimite HDP-22

AMP Part #:  748368-1 	Pins as numbered in AMP drawing 748368 1 of 1.

Metalized Shell Part #:  748677-5

Spring Latches #:  745255-2

Latch Blocks #  745245-5

Male Contact #:  748333-2

## Connector 2: At the Junction Board

Plug connector, Size 4, 62 position, Amplimite HDP-22

AMP Part #:  748367-1 	Pins as numbered in AMP drawing 748367 1 of 1.

Metalized Shell Part #:  748677-4

Spring Latches #:  745255-2

Latch Blocks #  745245-2

Male Contact #:  748333-2

Connector pin-out assignments:

| PIN @ CAEN | PIN @ JB | Conductor Number | Description | CAEN Designation | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | 1 | A 1 | Analog layer 4 neg. | AVNLY4 |  |
| 21 | 43 | A 3 | Analog layer 4 neg. | AVNLY4 |  |
| 40 | 23 | A 5 | Analog layer 4 neg. | AVNLY4 |  |
| 60 | 3 | A 7 | Analog layer 4 neg. | AVNLY4 |  |
| 2 | 22 | A 2 | Analog layer 4 pos. | AVPLY4 |  |
| 22 | 44 | A 4 | Analog layer 4 pos. | AVPLY4 |  |
| 41 | 2 | A 6 | Analog layer 4 pos. | AVPLY4 |  |
| 61 | 24 | A 8 | Analog layer 4 pos. | AVPLY4 |  |
| 3 | 45 | A 9 | Analog layer 3 neg. | AVNLY3 |  |
| 23 | 25 | A 11 | Analog layer 3 neg. | AVNLY3 |  |
| 42 | 5 | A 13 | Analog layer 3 neg. | AVNLY3 |  |
| 62 | - | - | Analog layer 3 neg. | AVNLY3 | n/c |
| 4 | 46 | A 10 | Analog layer 3 pos. | AVPLY3 |  |
| 24 | 4 | A 12 | Analog layer 3 pos. | AVPLY3 |  |
| 43 | 26 | A 14 | Analog layer 3 pos. | AVPLY3 |  |
| 63 | - | - | Analog layer 3 pos. | AVPLY3 | n/c |
| 5 | 47 | A 15 | Analog layer 2 neg. | AVNLY2 |  |
| 25 | 48 | A 16 | Analog layer 2 pos. | AVPLY2 |  |
| 44 | 27 | A 17 | Analog layer 2 neg. | AVNLY2 |  |
| 64 | 6 | A 18 | Analog layer 2 pos. | AVPLY2 |  |
| 6 | 7 | A 19 | Analog layer 1 neg. | AVNLY1 |  |
| 26 | 28 | A 20 | Analog layer 1 pos. | AVPLY1 |  |
| 45 | 49 | A 21 | Analog layer 1 neg. | AVNLY1 |  |
| 65 | 50 | A 22 | Analog layer 1 pos. | AVPLY1 |  |
| 7 | 29 | A 23 | Analog layer 0 neg. | AVNLY0 |  |
| 27 | 8 | A 24 | Analog layer 0 pos. | AVPLY0 |  |
| 46 | - | - | Analog layer 0 neg. | AVNLY0 | n/c |
| 66 | - | - | Analog layer 0 pos. | AVPLY0 | n/c |
| 8 | - | - | Dterm negative | DTERM_N | n/c |
| 28 | - | - | Dterm positive | DTERM_P | n/c |
| 47 | - | - | Dterm negative | DTERM_N | n/c |
| 67 | - | - | Dterm positive | DTERM_P | n/c |
| 9 | 51 | D 1 | Digital layer 4 neg. | DVNLY4 |  |
| 29 | 52 | D 2 | Digital layer 4 pos. | DVPLY4 |  |
| 48 | 31 | D 3 | Digital layer 4 neg. | DVNLY4 |  |
| 68 | 10 | D 4 | Digital layer 4 pos. | DVPLY4 |  |
| 10 | 11 | D 5 | Digital layer 3 neg. | DVNLY3 |  |
| 30 | 32 | D 6 | Digital layer 3 pos. | DVPLY3 |  |
| 49 | - | - | Digital layer 3 neg. | DVNLY3 | n/c |
| 69 | - | - | Digital layer 3 pos. | DVPLY3 | n/c |
| 11 | 53 | D 7 | Digital layer 2 neg. | DVNLY2 |  |
| 31 | 54 | D 8 | Digital layer 2 pos. | DVPLY2 |  |
| 50 | - | - | Digital layer 2 neg. | DVNLY2 | n/c |
| 70 | - | - | Digital layer 2 pos. | DVPLY2 | n/c |
| 12 | 33 | D 9 | Digital layer 1 neg. | DVNLY1 |  |
| 32 | 12 | D 10 | Digital layer 1 pos. | DVPLY1 |  |
| 51 | - | - | Digital layer 1 neg. | DVNLY1 | n/c |
| 71 | - | - | Digital layer 1 pos. | DVPLY1 | n/c |
| 13 | 13 | D 11 | Digital layer 0 neg. | DVNLY0 |  |
| 33 | 34 | D 12 | Digital layer 0 pos. | DVPLY0 |  |
| 52 | - | - | Digital layer 0 neg. | DVNLY0 | n/c |
| 72 | - | - | Digital layer 0 pos. | DVPLY0 | n/c |
| 14 | 55 | D 13 | 2VDOIM NEG. | 2VDOIMN |  |
| 34 | 35 | D 15 | 2VDOIM NEG. | 2VDOIMN |  |
| 53 | 15 | D 17 | 2VDOIM NEG. | 2VDOIMN |  |
| 73 | 57 | D 19 | 2VDOIM NEG. | 2VDOIMN |  |
| 15 | 56 | D 14 | 2VDOIM POS. | 2VDOIMP |  |
| 35 | 14 | D 16 | 2VDOIM POS. | 2VDOIMP |  |
| 54 | 36 | D 18 | 2VDOIM POS. | 2VDOIMP |  |
| 74 | 58 | D 20 | 2VDOIM POS. | 2VDOIMP |  |
| 16 | 37 | D 21 | 5VDOIM NEG. | 5VDOIMN |  |
| 36 | 17 | D 23 | 5VDOIM NEG. | 5VDOIMN |  |
| 55 | 39 | D 27 | 5VDOIM NEG. | 5VDOIMN |  |
| 75 | 19 | D 29 | 5VDOIM NEG. | 5VDOIMN |  |
| 17 | - | - | 5VDOIM NEG. | 5VDOIMN | n/c |
| 37 | 60 | D 26 | 5VDOIM POS. | 5VDOIMP |  |
| 56 | 59 | D 25 | 5VDOIM NEG. | 5VDOIMN |  |
| 76 | - | - | 5VDOIM POS. | 5VDOIMP | n/c |
| 18 | 16 | D 22 | 5VDOIM POS. | 5VDOIMP |  |
| 38 | 38 | D 24 | 5VDOIM POS. | 5VDOIMP |  |
| 57 | 18 | D 28 | 5VDOIM POS. | 5VDOIMP |  |
| 77 | 40 | D 30 | 5VDOIM POS. | 5VDOIMP |  |
| 19 | - | - | EARTH | EARTH | n/c |
| 39 | - | - | EARTH | EARTH | n/c |
| 58 | - | - | SHIELD | SHIELD_2 | n/c |
| 78 | - | - | SHIELD | SHIELD_2 | n/c |
| 20 | - | - | ENABLE 1 | EN_1 | Connected to PIN 59 in Connector at CAEN |
| 59 | - | - | ENABLE 2 | EN_2 | See Pin 20 |
| - | 9 | - |  |  | n/c |
| - | 30 | - |  |  | n/c |
| - | 20 | - |  |  | n/c |
| - | 21 | - |  |  | n/c |
| - | 41 | - |  |  | n/c |
| - | 42 | - |  |  | n/c |
| - | 61 | - |  |  | n/c |
| - | 62 | - |  |  | n/c |
|  |  | A 25 |  |  | n/c |
|  |  | A 26 |  |  | n/c |
|  |  | A 27 |  |  | n/c |
|  |  | A 28 |  |  | n/c |
|  |  | A 29 |  |  | n/c |
|  |  | A 30 |  |  | n/c |

Maximum voltage and current per supply.

| Supply Name | Maximum Voltage(V) | Maximum Current(A) | Number of Lines | Current per Line(A) |
| --- | --- | --- | --- | --- |
| UAV_0 | 10.0 | 0.6 | 1 | 0.6 |
| AG_0 | 0.0 | 0.6 | 1 | 0.6 |
| UAV_1 | 10.0 | 0.9 | 2 | 0.45 |
| AG_1 | 0.0 | 0.9 | 2 | 0.45 |
| UAV_2 | 10.0 | 1.5 | 2 | 0.75 |
| AG_2 | 0.0 | 1.5 | 2 | 0.75 |
| UAV_3 | 10.0 | 1.5 | 3 | 0.5 |
| AG_3 | 0.0 | 1.5 | 3 | 0.5 |
| UAV_4 | 10.0 | 2.1 | 4 | .53 |
| AG_4 | 0.0 | 2.1 | 4 | .53 |
| DVDD0 | 8.0 | 0.6 | 1 | 0.6 |
| DGND0 | 0.0 | 0.6 | 1 | 0.6 |
| DVDD1 | 8.0 | 0.9 | 1 | 0.9 |
| DGND1 | 0.0 | 0.9 | 1 | 0.9 |
| DVDD2 | 8.0 | 1.5 | 1 | 1.5 |
| DGND2 | 0.0 | 1.5 | 1 | 1.5 |
| DVDD3 | 8.0 | 1.5 | 1 | 1.5 |
| DGND3 | 0.0 | 1.5 | 1 | 1.5 |
| DVDD4 | 8.0 | 2.0 | 2 | 1.0 |
| DGND4 | 0.0 | 2.0 | 2 | 1.0 |
| +5V_DOIM | 8.0 | 2.8 | 5 | .56 |
| +2V_DOIM | 3.5 | 1.7 | 4 | .43 |
| DGNDP | 0.0 | 1.1 | 9 | .13 |

### Contact person

Matthew Herndon, x8619, herndon@fnal.gov

Bias, High Voltage Connection

### Cable

0.050" Shielded/Jacketed, Flat Cable, 28 AWG Stranded, PVC Primary, Halogen Free Cover

3M Part #: 3517/15

### Description

Manufacturer:  3M

Cable Type:     Shielded and jacketed flat cable.

Part Number:   3M 3517/15

Function:          Supplies high voltag to bias SVXII ladders.

Length:             60ft

Location_1:      Power/supply/FIB racks mounted on collision hall walls

Location_2:      Just inside ISL spaceframe

### Fire Safety

Flame test rating: Rated for 80 C @ 300V

Insulation material: PVC

Jacket material: PVC Halogen Free

### Electrical Considerations

Power conductor ampacity: 1Amp(estimated as this is a power limited cable)

Power conductor overcurrent protection: fused at power supply.  Also has hardware and software trip control.

High voltage conductor rating: 300V

## Connector at the CAEN Power Supply

Plug assembly, Low Profile, 25 position D Sub (Ribbon Cable)

3M Part #:  3357-4125

Strain Relief #: 3448-8D25A

Junction Shell #: 3357-4125

Jack Screw Kit #: 3342-2

## Connector at the Junction Board

Plug assembly, Low Profile, 15 position, D Sub  (Ribbon Cable)

3M Part #:  3357-4115

Strain Relief #: 3448-8D15A

Junction Shell #: 3357-4115

Jack Screw Kit #: 3342-2

Connector pin-out assignments:

| PIN @ CAEN | PIN @ JB | Conductor Number | Description | CAEN Designation | Comment |
| --- | --- | --- | --- | --- | --- |
| 1 | 1 | 1 | +VBIAS layer 0 pos. | VBPISL0 |  |
| 14 | 9 | 2 | +VBIAS layer 0 neg. | VBNISL0 |  |
| 2 | 2 | 3 | H.V.Ref layer 0 | VBFISL0 |  |
| 15 | 10 | 4 | +VBIAS layer 1 pos. | VBPISL0 |  |
| 3 | 3 | 5 | -VBIAS layer 1 neg. | VBNISL0 |  |
| 16 | 11 | 6 | H.V.Ref layer 1 | VBFISL1 |  |
| 4 | 4 | 7 | +VBIAS layer 2 pos. | VBPISL1 |  |
| 17 | 12 | 8 | -VBIAS layer 2 neg. | VBNISL1 |  |
| 5 | 5 | 9 | H.V.Ref layer 2 | VBFISL2 |  |
| 18 | 13 | 10 | +VBIAS layer 3 pos. | VBPISL3 |  |
| 6 | 6 | 11 | -VBIAS layer 3 neg. | VBNISL3 |  |
| 19 | 14 | 12 | H.V.Ref layer 3 | VBFISL3 |  |
| 7 | 7 | 13 | +VBIAS layer 4 pos. | VBPISL4 |  |
| 20 | 15 | 14 | -VBIAS layer 4 neg. | VBNISL4 |  |
| 8 | 8 | 15 | H.V.Ref layer 4 | VBFISL4 |  |
| 21 | - | - | ENABLE | EN_0 | Connected to PIN 9 in the Connector at CAEN |
| 9 | - | - | ENABLE | EN_1 | See Pin 21 |
| 22 | - | - | GROUND | EARTH | n/c |
| 10 | - | - | GROUND | EARTH | n/c |
| 23 | - | - | GROUND | EARTH | n/c |
| 11 | - | - | SHIELD | SHIELD | The shield pin on the CAEN supply should be attached to the shield of the cable. The cable shield will attach to the connector at the junction board and to the board through the connector. |
| 24 | - | - | SHIELD | SHIELD | n/c |
| 12 | - | - | No Connection |  | n/c |
| 15 | - | - | No Connection |  | n/c |
| 13 | - | - | No Connection |  | n/c |

Maximum voltage and current per supply

| Supply Name | Maximum Voltage(V) | Maximum Current (mA) |
| --- | --- | --- |
| DBPn | -125.0 | 5.0 |
| DBZn | 125.0 | 5.0 |
| DBGNDn | 0.0 | 5.0 |

(All 5 layers have the same maximaum voltages and currents.  There is one set of three lines per layer.)

### Contact person

Matthew Herndon, x8619, herndon@fnal.gov

Timing Signal Cable

### Cable

0.025" Pleated Foil Shielded Cable, 30 AWG Solid, TPE Primary, Halogen-free Cover

3M Part #: 90201/26

### Description

Manufacturer:  3M

Cable Type:     Shielded and jacketed high density flat cable.

Part Number:   3M 90201/26

Function:          Provides LVDS timing signals from the SVXII FIB transition module.

Length:             60ft

Location_1:      Power/supply/FIB racks mounted on collision hall walls

Location_2:      Just inside ISL spaceframe

### Fire Safety

Flame test rating: Rated for 105 C @ 150V

Insulation material: Thermoplastic Elastomer(TPE)

Jacket material: Thermoplastic Elastomer(TPE)

### Electrical Considerations

Power conductor ampacity: 1Amp(estimated as this is a power limited cable)

Power conductor overcurrent protection: n/a

High voltage conductor rating: 150V

### Connector at FIB Crate

0.050" Mini D Ribbon (MDR) Connector, IDC Wiremount Plug --- Shielded.

3M Part #:  101266000EC

Metal Junction Shell Part #: 10336-1230-00

### Connector at the Junction Board

0.050" Mini D Ribbon (MDR) Connector, IDC Wiremount Plug --- Shielded.

3M Part #: 10126-6000EC

Metal Junction Shell Part #: 10326-1230-00

Connector pin-out assignments:

| PIN @ FIB | PIN @ JB1 | Conductor Number | Description | Comment |
| --- | --- | --- | --- | --- |
| 1 | 1 | 2 | ICFE_CLKH |  |
| 14 | 14 | 1 | ICFE_CLKL |  |
| 2 | 2 | 4 | C_CLK |  |
| 15 | 15 | 3 | C_CLK* |  |
| 3 | 3 | 6 | C_DATA |  |
| 16 | 16 | 5 | C_DATA* |  |
| 4 | 4 | 8 | C_C0 |  |
| 17 | 17 | 7 | C_C0* |  |
| 5 | 5 | 10 | C_C1 |  |
| 18 | 18 | 9 | C_C1* |  |
| 6 | 6 | 12 | C_C2 |  |
| 19 | 19 | 11 | C_C2* |  |
| 7 | 7 | 14 | C_C3 |  |
| 20 | 20 | 13 | C_C3* |  |
| 8 | 8 | 16 | C_C4 |  |
| 21 | 21 | 15 | C_C4* |  |
| 9 | 9 | 18 | ICBE_CLKH |  |
| 22 | 22 | 17 | ICBE_CLKL |  |
| 10 | 10 | 20 | C_L1A |  |
| 23 | 23 | 19 | C_L1A* |  |
| 11 | 11 | 22 | CPIPE_RD2 |  |
| 24 | 24 | 21 | CPIPE_RD2 |  |
| 12 | 12 | 24 | C5_H |  |
| 25 | 25 | 23 | C5_L |  |
| 13 | 13 | - |  | n/c |
| 26 | 26 | - |  | n/c |
| - | - | 26 |  | n/c(option) |
| - | - | 25 |  | n/c |
| - | - | - | SHIELD | The cable shield will attach to the connector at the FIB rack. The cable shield will attach to the connector at the junction board and to the board through the connector. |

1 Junction Board

### Contact person

Matthew Herndon, x8619, herndon@fnal.gov