CONSTRUCTION SPECIFICATION

NE-214.  CATHODIC PROTECTION FOR BURIED METAL STRUCTURES

1.	SCOPE

The work shall consist of furnishing and installing all material necessary to provide cathodic protection for metal structures as shown on the drawings.

2.	MATERIALS

Anodes shall be the type and size specified on the drawings.  They shall be commercially cast and pre-packaged.  Each anode shall have a full length core with a #12 AWG or larger insulated lead wire attached.

Magnesium anodes shall have a chemical composition of 5-7 percent aluminum, 2-4 percent zinc, 0.15-0.25 percent manganese, a maximum of 0.7 percent other varied elements, and the balance magnesium.  The packaged backfill shall be approximately 75 percent hydrated gypsum, 20 percent bentonite, and 5 percent sodium sulfate.

Wire for header cables, anode leads, and joint bridging shall be a single conductor, stranded, plain annealed copper with a black, high-molecular weight polythylene insulation and jacket.  The polyethylene shall conform to ASTM Designation D 1248, Type I, Class C, Grade 5.  The AWG size designation shall be as shown on the drawings.

Powder Welding Process shall be of the type and composition recommended by the manufacturer for permanently fastening copper wire to copper wire or to relatively flat steel or cast iron surfaces.  The resulting weld shall be a permanent, low resistance copper connection.

Silver Solder Process shall be for very low voltage electrical connections.  Manufacturer's instructions shall be followed.

3.	INSTALLING ANODES

The anode metal shall be centered in the packaged backfill just prior to the installation.  Moist, fine-grained earth material shall be used to backfill around the anodes.  The fill shall be placed in layers not exceeding four (4) inches prior to compaction.

4.	TESTING STATIONS

The test box shall be a metal, weatherproof device.  The leads shall be connected with a split bolt connector.  The electrical circuit shall be insulated from the test box.